08-06 Skid Module Transport and Instrumentation Design

发言人 1  00:00:01

It has to go back to the PLC panelSo yeswithin your panel, there should be a hardwired interlock

发言人 2  00:00:11

The, this T O T O signal is also I S signal or free proof

发言人 1  00:00:19

I envisage they're all IS signals

发言人 2  00:00:22

Yeah, that's so. So this, this cable should be, um... Within the there would be go through with the two different people trees. One is.

发言人 2  00:00:37

forOh no, sorry, sorry, sorry. Oh, oh, oh, oh, oh,I see signal. Okay, okay, okay, got that. Yeah. Okay。so that would be only one, yeah, number one

发言人 2  00:00:50

And the result, yeah, no, no two or three. Oh, okay, okay,

发言人 1  00:00:55

okay. Within or control panel, barriers. Hardwired into locking, yeah, and then the signal will go intoThe PLC,

发言人 2  00:01:08

yes, yesOkayno problem okay soUm, that means the the ah cables and ah you know fromYou connecting to the to the web could be divided to two keyboards

发言人 2  00:01:28

Let me see, let me seeright

发言人 1  00:01:32

Oh, it comes from the remote IO and I don't know, maybe a ten pair coming backA junction box on the skid.

发言人 2  00:01:42

Uh huh, yes, yes, yeah, we can we can we can puta small doctor in,I aska small doctor post here, okay?

发言人 1  00:01:50

Yeah, the important bit is those signals don't go back through the remote remote IO. Otherwise, it wont be independent hardwired interlocks.

发言人 2  00:02:02

Okay，Okay。Okay, okay, umThis is the first question, okay? Um, and the second for for the um controllers. No, weThat controllers we is analog analog control, you know

发言人 2  00:02:25

And the input is the let me let me take aUm, FIC, for example, this this flow controller, um, AI is the flow flow, you know thatAi is the flow and all the output and the output is just the flow set point

发言人 2  00:02:46

It's the flow set point. So when, when we want to, um, force the, the valve to some certain position, like the shutdown, shutdown position or.

发言人 2  00:02:58

The totally open position, then we just need to set the output to zero or zero or 20 are 20 million million ampere. Okay. And the fourth, so sorry, four, four, four.

发言人 1  00:03:19

It doesnt mean that the valve is fullyopen because youre settinga set point into the controller. No, and I

发言人 2  00:03:29

Um, i, we have committed, uh, uh, communicate with the vendor and the, um, the outputNo, um, twenty ampereI'm equal to the, you know, open position

发言人 2  00:03:48

好。

发言人 1  00:03:51

but whatSay say you've got a null to ten liters per minute rangeAnd you set the output to ten liters per minuteBut there's a fault on the controller that sees

发言人 1  00:04:12

You've got twelve liters per minute. It would then close the valve fully, wouldnt it? 啊，你这一块咱们个人上。给他聊。See反正。You're not forcing a position.

发言人 1  00:04:30

Youre settinga set point that mayopen or close the valve depending on. What the price there is

发言人 2  00:04:40

Yes, but if we, um, set the output toYou know, the output zero or 100% output is a little bit special for that controllerOkay, no zero output means

发言人 2  00:04:58

To fully closedAnd the zero, I mean, I mean, one hundred percent output, I mean, twenty ampere, twenty million ampereshould be yeah cleaning mode

发言人 2  00:05:19

So 20 ampere, we got from the vendor is that they can make it to cleaning modeAnd the controller, the valve could be opened你。啊，fully open

发言人 2  00:05:48

哎，高工，高宇，高宇在吗？高工。

发言人 3  00:05:52

哦哦，在了，在了。

发言人 2  00:05:53

哎，咱们那个，他当时、当时跟他说的是那个什么？啊。那个20毫安的时候，那个控制器是是个什么模式来着？是清洁模式，对吧？

发言人 3  00:06:06

就是全，就是20毫安，就是它的流量上限。流量上限来说，就是它能开到的最大、最大开、最大值、最大开度。嗯，然后这个时候可以。就是清洗的时候嗯可以开着，而且它清洗的时候。嗯，就是这个时候，就是开到最大的时候，可以用于清洗，嗯。对对。

发言人 2  00:06:32

I couldWe we we got from the the the vendor that the when uh as we put uh set set uh set output to 100% that is the valve could could be uh um

发言人 2  00:06:46

We see it is basically is the set point is the flow rate is the maximumAnd they, it can be used for cleaning

发言人 1  00:07:03

Okay。

发言人 2  00:07:07

And the the the bad position is is is the maximum vision. Its not fullyopen it but its maximumI

发言人 4  00:07:17

think. 对对对对。

发言人 1  00:07:23

Okay, I understand what

发言人 4  00:07:30

好。

发言人 1  00:07:31

他只要把把。So how close are wetoto actually operatingI was looking on our internet schedule and we end zero, so zero is zero

发言人 2  00:07:54

I'm so sorry I didn't get you very clearly

发言人 1  00:07:58

On the interlock scheduleThose flow controllers tend to be forced to zero, fully closed for an interlock conditionso ifOur normal control range, the maximum flow through the bronchus.

发言人 1  00:08:24

I thought we were operating typically right at the bottom end of the the rangeSo with our operators set, set up, they wouldn't be close enough to the 20 million signal to trigger that fully open and

发言人 1  00:08:43

Is that the way you see it嗯，这种。

发言人 2  00:08:49

I'm sorry, there are some big signal is not very good

发言人 1  00:08:57

if we take something like the hydrogen feed, So I think we're feeding hydrogen at not toWhat was our range on that? Are we doing that in a.

发言人 1  00:09:13

is a hydrogen feed and没。到了。Is that flow set at the north? Yeah, thatll be set asa normal meters or normal liters per minute, wouldnt it?

发言人 1  00:09:31

And we were operating between

发言人 4  00:09:37

啊，肯定很高，因为

发言人 2  00:09:39

都都两个孩子。

发言人 1  00:09:41

God, Desmond, help me out. Whats the flow range on the hydrogen controller atMCO3? 然后

发言人 4  00:09:47

是。

发言人 2  00:09:50

啊，你跟淘宝说，你给翻译一下。

发言人 4  00:09:53

是咱们那个氢气 m i c o c o 三的那个氢气控制，哎，听

发言人 2  00:09:58

不见听不见，李超博士，

发言人 4  00:10:00

哦哦哦，

发言人 2  00:10:01

没没开麦是吧？

发言人 4  00:10:02

哦对，忘了开麦了啊，就那个他说他问的就是那个氢气流量控制器的那个流量范围是多少啊？

发言人 2  00:10:11

啊，

发言人 4  00:10:12

就miko三好像是他说一下。

发言人 2  00:10:16

嗯。哎，这啥是啥？at M A负三是什么意思？那个高高宇这边知道吧，高工

发言人 4  00:10:23

氢气流量控制器的呃流量控制范围。嗯

发言人 3  00:10:29

嗯，我查一下啊，等我说一个。不是。

发言人 4  00:10:41

嗯。对，

发言人 3  00:10:53

我选的是嗯0.04~2标力。每小时。

发言人 4  00:11:01

Okay, so uh uh go you choose uh zero zero point zero four to two uh the normal meter as a normal cubic meter uh per hour

发言人 1  00:11:17

So our maximum flow we are looking for is one normal meters cube per hour

发言人 4  00:11:24

嗯，所以，所以它是那个最大的这个流速、流量、流速是多少？是1立方米每小时吗？

发言人 3  00:11:34

2立方米，

发言人 4  00:11:36

2立方米是吧？

发言人 3  00:11:37

对，2立方

发言人 4  00:11:39

米，

发言人 3  00:11:39

就是它的最大能力。

发言人 4  00:11:41

呃， the its capacity， the maximum capacity is two。

发言人 1  00:11:46

Through the flow control，呃，对

发言人 4  00:11:48

对，呃，就是通过这个流量控制器的最大能力是吧？Yeah, it's through the flow controller.

发言人 1  00:11:57

So we we operate in the01 to1 normal meters cubed range. And then we would set it to two if we wanted the valve to open fully

发言人 4  00:12:10

嗯，也就是说我们运行范围是0.1~1的那个标的，然后那个当我们希望这个阀门全打开的时候，我们设定成2是吧。

发言人 3  00:12:21

啊，对，yes，

发言人 4  00:12:22

exactly。

发言人 1  00:12:27

Okay。

发言人 4  00:12:29

下午

发言人 1  00:12:29

的那那那那也不知道。来让。Yeah, I understand that.I'm not sure I like it. Its not intuitive for the operator. The operator doesnt... Normally, when you set the maximum

发言人 1  00:12:55

Set point。

发言人 4  00:12:56

对对。你就就接到N上就就行。Completely for me as well. Its not that intuitive.

发言人 1  00:13:04

对对对，他接

发言人 4  00:13:05

哪个模式？他他。 Yeah, go ahead, sorry.

发言人 1  00:13:12

It could work. Um, because on our, when the operator sets the flow set point, we can control that band frompoint one to oneSo they can't manually input to

发言人 1  00:13:28

And then within code we can use the twoSo I think it could workBut I'm not sure I like it.

发言人 4  00:13:40

Yeah, understand.

发言人 3  00:13:42

嗯。

发言人 4  00:13:45

但是他觉得这个就是他觉得他理解了，但是这玩意儿他就是有点别扭，他不太直观，比较复杂。他呢相当于就是说你可能就是这个程序上，然后他需要输入的时候，你只能让他们输一个0.1~1。然后你写个程序，然后说这个让它这个就全开的时候，然后你点一下，然后它相当于是用2来输出这样的一个状态，但是可能对操作工不是那么的直接，不是那么直观。

发言人 2  00:14:16

Yeah, so we can we can just make a soft button on the screen and the for cleaning mode or something else. You can if you click that we just forced output the maximum to okay.

发言人 1  00:14:32

白色是那个。Yeah, okay红色和白色的线，这个应该是温度的时候，

发言人 2  00:14:43

还是and and still my the the the question is um one one last question for me um thatIs is it still the the the the uh the VAV CV 004 or the CV 008? CV008, yes.

发言人 2  00:15:01

Um一周。咱们说哦，那那你那你靠方自己自己告你了。哎，高工那个C O C O C O呃，C V零零4和0零八那个那个信号类型出来了吗？就是那个到底是是本案的还是不不报的？

发言人 3  00:15:24

C V004是。嗯，是是哪个呀？是电磁阀吗？

发言人 2  00:15:31

啊，对对对，一个一个是电磁阀，cv08是电磁阀，004是那个开发阀。

发言人 3  00:15:39

呃，004，那就是平常那种开关阀，就是应该那个是本安的那个，呃，

发言人 2  00:15:46

他的他D O也是本安的，是吗？

发言人 3  00:15:48

D O。

发言人 2  00:15:50

也可以，

发言人 3  00:15:51

由由那个嗯，现在主要是厂家选型没选完，就是咱们是本安和隔爆的两种。嗯，我是提的是本安的，但是有的厂我是想先按本安的考虑，有的厂家万一选的。选的药厂家做不了本案的，可能就会是格报的，现在我提的参数是本案的。

发言人 2  00:16:10

行，明白。那那那0008呢？

发言人 3  00:16:12

08的那个参数我也提的是本案的啊，ok

发言人 4  00:16:16

ok ok，

发言人 3  00:16:16

就是这个电003和008不是两个电磁阀嘛？也是本案对对对对对对，我也都是本案。现在我能不是本案的都按本案提的，除了咱已知那个质量流量控制器选不了本案的。所以说那个是增安的嘛，增安可爆的，其他的都是按本安提的，但是厂家最后最终选择的话，厂家看能不能做了，这个就是，我了解的是有能做的，有有不能做的。

发言人 2  00:16:39

嗯。好的好的，行，那明白了，那那那这个就后面再说了，那那这个可 case 里面没有什么别的。差别有有，不行的时候再说啊。

发言人 4  00:16:47

好的。

发言人 2  00:16:48

哎，好的好的好的，行，那那没事没事。That's all. Thats all.

发言人 1  00:16:55

Okay, thanks Desmond

发言人 4  00:17:01

Sorry for the late.I had a meeting with claire on people live and it's running late for several minutes

发言人 1  00:17:10

That's all right

发言人 4  00:17:13

Okay。So do you have any agenda, like any comments on the documents we sent through?I got Shao Feng and I got some agenda, like questions and

发言人 4  00:17:32

Some input needed and but I think it it's quite a lot so we can start from your comments on on theUh, on the documents, and then we can go to our agenda

发言人 1  00:17:53

Go on peter, what documents are you talking about? The ones you sent through.

发言人 4  00:17:58

The cleaning, cleaning method and also the. 呃呃呃，sense sense roof，呃，by children the cleaning method and also，呃。呃，这这这3D layout白双双。

发言人 1  00:18:21

Have you got a date when you sent that through

发言人 4  00:18:27

Let me check呃。哦，清洗方案跟那个就是连锁说明这些的，咱们还没有发给那个英国这边，是咱们内部的啊。对对

发言人 5  00:18:57

对，对，咱内部讨论开会那个。呃，有一些反馈嘛，就说调整，然后这两天应该是。嗯，我看看啊，就是下周二之前应该是3D啊，还有这些应该都能完成。就是主要咱内部发出来以后，内部互相之间做了一个类似会审反馈。哦，

发言人 4  00:19:22

OK，哦，我

发言人 5  00:19:23

刚才说错了，

发言人 4  00:19:24

我以为这，

发言人 5  00:19:25

哦，

发言人 4  00:19:25

没关系，那人我以为已经发到他们那块去了，OK。

发言人 5  00:19:29

嗯，没有没有，因为因为咱们说避免就是嗯。沟通的时候，比如说有些问题我们自己呃，比如说跟kids沟通的时候，我们自己其实可以解决的，有些把这些先过滤掉。啊，是这个意思，你可以简单说一下，就我们内部。嗯。先梳理一下，有些问题就是发现了再升版。啊。啊，下周二应该，哎，对，这些就是清洗方案，还有那个3D模型的更新。

发言人 5  00:19:54

还有那个控制说明，这些应该是都可以成嗯。

发言人 4  00:19:59

oh okay yeah sorry i made a mistake it's actually the the email was sent through theChina team and Shao Feng and Chaoqun were thinking that we can get a line in the China team and give out some draft with some complete ideas and so and then send to you and I just asked them about the date

发言人 4  00:20:25

And then they were going to send by next tuesday and then i revealed them as a complete version andLike a China team complete version and doing some review on that, on that, including the 3D layouts, the cleaning method and also the

发言人 4  00:20:55

Uh, the the uh the control uh con uh control uh operation uh operation menu uh something like that yeah uh so uh let's uhLet's start from our agenda on some questions and also some input needed by in these documents

发言人 4  00:21:21

Uh, Shao Feng, could you share the screen

发言人 5  00:21:25

嗯，好的。

发言人 4  00:21:34

Yeah, so uh, there, there are some uh decision needed and also some input needed, uh, and we want to discuss, and uh, we, we can放大一点，然后直接看A的这个部分。

发言人 4  00:21:52

So the first one is the em is em one topic that em we we were discussing on last em Wednesday's meetingWith good and clear, so they, they, they are planning to make the decision of how should we install the whole ski and either we are doing the full module split

发言人 4  00:22:22

As a baseline, or we transfer it as a whole and put them in from the roof, and so they want to, they want us to give them some estimate about the

发言人 4  00:22:40

How the first question is, is the four module split is feasible or not. If its not feasible, we can only do the. The whole whole whole speed plan, then we can just decide and

发言人 4  00:23:05

The other, the other one is how, how does the cost for each of the plan we may have some basic plan for them to make the decision

发言人 4  00:23:16

And also there is one, uh, uh, Ziliang has some, uh, uh, has, uh, one bike, uh, for the previous, uhDiscussions and we found the the the the ski size is not only

发言人 4  00:23:39

dependent dependent on the lift dimensionsAnd it may also involves the sea freight itself requires the split. So today is verifying that and.

发言人 4  00:23:56

Uh, if it does, then maybe the roof option, uh, no, uh, may, may, may lose some cost advantageUh, so then do you have, uh, any further, uh, uh, ideas on on that?

发言人 4  00:24:12

个赵工昨天说的那个海运，他可能对那个撬块也有影响。您那个验证是。确认了吗？

发言人 6  00:24:22

是的，那个集装箱的那个高度，正常集装箱的高度应该是在2米35这个样子，然后高一点的是在2米。2米6吧，2米59应该是。然后，所以咱们那个翘，哦，整体有一段的高度不能高于2米

发言人 4  00:24:43

5。嗯。ok呃，正常的是2米2米几2米3是吧，刚才我没听清。

发言人 6  00:24:51

对，是2米35。

发言人 4  00:24:52

Ok so uh according to the down uh the uh uh you uh when when we doing the separate uh theThe height limit for the for the for the box is 2.35 meters high and there are some special one and it could reach as

发言人 4  00:25:17

as much as two point five metersSo if we want to doing the safe rate, we may limit our our height to 2.5 meters if we want to

发言人 4  00:25:34

Transfer as a host key

发言人 1  00:25:39

UM, IF WE DO THE WHOLE SCAREDWe would crane it in through the roofsoOur limitation in terms of weight and size would be that it fits in the room and we can

发言人 1  00:25:59

We can support it on the existing slabSo I say if we if we crane it in, we'll get a crane that's suitable to lift whatever weight

发言人 1  00:26:11

And the size of the skid that fits in the space we've got available, the height and weight limitations are only around getting it into the lift car

发言人 1  00:26:23

That makes sense,

发言人 4  00:26:25

yeah, butAs we need to transfer the the ski from China to UK, and so the sea transfer, the the ship has a size limit for the for the box

发言人 4  00:26:41

The the one way do we when we are doing the shipment and this shipment has has seen that is 2.5 meters high

发言人 1  00:26:53

And okay, they've got high ranks as well for their containers.

发言人 4  00:26:57

Yeah, yeah, the containers, yeah.

发言人 1  00:27:07

So if you wanted to ship something oversized, is that just an additional cost or is that not possible?

发言人 4  00:27:14

呃，那个赵工，他如果咱们就是比如说超过2米5的话，他是就是花钱更多，还是说。那个，那个就是就就不行了，就是没法没法超过这2米5，2米5已经最高了。

发言人 6  00:27:34

2米5是最高的。

发言人 4  00:27:36

啊，就是花钱也没有办法了，

发言人 6  00:27:38

是吧？对，就是它就已经是高柜了。啊。补柜的话就是2米3几的这个。

发言人 4  00:27:45

Okay, yeah, it's already the maximum container, it's 2.5. Its not about the cost, its the. It's container limit and the normal container is 2.35 meters high

发言人 4  00:28:00

So it's already the higher containers, uh, two point five

发言人 1  00:28:14

Well, you must be able to ship something bigger than that. Its its just findinga carrier that will take it and the cost associated with it.

发言人 4  00:28:23

Yeah呃，他他觉得肯定这个会就是运载这更大的东西，他。找个这个愿意做海运的这家公司，嗯，然后那个花更多钱的问题。

发言人 6  00:28:46

嗯，现在查的高柜可是这个尺寸。啊。他说有没有更高规格的，那有可能就得找进出口部。让他们去帮问问去。

发言人 4  00:29:02

行，那咱们咱们找，还是说怎么着让？他们估计更没有经验，那还是咱们找是吧？

发言人 6  00:29:10

咱们找

发言人 4  00:29:12

嗯，您这边可以吗？

发言人 5  00:29:13

那边被。嗯，

发言人 6  00:29:16

和他妈不认识啊。

发言人 4  00:29:18

嗯。

发言人 6  00:29:21

呃，我在网上查，可是这个尺寸没有再高的。

发言人 4  00:29:25

嗯，那就是肯定得专专业的team，那就是咱们这边需要协调一下进出口部，然后帮忙查一下，是吧？这意思。

发言人 6  00:29:35

嗯。

发言人 4  00:29:36

嗯，那高主管，呃，您这边那个什么想法？有、有、有能力吗？

发言人 5  00:29:45

没有这个，没有这个，没有这方面的经验。这采购的看他们了解吗？呃。

发言人 4  00:29:55

嗯，主要是找谁呢？那这个就呃向上汇报，

发言人 5  00:29:59

那个赵工说的。嗯。对，赵工说那个进口路进进出口口部是吧？嗯。是说的不是咱单位的吧？

发言人 6  00:30:12

是咱们单位的吧，咱单位

发言人 4  00:30:14

好像是是

发言人 6  00:30:15

有吧，有专门跑海运的吧。

发言人 5  00:30:18

噢那。那就问一下他们呗，我还不知

发言人 4  00:30:22

道这个部门，我也不知道这个之前好像听说过这个部门，但是没没打过交道嗯。

发言人 6  00:30:29

是我也是听说过，没打过交道。我看了一下哈，就是在百度上查呃。问问豆包，他说还有一个高一点的，最高一点啊，这也是2米69。

发言人 4  00:30:43

咱咱们那个

发言人 6  00:30:44

是那那

发言人 4  00:30:45

没有了，对多少的高度啊？

发言人 6  00:30:48

咱们那个翘双点那个高度不得可到3米多去了。嗯。啊。对，就是

发言人 7  00:30:56

就是那个那个切分离器就是最高处都快43米6多了。3米6，3米7多了啊，已已经很高了啊。

发言人 5  00:31:08

那个高度就是是柜子的高度，然后我们。哦上次说过能能放倒吗？拆开。

发言人 7  00:31:22

放到他那个一个柜子，也有一个。空间内部。

发言人 6  00:31:28

对，它有个内部空间，它的高度就是2米69。

发言人 4  00:31:33

嗯，就就是放到

发言人 7  00:31:34

包括您的意思。全部放倒吗？

发言人 5  00:31:38

啊，不是不是，就是我我我是说这个疑问，他刚才说最高的高度嘛。

发言人 6  00:31:43

拿宽当，拿现在的宽当高是吗？对。呃，对对

发言人 5  00:31:47

对，就那意思，它的尺寸就像咱一个方长方体。就是他的最高是2米，你刚才说2米6多是吧？那个不管是2米6的还是咱，但是咱那个呃跳高不是都快4米了吗？那是肯定超3米了，也就是无论如何你高的，你的高就是按照我们设想的让他那个站着是过不去的，是吧？那你是无论是。嗯，

发言人 6  00:32:11

高档款。

发言人 5  00:32:12

啊，对，你只能是把它躺下，就是这么装。宽

发言人 6  00:32:15

的话，它这个箱子是2米35。

发言人 5  00:32:18

宽是吧？

发言人 6  00:32:19

对，宽是固定的，高我看它是有差别的。

发言人 5  00:32:23

嗯。对，就是我们，那就是拆那个四个撬块，不就是说这个议题吗？也就是说，你你这一个撬块无论如何是装不下一个一个箱子，是装不下的，对吧？

发言人 6  00:32:33

对对，

发言人 5  00:32:34

是的。就是常规箱子，那不就是拆撬块嘛，然后拆撬块以后。对，拆迁和第二个方案就是这种运的时候能不能倒着放，那就是加固这方面有特殊考虑的，对吧？

发言人 6  00:32:46

倒着放，现在来看不行。就是你现在来看，就是如果四个，目前规划的四个能不能变成两个？

发言人 5  00:32:54

嗯。Peter.

发言人 4  00:32:57

Hi, Keith.

发言人 1  00:32:58

I just googled it, and it suggests a forty foot rack containerWill be good for a over height loadAnd that that'll do sort of 3 meters by 2 meters by 4 meters

发言人 1  00:33:17

And it says you can secure it onto a flat bed frameSo it it looks like you just need a a a flat rack containerif you've got an oversized load

发言人 4  00:33:32

Oh oh okay yeah em yeah em em ziliang was also em using google em and em we we we we haven't asked the input and output em department from china so

发言人 4  00:33:49

There may be some solutions, and could you send us the link you found on Google, and so that we canYou see test reference

发言人 1  00:34:02

UmSoCan you open these links? Let me share my screen.

发言人 4  00:34:19

Thanks。

发言人 1  00:34:30

That we're we're just looking at this forty foot flat rack containerThe joys of AI, they don't give you a direct link to page.

发言人 4  00:34:50

Yeah. So the right hand side there are some links, maybeUh, but it's not that detailed. Uh, its not, its like a. they

发言人 1  00:35:02

sayCan you can you access that

发言人 4  00:35:10

I can, but I'm not quite sure if Ziliang can or not. Theyre there,Im using the VPN actually, soI can access Google, but its actually banned from China.

发言人 4  00:35:30

他在那个谷歌上查了一下，然后那个他说有这个，他就他上面写的40 feet的呃flat rack container，然后说这个东西是3米乘2米乘4米的。然后有可能能行。然后，呃，就是他在谷歌上查的一些可能是行的，那咱们还是。得问问。问问进出口部，看能不能解决吧，一部分。

发言人 4  00:36:09

如果不能的话，

发言人 5  00:36:10

在刚才钉钉看了一下，咱部门确实有一个进出口部，嗯，查了一下钉钉，嗯，但是没接触过。对

发言人 4  00:36:19

嗯。

发言人 5  00:36:21

赵文，要不你问他一下，

发言人 4  00:36:24

呃，问一下他。

发言人 6  00:36:32

没开麦。嗯，那就回头。嗯，要是都不认识，那就回头我我去找也行。对对对，要是要是咱要是有认识的，那就最好了。都不认识，那咱们谁找都一样啊。

发言人 4  00:36:47

对。

发言人 6  00:36:48

嗯，

发言人 4  00:36:48

或者就CC我们这个，我就是需要的话，我去来把这个问题描述清呃清楚也行。那行，那我跟他说一下。李

发言人 6  00:37:04

李博士，我给你截了个图，你看这是在咱们百度上国内百度上找的。

发言人 1  00:37:12

I sent you the first search Peter, and I've sent you a link to that, and I'm guessingBut um that one there is looking at

发言人 4  00:37:22

嗯，补充。是不是这？Yeah, we will check on that.Zena was searching on the China vendors, carriers, and so it's maybe differentStandard and in China, he just sent me the China standard containers and for China standard containers

发言人 4  00:37:53

On the there are fifty, uh, forty five feet, uh, uh, high, uh, H Q is called andAnd the the height is isThe height is 2.67 meters

发言人 4  00:38:11

Uh, and so it's maybe a little bit different, uh, from the Europe company and China company. We are doing some more, uh. Research on that, and also there is a input and output department in China, and then we'll contact them and to let them to find the wonders to see if

发言人 4  00:38:36

Uh, there are, uh, possible or feasible, uh, carriers for for the whole ski plan

发言人 1  00:38:47

Sure, it's these look like they were open top, so I'm not sure what would be the height limitation if they're open topIt must be some but

发言人 1  00:38:58

Yeah, it it it was open top, it could be three, three and a half meters and it wouldn't be an issue.

发言人 4  00:39:03

Yeah. According to Shuangshuang, the highest height reaching to like 3.6, 3.7 meters for the on the separator

发言人 1  00:39:21

Okay, we need to look at that.

发言人 4  00:39:24

Yeah. Uh, let's check the 3D model, and and then, uh, looking at that, and uh, but, uh, the, the, uh, the plan for the, the, the split module plan, and also the whole speed, uh, plan that we may

发言人 4  00:39:43

Put it into our tracker and to to to see the basic plan and their and and estimate their cost and the time limit and alsothe cost for the money and also cost for the F A T, S A T and other procedure and the risk, and so that we can let the high teams to

发言人 4  00:40:10

do the decision

发言人 1  00:40:12

Yeah, not sure

发言人 4  00:40:15

Thanks。呃，那我我跟他说一下，咱们找进出口，然后但是说把这个就是评估的事提上议程啊。那我们继续那个高主管能在线一下吗？

发言人 5  00:40:32

好的。

发言人 4  00:40:48

So the second one is the separators cleanliness verification, and our question is that the set glasses can cannot be fitted on the reaction column or the separator on the

发言人 4  00:41:05

At the operating procedure, so we show verification is may maybe not that feasible. So we are proposing to verify the cleanliness by sampling and the residue concentration and analysis.

发言人 4  00:41:26

And so, uh, do you think this, uh, verification method is a set ball? And, uh, about the acceptance criteria, uh, and could. Sandwich side QA to define the acceptance limit and analytical method

发言人 1  00:41:50

umYes, I do. Personally,I dont think theres any other choice. so i think we could build a case to say that was okayUmI'm guessing

发言人 1  00:42:15

When we've got the skidLayout sorted, we can work out an internal surface areaAnd from that internal surface area we can then work out a residual limit that will be acceptable

发言人 1  00:42:32

umAnd I'm pretty sure that's what our QATeam would look for is that internal surface areaYeah, but I don't know whatA smallThat's all based around larger scale equipment

发言人 1  00:42:52

Do you have anything forthe small scale continuous processesIs there any because that method may not be appropriate for small continuous operations

发言人 4  00:43:08

啊。ok，呃，let me ask，呃，我问了一下，那个就是这个咱们昨天不是说这个反应柱跟分离器的操作压力高，没法配目镜嘛，然后目视检查不行，只能用这种。取样分析，然后残留浓度的这种的方式，然后他说他他觉得是可行的，就只能用这个，拍一下这个验收限度的方法，是不是那个，呃就是英国的这个qa来做，然后他说他们就是要，就是用3d模型算个表面积，然后根据这个表面积，然后来确定这个。

发言人 4  00:43:48

呃，验收限度，然后，但是这个是对于大型的设备，他们是这么搞的，然后，但他不知道这个咱们这种小型的还是连续的这个设备这么搞，对不对？对不对？然后问问咱们有什么经验没有？嗯，高主管或者冯博士。这个，啊，或，啊，您说。这个，

发言人 5  00:44:11

对，呃，这个我们没有什么经验，冯博士他有点，所以。啊。对，那个什么清洁度，就QA的那些。嗯。嗯，就是咱们

发言人 4  00:44:22

对。啊，那就是咱咱们也不太知道，就是这个是按这个表面积来算，还是有一个特殊的方法是吧？

发言人 5  00:44:32

这个嗯是那个什么方面的，这个我们没有经验。ok。

发言人 4  00:44:37

对，那我就跟他说一下，然后咱们问一下冯博，然后让他或者让冯博去问一下QA，然后给他这个写个邮件回复一下。

发言人 5  00:44:48

嗯，冯博的意思不是咱这边的，有可能跟英国的要求不一样嘛啊。

发言人 4  00:44:54

啊，就是他们可能想参考一下咱们具体的方式，就是我觉得还是他们定，但是这个。呃，告诉他们一下，咱们怎么定这个数啊？可能他们需要也参考一下这种状态。呃，就可能

发言人 5  00:45:15

行啊，不是具体数字，

发言人 4  00:45:17

就得告诉他们一下方法。

发言人 5  00:45:20

对中国现在没在线是吧？

发言人 4  00:45:22

嗯。对，那那我跟他说一下，然后呃您这边问一下冯博能不能给他们就指导一下方法，

发言人 5  00:45:31

然后我们就更新到那个进展里，现在这些特别多，

发言人 4  00:45:35

就是

发言人 5  00:45:36

第一条是什么？结果就是。

发言人 4  00:45:39

这个呃，

发言人 5  00:45:40

赵工得让赵工去核实嘛，咱进去咱更更新进去。

发言人 4  00:45:44

聊一下啊。对

发言人 5  00:45:45

对对，你稍等你稍等，我找一下那个这个是哪

发言人 4  00:45:48

一个是

发言人 5  00:45:49

分分撬那个。

发言人 4  00:45:51

对。冰箱那个。

发言人 5  00:45:53

好多模式切换，

发言人 4  00:45:55

嗯。哎。行，那我这么先跟他说一下啊，那个第二个问题。嗯嗯嗯嗯。呃，hey kis，i just ask，呃，ask the shao feng and he he is notHe doesn't know about this one, but jian tao and q a team may may know about what method we use for the continuous and small scale

发言人 4  00:46:23

Equipment and we will ask xintao and the q a team to get the methodWe were worrying the standard may be different. We can give you the method.

发言人 4  00:46:43

The real number may be taken from the UK's Q18.

发言人 1  00:46:53

okay, I don't believe we have any umStandards for continuous.

发言人 4  00:47:00

Oh, okay.

发言人 1  00:47:02

So this would be new for us

发言人 4  00:47:04

OkaySo which

发言人 1  00:47:06

is goodHave flexibility.

发言人 4  00:47:09

Yeah.

发言人 1  00:47:10

But bad in another, as they wont want to makea decision.

发言人 4  00:47:15

OkayOkay then, uh, I will contact to Xintao and to get as much detail as, uh, as I could and, uh, and send through and then we can decide together, uh

发言人 4  00:47:31

To work it out, yeah

发言人 1  00:47:34

Yeah, thanks Peter

发言人 5  00:47:46

哎，里边就这条是吗？刚讨论的。

发言人 4  00:47:50

呃，对对。是吧？嗯。对，就是按蓝色那块的，对，没错。

发言人 5  00:47:59

对，然后是刚才说的是需要冯博答复那个验证。

发言人 4  00:48:06

对，就是验验证的方法也是也是在这一条呗。

发言人 5  00:48:11

嗯，对我是说需要呃。冯博士。提供一下那个什么。

发言人 4  00:48:18

就是需要提供一下那个计算呃验证。呃，验验收限度的方法。就是国内怎么做？嗯，对，就这个意思。嗯。好的。

发言人 5  00:48:53

那跟俏那个没找到啊。

发言人 4  00:48:55

行，那后续再再弄吧，那个分翘那个。

发言人 6  00:48:58

是不是在最后面？分

发言人 7  00:48:59

翘分翘那个。80

发言人 5  00:49:02

20是吧？对对对，写上吧。那个扣扣就担心忘记了。

发言人 4  00:49:08

嗯。

发言人 5  00:49:09

80变了是吧？那在这个

发言人 7  00:49:11

前面77、10哦，我刚还看。

发言人 5  00:49:17

哦，对，这个啊，这个是说让。

发言人 4  00:49:22

嗯。

发言人 1  00:49:46

Peter, we've been looking at the 3D model. Its nowa good time just to show you where we are with. 在

发言人 4  00:49:56

吗？Yeah, great

发言人 1  00:49:59

yeah, that's好的。

发言人 4  00:50:06

好的，他说他们那个，他们也在看那个3D模型，然后现在要给我们看一下，就他们的思路和他们做的东西。

发言人 5  00:50:16

呃，意见是吧？

发言人 4  00:50:17

好的。

发言人 1  00:50:19

Can you say that beta?

发言人 4  00:50:21

Yeah,I can see. 还帮。

发言人 1  00:50:32

没有。没看到礼貌。So we have gotour servicesAre coming in through that side wallUm, so we were looking at trying to organizethe tcusSoPhil was going to draw up

发言人 1  00:51:01

Draw some time points. Hes going to take an extract from this with some time points. And we were trying to make it so we come.

发言人 1  00:51:10

First one comes into these two flow returnReactor goes in there, reactor into the next pairUM CONDENSERThink into the next pair and then

发言人 1  00:51:25

reactor three into the last pairSo we were looking at potentially giving you some time points at the backSo you can then route your piping to the back and up. Weve tried to make it so the pipes dont cross.

发言人 1  00:51:39

in terms oflayout for which tcu goes whereumon aEmergency relief, we're going to come down不对吧。I can't remember whether we were gonna try and take it across, cause I think your time point is somewhere over there.

发言人 1  00:52:02

And then the hydrogen, we were gonna cut that short, drop it down. And drop in. So we we should be able to give you an extract showing where we think is the best place for the tie in points.

发言人 1  00:52:15

The nitrogen is here so we can put our rotameters in line and then connect into piping on this faceWe may need to reverse the direction through one of the vent headers

发言人 1  00:52:34

Well, that doesn'ton the p and i d it matters, but it doesn't matter in in realityAnd then our vent header will again come through the back wall somewhere around that point. So we were looking at.

发言人 1  00:52:48

Sorting out some proposed tie in point locationswe have some extract duct that comes through the wall herewhich looks like it could clash

发言人 1  00:53:02

I feel was going to pull that into the model as wellAnd make sure thatWe have an option not for any clashes when we go outside the skid on the high

发言人 1  00:53:15

We got the emergency shower sits in herewhichIt was going to showThis panel, I think we can still fit in on the top. This panel.

发言人 1  00:53:27

Doesn't fit in that locationBut we need to look for an alternative for a low level panelYeah, so Phil wasGonna pull together some

发言人 1  00:53:44

extracts from the model so we can send it to you guysYou can see where we havesome fundamental clashes, limitationsAnd hopefully that'll be in the next few days. He was working on that last week.

发言人 1  00:54:03

And then once weThat part works sorted out, we can then start looking at how we access valves actually within the skidAnd make sure that the operators can access the valves and then the maintenance guys can access what they need to take out or visually inspect for

发言人 1  00:54:23

for annual plan maintenanceSo yeah, it'sThere's some work on the interface between the twosystems but it's it's lookingLooking okay. Yeah,

发言人 4  00:54:41

great. Thanks。Let me transfer this one to Shangshang, and I remember them, most of them呃，就是呃，范工他们现在做的是把各个这个就是呃，两个界面的接入点，然后现在现在搞出来，

发言人 1  00:55:02

然后

发言人 4  00:55:03

他们下呃，这这几天可能就能把这个接入点这块儿，然后更详细。你看上面这块儿，那八个网站的时候，是他们那个TCU的接入点。然后分别给那个三个反应器和一个这个冷凝器接入这个TCU，然后最左边最高层的那块，那个相当于是它的那个泄放管道，然后他们正在找一个好的点，然后它这个泄放管道它跟呃这块可能会有冲突，他们尽量让这些管道。

发言人 4  00:55:36

就是不交叉之类的，然后右边那个玩意儿是氮，嗯，氮气、氮气供给，然后那块也是尽量不交叉，然后那个在那个整个撬块的右边，它是那个啊那个那个呃紧急淋浴，紧急淋浴它上边那个

发言人 3  00:55:58

控制柜。是那个

发言人 4  00:56:00

那控制柜那块吧，底下那个控制柜是跟那个紧急领域有冲突的，得看一下怎么搞，就底下那块了，然后这个他们把这些timing point和两个交叉弄完以后。然后再看看这个，确保这个

发言人 6  00:56:16

板

发言人 4  00:56:17

操作功能够得着够得着，能够去那个正常操作，然后那个需要维护保养时候维护保养人能拆出来，然后基本上就行，他们目前看。应该是就是还好的。啊，情况

发言人 7  00:56:36

就是啊，那个李博士他就是嗯，他希望就是咱们把这个管口和他现在给的咱们这几个管口对上，是那意思吧？

发言人 4  00:56:43

他的time point就是比方

发言人 7  00:56:45

说这几个tcu的，我是嗯，我是在这边出的，他想在那个那边出，然后我给他对到对到他那上面。

发言人 4  00:56:51

呃，对，就是他这些那个对接的界面，他可能这这几天给弄好，然后估计还看看。就他确定完对接的点以后，可能会给一个方案，然后咱们就弄就行。我、我、我感觉他们会给方案的。

发言人 7  00:57:09

哦哦哦，就是行行，那他他这个嗯他回头是给咱们一个方案，他会给咱们一个模型吗？

发言人 4  00:57:18

就是

发言人 7  00:57:19

就是他这个。

发言人 4  00:57:20

是这这个。

发言人 7  00:57:21

他给他们一个模型

发言人 4  00:57:22

是吗？是不是他们自做的呀？我感觉不是咱做的吧。对对对。他就是给这种模型。

发言人 7  00:57:27

黄的是那个嗯。嗯。黄的是tcu哦哦那行那行就是他给了之后咱们去找他的口

发言人 4  00:57:33

呗。对对，就等于是把这个给接上的那种状态。

发言人 7  00:57:39

可以。

发言人 4  00:57:40

嗯，行，ok，yeah，just let let shuang shuang know and thank you for the update

发言人 1  00:57:49

That's okay. We will probably ask for some brackets. So when we put our rotameters somewhere along here, if we can put some mounting points for them

发言人 1  00:58:03

And there's a couple of cones that will sit above the skid for hydrogen detectionumSo we canIf we can put some mountain brackets for those

发言人 1  00:58:20

uminstrumentationOne in there, cave. Here are young Roy. I can't remember all that stuff we yesterdayPolyester foam or whatever it was in purple bags and put in the purple skin.

发言人 1  00:58:49

Thats right. So weve weve got these cones going above. Weve gota hydrogen detector that sets. In that area thereAnd there's a little L shaped bracket, so we can just get a mounting point so we can put the brackets above the skid

发言人 1  00:59:04

So there is a hydrogen leak we can detect it. But well sort that out and well let you know so you can see. where we think it would fit and

发言人 1  00:59:17

some suggested locationsOkay, yeah, there's a couple of little things there. We also had the hose connection for raw materials.

发言人 1  00:59:25

Speed and the product discharge, we were going to show locations for thoseThat we can make sure that we pipe up toTo a good point for the operators

发言人 4  00:59:39

Yeah, that's great呃，他、他们还这个会做那个，就是氢气探测，就是信号检测的几个点，然后他就那种l型的这个这种支撑的这种的孔状的。这种的，刚才他放的那种的 pid 类似，呃，不是 pid 是那种 3D 图的那种类似那种装置，然后他会把这个位置确定好，然后告诉咱们在在哪块，然后还有就一些软管的，就是他加加料的。

发言人 4  01:00:09

这些的这个位置什么的，然后估计在上边都这些都是在撬块上面的位置，然后他也都会确定好，然后这样的话就更详细一些。嗯。Yeah, thank you

发言人 1  01:00:26

That's probably

发言人 4  01:00:32

诶。andSo, uh, Shao Shao Feng could share the screen, and we are run out of time. Uh, do, uh, could you, uh, stay for another like half an hour? Yes, thanks.

发言人 4  01:00:56

yeah thank you那高主管，那我们再搞个半小时，然后尽快的快速过一下后头的问题。

发言人 5  01:01:06

对，就是快速影响，有可能影响大家往下设计的，然后快速那些简单的跟他过，有特别难的咱就哎对。对，是

发言人 4  01:01:14

的，我我也这么想，就

发言人 5  01:01:16

对，超群分享一下那个需要的话，超群分享那个。呃就那个跟踪表是吧？嗯对。吕博士啊好的。

发言人 4  01:01:24

都可以啊。嗯嗯

发言人 5  01:01:25

嗯好的。

发言人 4  01:01:26

分享一下啊。就是。就是你取个名字。

发言人 7  01:01:45

是要过那个蓝色的吗？

发言人 4  01:01:48

对，呃，过那个蓝色的，我看。有一个喷淋球的形式。

发言人 7  01:01:56

星球的形是放哪儿的？

发言人 4  01:01:59

经经力器就看到哪个说哪个吧，经力器也可以。

发言人 7  01:02:05

我看一眼啊。

发言人 4  01:02:09

呃，嗯，没事，咱们就从从头往下过也行。嗯，啊，

发言人 7  01:02:13

行。

发言人 4  01:02:15

就是遇到蓝色，我们停住就行。我看到一开始是激励器，

发言人 7  01:02:19

这个是过完了。

发言人 4  01:02:22

嗯，清洗的过完了啊。嗯，

发言人 7  01:02:24

对。

发言人 4  01:02:25

然后往下。

发言人 7  01:02:27

这个是那个。

发言人 4  01:02:35

这个7月10号的反馈是不是之前的问题？还是昨天的，我不记得昨天是。

发言人 7  01:02:45

李博士，这个说来着，这个昨天就是说，嗯，说咱们这个就是现在这个反应反应，他不是要加卸料吗？现在这个反应柱的进出口的位置，就符不符合他那个加卸料的一个加卸料的方式。

发言人 4  01:03:00

呃，他刚才

发言人 7  01:03:01

就是还得看3D模型，

发言人 4  01:03:03

给给给我们看那个3D模型的时候，说他们那个在在设计软管的位置，就按咱们的3D模型，他们在设计软管位置啊。就是他们已经在做这个事了啊。

发言人 7  01:03:18

那就，那就等他们3D模型返回来之后，我再去看一下这个啊。对，

发言人 4  01:03:22

嗯。行。

发言人 7  01:03:24

行，那这个过了。可以。往下。

发言人 4  01:03:26

可以。嗯嗯。

发言人 7  01:03:27

嗯。这个，这个好像是孟工的。

发言人 4  01:03:34

嗯。孟孟工是不是一开始说完了？我不知道这个我当时没在

发言人 2  01:03:43

啊，对对，我这个这个说

发言人 4  01:03:44

完了说完了，好的，完了

发言人 2  01:03:47

嗯。

发言人 4  01:03:48

yeah

发言人 7  01:03:51

然后就是这个了。

发言人 4  01:04:03

呃，这个，这个是咋回事？我也忘了啊。

发言人 7  01:04:07

我看一下啊。

发言人 4  01:04:20

给他们看一下价格。哦，你这个剩下的。

发言人 7  01:04:31

这个。

发言人 4  01:04:34

听过来。对。还是我看。嗯，

发言人 7  01:04:56

这个回复是之前、之前就回复的，是吗？

发言人 1  01:05:03

California, I used to spend in the upstairs over there. They said position but car protection.

发言人 4  01:05:10

呃，我不记得了，这个是昨天聊的吗？

发言人 1  01:05:14

Peter, I'll just see thirty seconds. Okay, sure.

发言人 7  01:05:20

我看一下昨天。

发言人 1  01:05:25

对。

发言人 4  01:05:29

哎，你那个。这个需要问他什么吗？今天没有。明天。

发言人 7  01:05:35

那个催化剂的是吗？

发言人 4  01:05:39

嗯。呃，高主管，您这边有印象吗？

发言人 7  01:05:47

5个。

发言人 4  01:05:50

都得。

发言人 7  01:05:55

就是那个催化剂的这条是要。就是现在屏幕显示的这个收款机，这个收款机这个

发言人 5  01:06:04

不是说那个呃，就是我们后来定的是3的位置做那个收款机装填嘛，嗯，所以就当时那意思呢。就是这个，他的顾虑这些是不是三个位置就考虑了？应该是这个想法啊。因为最开始的时候是，嗯，他有这个疑虑，就是放在这块，应该是这个意思。

发言人 4  01:06:27

哦，这个，这个好像是他们已经回答过的吧？我怎么记得？

发言人 5  01:06:32

刚才过来就是，那就yes了，是不是能关掉？应该就这意思，简单的问一下就关掉了。ok，呃就是不需要在我们这再挂着了。嗯

发言人 4  01:06:41

行，yeah，呃for the呃rose sixty three and呃about the呃the the calories。AndWe we found the ah there there was a previous question about the ah design face and also be and

发言人 4  01:07:02

Um, it's about the, um, the exposure level requiring OEB 3 or lower containmentAnd, uhAnd we saw there was a response from your side.

发言人 4  01:07:19

Could we close that? Or is there any verification should be done by the China team?

发言人 1  01:07:28

I don't believe anything needs to be done by the China teamIt wasif anything, that's just aA trail, soIt showsIt didn't meet OEB 4, we agreed that OEB 3 would be fine, and that's that's it.

发言人 1  01:07:48

Well close it out and go from there.

发言人 4  01:07:51

Okay. yeah，great，thanks。这这块不用那个这个咱们呃就是中中国团队做任何事情，然后但是这边也没有close，他他们得那个自己弄一下。就是看做做一些试验，然后如果就OEB3就行了，就就完事了。他他们来close这件事，然后但是这个就不用那个啊，国内团队做任何事情的。

发言人 5  01:08:18

嗯，好的，那我们对是不是还需要做？哎，对对对，就是相当于负责人。哎哎，对对对，这样改，大家都避免忘掉，是吧？OK，

发言人 4  01:08:27

嗯嗯，行，好，嗯。OK，那继续往下吧。

发言人 7  01:08:37

这个刚过了，

发言人 4  01:08:38

对，这刚过了，嗯。

发言人 7  01:08:40

这个应该是不是也过完了？这个

发言人 4  01:08:43

对，过完了。嗯。

发言人 7  01:08:50

然后是这个。

发言人 4  01:08:57

So, uhAbout the em FTR 98 em 32 em the polishing filterAnd the differential pressure monitorWith the interlock has been added and the solvent cleaning

发言人 4  01:09:21

Um, addresses the um part part particulates and is this um differential um pressure interlock plus the periodical cleaning um sufficient or do you think

发言人 4  01:09:38

We, uh, uh, we, we need a duty or standby filter with online changeover

发言人 1  01:09:47

UmI think we I think we talked about this, and we didn't think we needed duty standby filter. Uhhuh. UmBut if you look at the filter, if that filter did blind

发言人 1  01:10:05

Umwe would pressure our systemIf we set an interlock, that interlockUm, I suppose the inlet will be on the differential pressure, which is

发言人 1  01:10:21

Goodhow do we depressurizethe reactor system to be able to change itI think that's that's kind of the question that sits there

发言人 4  01:10:38

嗯。

发言人 1  01:10:40

So yes, greatIt's blindedSo we shut the plant downbut if it was a sudden breakthrough ofdust, debris, whatever from catalyst breakdown

发言人 1  01:10:58

How do we thenThe pressure on the plan because that's in effect a blockageAnd our vent for the planIt's downstream of that filter

发言人 4  01:11:12

嗯。Okay。呃。

发言人 1  01:11:20

Yeah, it'sI'm just wondering whether we need to putI don't like put an event there, but whether we need to put event so we canDrop the pressure

发言人 1  01:11:32

If we do put a vent there, where are we venting toBecause potentially it's going to be a fire meBent streamAs we drop the pressure

发言人 4  01:11:52

yeah呃，他想问的是，就是这个激励器嘛，然后他这个咱们当时是加了一个压差监测连锁，然后那个，然后同时就是，呃，这个定期清洗，然后这个就是这种粉尘之类的。然后他说不需要这种，那个就是备用的，然后在线切换什么的。然后但是他有一个问题是，这玩意儿如果堵了的话，那这个咱们怎么减压？因为那个泄压的那个。

发言人 4  01:12:27

这个这个呃，谢放全在后头，他不在前头，所以是不是要在这上头加一个谢放，但是谢放的话。加的话，加一个管呢，排到哪儿去？然后。呃，是个问题，他们他也没想好，然后看咱们这边有什么想法。

发言人 7  01:12:50

是不是可以加个彭通啊？进滤器要是过滤器堵了，然后加一个旁通，然后从旁通先泄压。

发言人 4  01:12:59

卸卸到哪儿啊，就是继续往下走，是吗？

发言人 7  01:13:02

对对，走到分离器那儿，分离器那儿不能泄压吗？ok。

发言人 4  01:13:09

So Chao was thinking about adding a bypass, and if this, if the polishing filter is blocked, and then we can go through the bypass to the separator directly

发言人 4  01:13:22

And relief from the separatorThere's a relief on the separate

发言人 1  01:13:33

Yeah, that, thatThat makes senseThe only thing with a bypass is it's not a bed leg for cleaning.

发言人 4  01:13:45

嗯，也，那就是引入了这个清洗的时间，他如果有一个好的服务的话。

发言人 1  01:13:55

So that might be it.I'm guessing if it goes up and overand it free drains, then you do drain it out, and then you'll fill it with cleaning

发言人 1  01:14:07

Or maybe we need to open it during cleaning just to flushthatThat little bypass through

发言人 4  01:14:15

那是不是那个、这个、这个、这个旁路重按这种，就是晶粒器堵堵的情况下，否则都用不上，就没有必要、必要清洗吧？但他是担心那个，这个就是那个就是这个你的这个旁路会那个增加它清洗的死空间吗？然后就是你清洗的时候也得洗它那种状态，那我感觉是不是它平时就就很少会用。

发言人 7  01:14:45

那旁路平时用不上。

发言人 4  01:14:47

嗯，那那这种情况下，咱们还需要清洗旁路吗？

发言人 7  01:14:56

那可能可能。那可能还是得洗的，那那有死空间在那儿

发言人 4  01:15:04

啊，确实有死空间是吧。

发言人 7  01:15:07

嗯对

发言人 4  01:15:08

嗯。

发言人 7  01:15:12

那就不适合加跑路了。

发言人 4  01:15:14

嗯。那我们再想想，还是在这块儿有什么直接的想法跟他说。Yeah, we also think there there will be in em introduce some dialogue em for cleaning and it may be not that suitable for a bypass here

发言人 1  01:15:44

I like the ideaEverything is a compromiseIf we put the bypass in, then we canBe pressurized. Yeah. Which is good. And we can always open it during cleaning and flush it through as part of the cleaning cycle. SoI think its probably.

发言人 1  01:16:06

The most pragmatic, the the best just seems to be the best solution. Does make sense.

发言人 4  01:16:11

Yeah, oh okay, thanks. 他说他觉得盘古就是你，你得妥协一下嘛。然后那个有个盘古的话，他能解决问题，而且可能是已经是最好办法了。然后到时候清洗的时候，直接把盘古打开，让它全留留一遍就行。然后加一点死空间，就加点死空间呗。然后他觉得这是妥协后最好的解决方式嘛，可能。

发言人 4  01:16:40

也。嗯。嗯。您您觉得呢？

发言人 7  01:16:45

可以。就加个旁通。然后洗的时候就是把旁通开开都一起洗了。

发言人 4  01:16:52

对。Yeah, okay, so, um, Chao Chun think that that would work and we can clean, when doing the clean, we can open the bypass and limit the, um, influence

发言人 4  01:17:06

And so, yeah, so uh we will uh record this solution uh in the tracker

发言人 1  01:17:16

yeah noIt's good,

发言人 4  01:17:18

thanks行，那这个就等于解决了。嗯，

发言人 7  01:17:25

然后下一个是差压的这个。

发言人 4  01:17:29

嗯。插压的这个呃。

发言人 7  01:17:36

就是反应器的话，因为现在它那个不是用的差压，是用的两个，是用的两个反应器的压力相减的。然后的话，因为那个反应器被压比较大，所以它可能那个精度不够。然后我们现在是差压也做上了，然后最大误差。就是高于给的40千帕，然后也把压力高高都做上了。问一下这样可以吗？

发言人 4  01:18:02

OK，

发言人 7  01:18:03

还是查压，还是取消？嗯。

发言人 4  01:18:09

是，呃呃等等等，就是咱咱们插压已经加加上了是吧？

发言人 7  01:18:18

嗯，给你看一眼，他现在就不是这是一个计算的那个插样嘛。嗯，他是用的这个压力减的这个压力，这个压力减这个压力，然后呢，因为这个压力他。值比较高，倍压不是1~6嘛？然后的话，差压其实这个反应度差压比较小，它可能精度达不到。因为它本身的进价比较高，嗯。然后他进度可能达不到，然后我们现在做的是呃，插压也保留了，然后的话这样压力高高也做了连锁，对的，

发言人 4  01:18:50

3个位。嗯，然后那个，我想问他这个可不可以，然后你说什么拆拆压需要减，就最后一句我没听懂。但是临时比如说跟什么，

发言人 7  01:19:01

就是咱拆压现在最大的误差是40千帕。嗯。

发言人 4  01:19:05

可以，然后直直接问这个方案可不可以就行了是吧？就是说不需要做任何改变是吧？嗯。

发言人 7  01:19:12

嗯对。

发言人 4  01:19:12

yeah so uh this one is about the differential uh differential pressure monitoring andFor this one, based on the transmitter accuracy on the reaction column and

发言人 4  01:19:32

Inlet outlet lines, the maximum differential pressure error is approximates 40 K, 40 K PascalAnd a pressure interlock was added for high, high as well.

发言人 4  01:19:50

And so, is there any remaining concern on the accuracy? Or otherwise, we can close this item. Item or not

发言人 1  01:20:01

I amThe problem with this one is we, we measure aA static pressure or absolute pressureand then we use two measurementsto give us a differential

发言人 1  01:20:25

UmSo ifyou send fortyforty kilo point o four barYou're saying it's accurateSo if, if oneAre they really that accurate

发言人 4  01:20:46

According to Gao Yu, that's the maximum differential pressure error

发言人 1  01:20:58

but then measuringThey're measuring aA static pressure aren't they

发言人 4  01:21:06

咱们相当于是那个，这个测的是静态压力，是吧？

发言人 7  01:21:11

对你现在测的是静态的那个压力，yes，然后用它两个值减的是差压。

发言人 4  01:21:17

yeah，measuring the static pressure using the difference

发言人 1  01:21:28

So those gauges are accurate to within point zero five percentpoint zero four percent

发言人 4  01:21:35

等于，那就是它的这个精度就是0.05%。那种状态，0.4、0.5的0.4%、0.5%，是吧？

发言人 7  01:21:48

那个那个压力表精度是多少来着？哎，你。浩宇在吗？他之前跟我说了，我有点忘了那个压力表的精度。

发言人 3  01:21:58

0.0%嗯，那个管道上那个是0.5。嗯，管道上0.5，然后塔的那个应该是0.0.1。嗯，ok，嗯，所以综合下来的误差最大误差是是这个。

发言人 4  01:22:15

ok，so theThe the the the level transmit, the the transmitter, pressure transmitter, the on the pipe is 0.5 accuracy percentage effort and

发言人 4  01:22:29

Uh, the tower one is uh zero point one percentSo, as a whole, it may going to forty K pa空。单位非常不对。基本上是这。

发言人 1  01:22:49

umpoint four fiveor point zero four fivePoint four five.

发言人 4  01:23:04

Point five.

发言人 1  01:23:07

Yeah, forty five kilopascals45KPA

发言人 4  01:23:13

呃，45千帕是吗？Oh, we

发言人 3  01:23:26

就是键盘，嗯。

发言人 4  01:23:32

You mean the maximum differential pressure errors

发言人 1  01:23:37

The maximum error measuring a pressure at that pointis going to beJust on calibration on instrument accuracy is forty five kilopascals

发言人 4  01:23:52

Approximate 40, 40 kilo pascals

发言人 1  01:23:58

Okaywhich isI'll throw it into my point point four bar

发言人 4  01:24:08

yeah

发言人 1  01:24:09

And so you got point four bar error on one pressure transmitterYou got point four bar error on the other pressure transmitter.

发言人 4  01:24:19

No, not exactlyIt the the the compromise, the the the as a whole, the the the uh it's like 40K par, not not one呃，每一个的那个这个误差是多少啊？他你0.5%那个看了管

发言人 3  01:24:43

道上，那是0.25%，0.25%啊，

发言人 4  01:24:47

0.25%啊，那是多少？它是正负的关系吗？啊，对，正

发言人 3  01:24:51

负。正负多少？正负的关系，如果都取最大，我这个是量程是0~0到千帕，0~1万千帕乘以对10bar，然后乘以0.25的话，10bar乘以。0.25，那还不是0.025。不是百分之。等于是25。对，0.25%就是25千帕的呃误差，然后另外一个。那个，这是管道上的，如果设备上的是0.1，设备上0.1选的是。

发言人 3  01:25:30

嗯，设备上我看一下，设备上是也是10吧，0.1，那就是。嗯。10千帕。

发言人 4  01:25:41

嗯。

发言人 3  01:25:43

也是18、11万乘以。01是10千瓦，

发言人 4  01:25:48

10千瓦啊，一个是25千瓦，一个10千瓦是吧？

发言人 3  01:25:52

10千瓦，嗯。对误差，然后这是绝对误差，然后那个如果是这俩加一起，就是哎是0.1呀。

发言人 4  01:26:04

0.35是吧？

发言人 3  01:26:09

嗯，23。嗯，10，知道我

发言人 4  01:26:14

看这个数据。

发言人 3  01:26:16

这家也

发言人 4  01:26:17

也行。

发言人 3  01:26:20

0.对，那就是大概是。加一块是35千帕吧，

发言人 4  01:26:30

不是10帕，0.25%，0.25%，不是2.5%，是吧，0.25%。

发言人 3  01:26:36

对，0.25%。那1

发言人 4  01:26:37

0bar啊，那10bar的1%。不是10

发言人 7  01:26:40

吧，应该是100。10

发言人 4  01:26:42

0bar吧。

发言人 7  01:26:42

应该是100bar，因为它超压力不是10~80嘛，选择量程应该是100吧。100

发言人 3  01:26:48

bar吧。啊100bar就是1万千帕。

发言人 4  01:26:50

OK100barOK我知道了OK。So I got it, got out the information. Its actually the make the range is zero toa hundred bar, and for the instrument on the pipe, the accuracy is.

发言人 4  01:27:09

Zero point two five percent and so it's zero point two five barUh, for the uh, uh, accuracy, uh, the, the, uh, maximum error, uh, on the equipment, uh, is also the range is one hundred bar and the, uh, the error rate is

发言人 4  01:27:32

The accuracy rate is the zero point one percent, so it's zero and adding them as a total is zero point three five bar

发言人 1  01:27:48

So if you had a perfect calibration

发言人 4  01:27:53

yeah

发言人 1  01:27:55

You can you could potentially be

发言人 4  01:28:02

That one is going to zero point two five bar up, and another one is zero point one bar down, and so it's zero point three five bar

发言人 4  01:28:13

A maximum error

发言人 1  01:28:16

And we are, what's what's the expected pressure drop acrossthosedistribution plates filters

发言人 4  01:28:28

嗯，那这个就是这个压差的降下降是。就是的期望是多少？故宫。哎，好的。咱们可能就是错，就是他那个最大错误是0.35，他压差下架的期望是多少？看这个比例关系吧，我感觉他是想看。

发言人 7  01:28:56

咱咱这个反应柱应该压压差不大，嗯，

发言人 4  01:29:00

不大是多少？

发言人 7  01:29:03

你。这个的话，得问一下研发具体的值，应按照那个目前情况来看，应该也就几十千帕吧。

发言人 4  01:29:13

几10千帕就换成bar是多少啊？就是几bar是吗？

发言人 7  01:29:19

零点几吧，不到

发言人 4  01:29:20

一半。不到一半是吧？

发言人 7  01:29:22

哦，对，不到。嗯。

发言人 4  01:29:25

Yeah, the accurate number may be given by the research group, but according to chaoqun, she estimated like less than one barThe differential will be

发言人 1  01:29:44

Yeah, that's that's where I amWe've got it's just making it clear to peopleButThe way we'veThe way we've designed the system, we could have half bar error on the calibration

发言人 1  01:30:05

And we're trying to measurehalf a bar differentialSo it'sIt's good forInformation, so if one of them is blinded, you'll see it having a high reading, but it's not an exact

发言人 1  01:30:29

Reading, yeah, the calibration error is large in comparison to what you're trying to measureUmSo it's just making sure people are aware of that

发言人 1  01:30:43

In terms of calibrationumHow how do you do the calibrationsBecause if you take the instrument off and do a calibration on the bench,

发言人 1  01:30:58

when you refit it back to the part work and you talk it up slightly differently, Chances are you'll introduce errors on the reading that way

发言人 1  01:31:09

you never gonnaget your point oneOr point two five percent accuracy, if you've taken it off to calibrate and put it back onumI was just wondering whether

发言人 1  01:31:27

whether weWe do calibrations with themon the equipment

发言人 4  01:31:36

嗯，

发言人 1  01:31:37

对，但是说。Lost my mouse, Peter. The world is. yeah

发言人 4  01:31:53

Yeah, I I I got your idea and I can transfer to Chaoqun and let's see what what she thinks

发言人 1  01:32:02

叶秀，

发言人 4  01:32:02

嗯，他主要两个疑问，一个是这样的话，就相当于是你误差是半半，然后你要测一个半半的东西。然而这个等于就是靠谱性就不是特别大。然后另外一个就是说你怎么做这个校准啊，你如果把它拆下来校准，可能你永远就达不到这个0.2。0.1跟0.25，然后这个那啥，然后所以你就可能是需要在把它安装上的时候，在它在上面的时候就做校准。

发言人 4  01:32:36

是吗？还是怎么样的呀？

发言人 7  01:32:40

那个，因为这个压差确实精度不太够，所以我想的是那个用压力的那个连锁，嗯，用压力的那个静压呢，它的精度应该是够的。

发言人 4  01:32:53

呃，这、这个，您详细解释一下，我这个不太懂。就是压力，他那个是就是有什么仪器，然后怎么测之类的。还是

发言人 7  01:33:04

不是压力？那压力那个精度不是0.25%。

发言人 4  01:33:09

嗯。然后呢。

发言人 7  01:33:13

0.25%不就是25千帕。

发言人 4  01:33:16

对。

发言人 7  01:33:18

那可能就是比插压的那个精度稍微强一点。他不是两个姐吗？还有两个表，

发言人 4  01:33:28

嗯。那不是，

发言人 7  01:33:30

这不是稍微那

发言人 4  01:33:31

25、25千帕，那你半坝跟25千帕不是也是2:1的关系，你你你测一个，比如说你测一个半坝的东西，然后你那个误差0是0.25吧，然后你，那你这不是你这个参考意义也没有那么大呀。就对，

发言人 7  01:33:51

但是如果你是他，不是怕堵了吗？你要是堵了，那个压差就会很大。嗯，咱正常的情况下，咱正常情况下那个压差是很小的，就是如果通道是。通道没有堵的话，压差比较小，咱说的都比较小的，就是正常供放的。你要是堵了的话，那个压差就会大了。

发言人 4  01:34:12

哦，这这个意思。哎，超军，

发言人 5  01:34:14

对，补充一下那个40千帕最大差压误差大约40千帕，这个是怎么来的呀？

发言人 4  01:34:20

这刚才已经讨论过了。高

发言人 5  01:34:21

宇高宇在吗？已经

发言人 4  01:34:23

已经已经给他解释完了，加起来35000多。这个已经解解释完了。所以所以实际上我们要测的不是那个正常情况，我们是需要他测的是他异常情况，异常情况的话它会比较大。对，逻辑是这样的，我们就是他正常情况下，那个读数对于我们来说没有意义，我们只要知道他不堵就行，是吧？

发言人 7  01:34:47

对，因为那个差呀，本来误差就比较大，就怕它正常情况下它都会有误报啥的。呃，

发言人 4  01:34:53

就是误报说正常情况下误报成。这个比如说你正常情况下的阈值是0.5然后你误报成一个一。嗯。这样的。

发言人 7  01:35:02

对对对，但嗯。

发言人 4  01:35:04

但是那你那个就异常情况下会是多大呀？

发言人 7  01:35:08

异常情况下的话，看堵多少，堵堵的比较比较严重的话，应该挺大的，几半儿应该都有。

发言人 4  01:35:15

几半儿，然后那就是普通的异常情况，那是多少呢？你比如说23、两三瓣儿的话，我觉得你差个0.0.5，然后它本身是0.5，那那我也可以接受，是不是？

发言人 7  01:35:33

这个这个堵的话，

发言人 4  01:35:35

嗯。

发言人 7  01:35:37

补的工况的话，没没测过那个压力值呢。

发言人 4  01:35:41

啊，没有测过。

发言人 7  01:35:43

哦。

发言人 4  01:35:46

嗯，那这这这个这个会我跟他说一下，然后另外一个问题就是你怎么校准？你如果拿下校准的话，他认为你就达不到那个精度0.1跟0.25嘛。那你就是放在上面校准吗？

发言人 7  01:36:02

高远，这个校准咋整啊？

发言人 3  01:36:06

校准，

发言人 7  01:36:07

嗯。

发言人 3  01:36:13

这个我还真不太清楚，这个在线校准。

发言人 4  01:36:18

嗯，就那这个教主，咱们得了解一下，是不是拿下来就没那么准，还是说拿下来也准，然后还是怎么样的？

发言人 3  01:36:27

嗯，拿下来就是这个这个精度，一般是出厂经过检验的。嗯嗯，出厂有检验的，而且还会有第三方检验认证的。嗯，如果是怀疑他的话，就是可以摘摘拿下来再去进行检检验就。就是就是自己是没法现场没法那个进行校准的。那他一般是进行。

发言人 4  01:36:55

不是几年一校准的吗？难道他就是一用用用一辈子的是东西啊。

发言人 3  01:37:01

呃，就是拆下来，每年年检的时候，嗯，就就是去到，嗯，去上检验台去校准这个东西的。

发言人 4  01:37:09

啊，那就在校检验台校准的话，它是。

发言人 3  01:37:15

呃，在第三方，呃，不是不是，

发言人 4  01:37:17

我就说在检验台校准，它那个再回到再安上去的时候，它不会影响它的精度，是不是？

发言人 3  01:37:24

啊，对，不会就校准完了，然后再安上，就是就是精度是能保保证的，而且刚出厂的时候精度也是能保证，可能就是使用段时间，每年要就是有年检，然后去去校准。OK，

发言人 4  01:37:37

这个这个这个您确定，然后我就这么回了。

发言人 3  01:37:42

嗯，对，可以。这个基本咱们现在使用的也是这个，跟就是在使用前都得去再校一次准行。嗯，然后一旦安装上以后，你就。没法校准，没有在线教。

发言人 4  01:37:56

呃，OK行，那我这么回答一下。Hi, kissYeah, I asked the Chaoqun and Gao Yu em about these two em concerns. And for the first one em its actually if the em if its not blocked em the.

发言人 4  01:38:17

The pressure differential could be like half bar or less than one bar, and the accuracy, the arrow maybe half barAnd if it's blocked, which we may want to detect this one, well, increase the pressure differential to several bars

发言人 4  01:38:40

We are not quite sure about how we haven't do the experimentAbout how many bars, but according to Zhao Qun, it well goes to several bars. So the if there are some block scenarios happens, we can.

发言人 4  01:39:00

Uh, detect them, uh, by the, uh, by the, the, uh, the differential pressure monitoring, uh, even though it's like half bars, uh, arrow, but the half bar arrow will influence what is well

发言人 4  01:39:16

Giving us some like false notice, like it's not blocked, but we thought it's blockedKind of like this one false alert, kind of like this fake alert, something like that

发言人 4  01:39:34

And so, but if, because we are not, we haven't do some experiment on what the normal block will increase the pressure too. So if its going to several bars,i dont think they are well be.

发言人 4  01:39:54

Much uh fake fake alertAnd for the second question about how we do the calibration, I asked Gao Yu and it's when they are before they are shipping to the plant

发言人 4  01:40:14

They will do the calculate and after it's not necessary to do it. Actually, we cannot do the online calibration. It must be taking out and going to.

发言人 4  01:40:28

The party wonder and on the uh calibration uh equipment uh and or table and to to do do the calibration but uh it won't influence the accuracy after we

发言人 4  01:40:43

put it backLike it's kind of like annual, annually calibration

发言人 1  01:40:55

umah ah struggle that you getThat that level of accuracy if you take the transmitter off and refit it andEspecially the ones with the the diaphragm seals, the pressure pads

发言人 1  01:41:25

It were going into the reactorsThat's that's just one of theCan you not do the calibration in situIf you could pressure up the system to accept pressure

发言人 1  01:41:46

You could use that to calibrate your or to check stroke span your operating range

发言人 4  01:41:57

yeah ah

发言人 1  01:42:00

Then you don't have to worry about leaks because you haven't taken it off and you haven't refitted it, so you don't have to check for leaks

发言人 1  01:42:07

And then do your helium leak test

发言人 4  01:42:14

Yeah呃，他说那个，他觉得他他比较难，很难相信说这种东西，因为他这是带隔膜的，然后带这种压垫片的，然后你再重新安装的时候。他安的特别好，然后不会这个有这个泄露啥的。所以就是他因为0.25%这相当好的精度嘛，所以他觉得这个很难相信他还能就是你把它拆了再安，还能达到这个精度。

发言人 4  01:42:47

然后他说：“是不是在系统上直接给他加压，然后就能做校准？这样的话，就不用不会担心各种就是拆了装的线路问题。呃，高工。嗯，

发言人 3  01:43:12

系统上加压校准。

发言人 4  01:43:14

嗯，对，我没没听，我我也没听懂他到底是怎么校准的，但他的意思就是说不拆校准那种感觉。嗯。他他意思说他这个不是有隔膜的，小雨。那个那啥。

发言人 5  01:43:26

哎，那个李波，就是高宇，这个校准是不是有什么规定啊，规范制度啊？

发言人 4  01:43:34

对我这个，

发言人 5  01:43:35

我就是程序方面的。

发言人 4  01:43:37

主要校准应该这个

发言人 5  01:43:38

方面校准

发言人 4  01:43:39

标准化的东西吧。

发言人 3  01:43:41

对，校准一般像我们这校准就是嗯，去到第三方检验去校校准。对呀，

发言人 5  01:43:48

你不是自己弄的。

发言人 3  01:43:50

嗯，对自己弄的总有误差，那你你的你的那个。你的你的你的误差会很大，就是他们有精密仪器的这个校准。

发言人 4  01:44:00

对，我我也不太懂。

发言人 3  01:44:03

起看的话也判断不出来到底准不准，要自己搞自己弄。的话，我也想象不到怎么自己交，嗯，不太了解这个，自己太小。

发言人 4  01:44:15

yeah so uh according to gao yu the china team uh doing the collaboration is all uhtaking them to the third party, so we don't do it ourselves, so we don't have this kind of experience on that

发言人 4  01:44:31

What, what we do is, uh, let the, uh, third party to handle itSo, ah, ah, but ahWe we are lack of experience on that. How we do the calibration online, were doing it by ourselves.

发言人 1  01:44:53

Okay.

发言人 4  01:44:54

Yeah.

发言人 1  01:45:05

对那。I think really all this one is is tothe sideAt low differentials, the reading, the calibration error will be significantbut at higher pressures indicating blockage

发言人 1  01:45:28

UmThe calibration error is is acceptable and then close it out

发言人 4  01:45:37

yeahYes, it's what I was thinking嗯，可以。就是觉得，就可能就是说，你说那个。就是它正常工况下，它这个误差会比较大，但是在这种我们需要检测的这种异常的这种。嗯，堵塞的情况下，它还是就是可以接受的。这个误差等于它不会影响我们检测堵塞。

发言人 4  01:46:26

然后就

发言人 7  01:46:27

把它关了，

发言人 4  01:46:28

然后就把它关了，就这种的状态吧，也只能这么搞了。

发言人 7  01:46:35

因为正常压差太小了，确实确实有误差。对

发言人 4  01:46:39

对嗯嗯yeah i just transfer to chaoqunYeahThanks。So, uh, should we close it now or, uh, hold it

发言人 1  01:46:55

Ah well, you close it, that's fine.

发言人 4  01:46:57

Okay, thanks. 那这这个就关了吧，啊，他的意思是说。好的。

发言人 7  01:47:09

那就往下走，嗯，下面呢。

发言人 4  01:47:12

呃，有点晚了，我们加加速，然后如果小的问题，我们能自己就就解决，解决大的问题呗。

发言人 7  01:47:21

嗯，就这个。这个赵工是昨天说要沟通啥来着？

发言人 4  01:47:29

哦，不提的，那

发言人 6  01:47:30

提示一下就行。行，

发言人 4  01:47:31

哦耶，这里

发言人 6  01:47:32

不是你不是咱们给case发邮件了吗？我记得

发言人 4  01:47:34

我记得这个我说吧，哦，yeah，about the step，呃。This one, I sent you an email about asking about the size of the step, but we haven't got the response.

发言人 4  01:47:50

We may need this one, the step size. Uh, for for the three D layout, maybe

发言人 1  01:48:00

yeah nowI've forgotten that one Peter sorry I'll send that on. Okay

发言人 4  01:48:05

thanks. 然后，下一个呢？

发言人 7  01:48:10

价格好像是那个赵工是说垫片

发言人 4  01:48:13

是吧？嗯，对我想想，

发言人 6  01:48:14

对那个金属金金属垫片嗯，316R换成铜的嗯，

发言人 4  01:48:19

OK行。The next one is about the gasket material, sothisUh, the previously we are choosing the 3316L, uh, and the it's now the the temperature is 270 centigrade and seven

发言人 4  01:48:42

Three, uh, seven point five, uh, megapar, Pascal, and theUh, we are thinking there, uh, the the the ceiling may be unreliable, so we are proposing to

发言人 4  01:48:58

Uh, uh, uh, uh, uh, this similar metal gasket, for example, CooperTo secure the sale

发言人 1  01:49:14

Um, you got corrosion issues there, haven't you

发言人 4  01:49:19

呃，但铜的话，是不是有这个腐蚀的问题啊？

发言人 6  01:49:26

嗯，查了一下，已穿已止应该是可以的。

发言人 4  01:49:30

Yeah, we searched on the the the the the the servant the S T what is calledIt's not, uh, won't, uh, corrupt Cooper the, uh, the server system we choose

发言人 1  01:49:49

But our our system isn't just the solvent, the solvent is the bulk of the material, but we doI saidSo it's in therethe actual material that we're processing is in the solvent.

发言人 4  01:50:06

okay. that

发言人 1  01:50:07

will be corrosive.

发言人 4  01:50:09

他说咱们的原材料可能是酸的，然后就有腐蚀性。但咱们那个溶剂是乙酸乙酯，但是它这个原材料是溶于这种乙酸乙酯的呗。

发言人 6  01:50:25

这个是啊，你那样的话，嗯，垫片用316l的，然后法兰也是316l的，它俩是同材质的，没有硬度差。就不容易密封

发言人 4  01:50:38

哦。Yeah, the the the real problem is the the gasket is 3316 l and also the the french is also 316 l and so there is no differential on the

发言人 4  01:50:53

uhOn the em what is called, let me check the hardness difference. There is no differential on the hardness, so its hard to. 笑。To form a reliable seal according to

发言人 1  01:51:16

So what are they suggestingIs it just copper?

发言人 4  01:51:21

除除了铜以外，咱们还有什么想想法吗？

发言人 6  01:51:26

嗯，我之前查了镍、铝这些都不行，对乙酸乙酯都有腐蚀，它要是酸的话呢，更不好弄。

发言人 4  01:51:36

Okay，yeah。呃。And the ziliang did some research and the other materials even it could be copied by thethetheLike, uh, he, he, he researched the, uh, nickel and aluminum

发言人 1  01:52:15

嗯。

发言人 4  01:52:16

那等于就是两个316L不太行，是吧？

发言人 6  01:52:21

对，他俩是同材质的，嗯，而且压力这么高。它容易密封，密封不出的。

发言人 4  01:52:36

The most concern is as the pressure is high and we are, if we are using the same material forUh, the French and the gasket, the seal may be not that good

发言人 1  01:52:57

Yeah, it needs to be good because it's hydrogen and it will find the smallest of gaps.

发言人 4  01:53:02

Yeah.

发言人 1  01:53:08

And that's kind of one of the reasons why in the calibrations we don't want to take the transmitters off becausetrying to get them to reseal is not going to be easy

发言人 4  01:53:18

yeah这也是说，这种密封确实比较重要，然后，而且这也是当时说那个，我们就是做做这种那个校准的时候，也不想把它给拿下来，因为这个再做密封真的非常麻烦。因为它毕竟涉及氢气嘛。

发言人 6  01:53:39

是的，是的，所以所以这个事情是比较麻烦的一个事儿。哎，他这个设计温度要是降到200度，能好像不行是吧？超全当时说这个。

发言人 7  01:53:53

剩余温度200的话，是那个对罐来说可以的，就是咱只是卸放的时候温度比较高。

发言人 4  01:54:02

正常

发言人 7  01:54:03

用的情况下。

发言人 6  01:54:07

200的话，这不是还选那个P D F E嘛，就是316L缠绕垫，316L包覆这个这个这个P D F

发言人 4  01:54:17

E。I think the key limit is about the temperature. Our design temperature actually, the normal operation temperature is200.Centigrade, if we are doing this one as the design temperature, then we can use the PTFE. But we actually said the.

发言人 4  01:54:41

Temperature as the the relief temperature, the maximum temperature that will reach when we are doing the relief is 270, so that it will

发言人 4  01:54:54

Exclude the P T F EMaterial

发言人 1  01:55:03

Yeah, and that doesn'tThat doesn't work because you can'tAssume you're going to get a relief at two hundred and seventy degrees C and then allow your gaskets to fail before that temperature

发言人 4  01:55:16

yeah

发言人 1  01:55:18

So we need to holdWhole temperature and pressure up to the full relief conditions

发言人 4  01:55:28

嗯，我尝试说服他失败了。那个，他说：“这个，你这个材料必须得能够坚持到这个。你这个整体的这个西方条件下。但是说不能说这个还没，哎，赵工，还，李波，嗯，那您说。嗯，

发言人 5  01:55:48

对，哎，赵工，那个有那个耐腐蚀的那个哈C啊什么的材料，金属垫吗？这个硬度差，有差别吗？

发言人 6  01:55:56

他比3162更更差的。更硬。

发言人 5  01:56:00

嗯，更硬的是吧？对。应该找一个软的是吧？它夹着。对。哎，咱们这个材料主体材料是带L的是吧？

发言人 4  01:56:08

是。

发言人 5  01:56:09

哦，不带L的硬点，我记得带L的软点。那就选了那个耐腐蚀的，更更硬，就不适合。

发言人 6  01:56:20

对，选垫片得软，按理说

发言人 5  01:56:23

嗯是，但是也。也有耐腐蚀的垫片，就是它适用的主体材料也是硬的。

发言人 6  01:56:36

嗯，是嗯。是什么呢？

发言人 5  01:56:41

就按照你刚才的理解说，意思是吧？

发言人 6  01:56:46

我的意思是，是这个垫片啊。这个基础这个环嘛，它不是。嗯。

发言人 5  01:56:53

嗯，这个环。啊

发言人 6  01:56:55

对，它这种

发言人 5  01:56:55

硬度硬度比那个法兰的软点，咱现在是316L的，对吧？

发言人 6  01:57:00

对，它俩是相同的。嗯，

发言人 4  01:57:02

那法兰用那个哈C，然后那个哈氏合金，然后那个。

发言人 5  01:57:06

那就贵

发言人 4  01:57:07

了。就太贵了是吧？哦，我以为法兰。对。

发言人 5  01:57:10

你法兰对那个焊接那个什么那个主体就贵多了，

发言人 4  01:57:14

那个。那贵多了，那没办法，那不太行。对对

发言人 5  01:57:16

对对。嗯，

发言人 4  01:57:17

我以为法兰没那么大呢。嗯，

发言人 5  01:57:19

呃，不是法兰，你管道连接设备不好的。

发言人 6  01:57:23

嗯，对。

发言人 4  01:57:25

Yeah

发言人 6  01:57:28

因为咱们这里头好多这种涉及到高压的，都是涉及到这个问题。嗯。气液分离器呀，还有那几个反应柱子，高压

发言人 4  01:57:38

的。嗯，

发言人 6  01:57:40

不，不是不是，不不单单是主体这个，你和那个管道上连接的。也存在这个问题啊，嗯。他这不是有法兰跟法兰盖吗？

发言人 4  01:57:54

对。

发言人 6  01:57:56

除了这道口之外，还有就是像进出口，嗯，它不有法兰的嘛，就虽然进出口好像有那个，呃，你看切分离器里头不是有那个液液位计口吗？嗯。他在连接的时候，那个密封垫。也也也是个问题，他们是问题都是相同的。所以这个垫片这个事情是。Faith比较难弄。还得抗腐蚀。白的软。

发言人 5  01:58:47

叫什么蒙代尔？那个行吗？

发言人 6  01:58:51

冯戴尔也不行，我查了。你也得我也查了。

发言人 4  01:59:03

都有腐蚀性问题，都是乙酸乙酯就腐蚀是吧？

发言人 6  01:59:06

对对对，当时还没说有酸的事儿呢，你这有酸的话还得看什么酸啊。

发言人 4  01:59:12

那那刚。这个

发言人 5  01:59:13

东西太难了，就是适合的话。嗯。

发言人 2  01:59:18

我是说那个

发言人 3  01:59:20

密封圈，那个rt沟那个

发言人 4  01:59:22

中间环儿，

发言人 5  01:59:23

哎，对，金属环垫片那个，嗯。

发言人 1  01:59:28

那个金属的

发言人 4  01:59:28

不行，现在是。

发言人 6  01:59:30

不，现在是找不到合适的金属环垫片。

发言人 4  01:59:35

那个温度、压力，那个

发言人 1  01:59:37

PEK的项目。

发言人 4  01:59:39

如果是。

发言人 6  01:59:40

PEK是什么？匹克啊？

发言人 4  01:59:44

这个能耐

发言人 2  01:59:45

高温，压力

发言人 1  01:59:47

好像也。谁。

发言人 6  01:59:49

匹克应该不容易变形啊。他是应该是一个很硬的一个东西啊。

发言人 3  01:59:58

一般之前

发言人 4  01:59:59

我们做做那个密封，经常用这个。

发言人 3  02:00:02

如果是高温

发言人 4  02:00:03

高压的，用pek的。如果是软密封，它

发言人 1  02:00:06

也能，它

发言人 4  02:00:06

也算软密封的一种。

发言人 1  02:00:10

就是居民尼童。

发言人 5  02:00:14

那我下来，我们查一下它的硬度，对比一下。

发言人 6  02:00:18

行，可以，嗯。

发言人 5  02:00:22

匹克，呃，匹克对。

发言人 6  02:00:25

P E E K吧，还是P E K呀，

发言人 4  02:00:27

E E两个E W E。也是我，

发言人 7  02:00:32

我给你。

发言人 6  02:00:34

是啊，那不匹克吗？那匹克。

发言人 4  02:00:36

嗯。

发言人 6  02:00:42

对呀，那那那非常硬的一个东西，它怎么能作为垫片来用呢？

发言人 1  02:00:49

电票。好。

发言人 3  02:00:54

好像确实是用的比较少，一般以前。

发言人 6  02:00:56

他不是泵上的这个好多匹克的，那不是耐磨的吗？

发言人 4  02:01:00

填料的时候用。

发言人 6  02:01:08

我我感觉不太行。匹

发言人 4  02:01:09

克是远远低于那个311L，它还是一个那种。那种那个那啥就是塑料，相当于然后这个316L能轻松划伤匹克。然后，但是匹克抗压耐高温很好，属于软质密封，但属于软质密封，高压下发生微量塑形变形，不是金属对金属的硬密封。

发言人 6  02:01:42

因为这里头啊，不单单是他平常运行，还有一个还捡漏呢。这个氦检漏它也是非常厉害的一种，就是渗透检测的一种方式。你但凡密封不住一点儿，它就检测出来了。

发言人 4  02:02:00

那把这些那个工况说出来，然后让AI帮我们查一查吧，看看AI

发言人 6  02:02:06

是不是。行行。下面咱们再再找找吧。行。再找找吧，然后和和case也说一下，看看他们那边有没有什么

发言人 4  02:02:14

好的建议。他估计现在就在找。那那个呃呃，超群帮我看一下后头还有多少啊？

发言人 5  02:02:24

那没了就一个了，就

发言人 7  02:02:26

就一个了。嗯。

发言人 4  02:02:28

就一个FAT那个啊那个就说一下就行啊。

发言人 7  02:02:32

对，行，其他没了。

发言人 4  02:02:33

行，那我跟他说一下吧，然后这时间也差不太多，咱们赶快结束了得。

发言人 7  02:02:39

因为。行，那就直接过到这条了是吧？嗯，

发言人 4  02:02:42

行，我跟他。

发言人 7  02:02:42

还是这个还是

发言人 4  02:02:43

再说一下。对我跟他说一下也。嗯，行。yeah hi guys

发言人 1  02:02:49

Yeah,

发言人 4  02:02:49

we we have several discussions on potential materials, but haven't found a good one. We are going to doing more search on that and.

发言人 4  02:03:02

In the meantime, could you also have us if you can have if you have any ideas, just let us knowAnd we can figure it out

发言人 1  02:03:15

YeahI think we we need to go to a specialist company becauseYeah. Were at the limit of what were trying to achieve with the materials. Weve got pressure cycling which is not gonna.

发言人 1  02:03:30

make life easy for thethe gasket

发言人 4  02:03:35

嗯。

发言人 1  02:03:37

Um, yeah, that's that'sReally need to talk to somebody who specializes in thisOtherwise, we're going to put something in that

发言人 1  02:03:49

Either leaks oror doesn't meet the requirements

发言人 4  02:03:55

yeah

发言人 1  02:04:01

Yeah, I'm not sure we got that experience in the room

发言人 4  02:04:07

yeahYeah, we are trying to find some specialist from the China side as well. And we are trying to search online for the typical normal.

发言人 4  02:04:25

Materials but, uh, Currently there, uh, nothing matched, but we, we, we will, uh, do our effort, uh, after the meeting and to see what we got

发言人 1  02:04:41

Okay, um, calrez is another material that we useIt's corrosion resistantBut again, I don't think it does high temperature, high pressure

发言人 4  02:04:55

YeahOkay, butThanks, uh, I think we cannot, uh, solve it, uh, for now, but we will keep, keep on working on that他呃，刚才他说了一个叫“kalrz”（kalrz）的一种材料，但这个东西 K A L R Z R E Z的一种材料，但这个东西可能不太耐高温高压，它的这个。

发言人 4  02:05:27

这个密封还是够的啊，那个反正我们下去再找找专家，然后或者看看其他的方式再搞一下，然后再跟他讨论吧。Okay, I think last one is just a lie, the question, but it's not the currentUh, stages for the next stage, uh, is raised by, uh, Claire from last Wednesday, and he is think she, she was thinking about the F A T

发言人 4  02:06:07

How do we do the FTT? Who will prepare? Who will send off? And she thinks this one need to be. Giving some salt on from the current stage, but this next stage thing and so to do have any ideas on this. And if we were thinking that we can use the.

发言人 4  02:06:37

Uk template and the china team will provide the information needed and but the template and the procedure we will follow the uk's

发言人 4  02:06:49

standardWhat do you think

发言人 1  02:06:54

UmStraight off we don't do FATSTo have a template. Theyre always done by the external supplier. So we havent got anF8 template. If we were doing anF8 template,

发言人 1  02:07:13

It would look very similar to an IQOQ

发言人 4  02:07:18

嗯。

发言人 1  02:07:19

Um, umI'm not precious about the templateIt just needs to go throughWhat you'd expect to see in an IQOQdo as much testing as as you can

发言人 1  02:07:36

Before it ship, final connections are madeYou know, you can do all your material cert testing, your ATEX certYou can make sure the installation is um as per design or the equipment is as per design

发言人 4  02:07:52

Yeah

发言人 1  02:07:53

What what we will need to do that one of our procedures says thatIf we try to use some of the FAT to reduce the amount of IQ OQ testing we do on site, our QA need to pre-approve and sign it off

发言人 1  02:08:10

So on the FAT templateIf we could get one of our QA people to sign sign it off as and suitable for useThat will save usA lot of testing or repeat testing on site potentially

发言人 4  02:08:26

Okay, got it. So, uh,QA from the UK side, right?

发言人 1  02:08:31

YeahIt's it's not onerous. They just need to sign their life away. Okay.

发言人 4  02:08:44

Yeah, thanks. So we understand thatI think if thats so,

发言人 1  02:08:54

if we were there. We would take our normal IQOQ template, so you could use your IQOQ template and then just change it to FATAnd then go through it and see what

发言人 1  02:09:11

I'd imagine you could probably do ninety percent of the tests on the skid without it being installedSo if you, if you used one of your previous validation documents

发言人 1  02:09:24

Change the titleAnd then take out the tests that you can't do on this skid as a standalone unit

发言人 4  02:09:33

嗯。Okay，understand，thank you。就是咱们之前做这种的验证的这些东西，然后换个名字，然后把IQOQ变成这种FAD，然后那个他觉得90%的东西在不安装的情况下都能做测试了，然后。这种的情况，然后把这个东西给弄好，然后可能给到英国那边的QA、QA签个字，然后可能能节省很多一些重复的工作。

发言人 4  02:10:24

大体上，他说这些的思路跟流程吧，我觉得这是下阶段的事儿，咱们有个了解，有一个心理准备就行。呃，高主管，您这边什么想法？嗯嗯，

发言人 5  02:10:38

这个这个就您说的属于下阶段的事儿，就是我们嗯呃等于在前期做这个东西，就这个壳块的设计相当于工程化这块。呃，负责这块，这个下游的得可能，如果要需要配合，也得咱这边管生产这块的什么质量的人进来。再协助。对，如果是那样的话，对，按照冯博的意思说，也是现场那边的来做嘛。

发言人 4  02:11:08

行，

发言人 5  02:11:09

反正这个问题呢，你关闭不了，就是等我们到一定阶段还得，对，嗯，还得还得

发言人 4  02:11:14

再聊。yeah，嗯，uh，yeah，thanks for sharing，and i just transfer to shao feng and weWe think it's what we thought. We very agree with you and we are allied.

发言人 4  02:11:27

And so its mainly the next stage one that we can have some ideas thoughts being prepared. And yeah

发言人 1  02:11:37

Thanks. Yeah, sure. It makes it makes the sandwich site job easy because all we need to do is connect up utilities. and prove that the utilities

发言人 1  02:11:50

are what you required as part of the designUmSo if the skid has a good FAT, we just connect up utilities, prove we have the temperature ranges

发言人 1  02:12:02

And we can put it into beneficial use. Thatsa lot of time and thats where. if you test the skid as an assembly in china, and do the full document set

发言人 1  02:12:18

If it comes as modules and you have to disassemble it and then we have to reassemble itWe have to do a lot of repeat testingWhereas if you can ship it as one skid and we crane it in through the roof. Yeah.

发言人 1  02:12:33

We can use all of that testing and then we just need to check our servicesSo we can put it into use a lot quicker

发言人 4  02:12:41

Yeah, um,

发言人 1  02:12:42

um,

发言人 4  02:12:44

Is that the uh, a lot, uh, uh, a big part of the cost for the modular design? Uh, but not taking asa whole. Yeah, so this could be uh, in the family uh,

发言人 4  02:12:59

Giving to the head team to the to to make the decision whether we are using the host key

发言人 1  02:13:06

or yeah in the cost to design it as a modular unitThe additional steel work to support the modulesThe cost to disassemble it once you've finished testing, then we have to reassemble it, we'll have to reroute cables, reconnect bike work

发言人 1  02:13:25

Re-test it all and then carry out IQOQ again. Theres, theresa huge impact. onSandwich costs in time associated the modular design

发言人 1  02:13:41

AndBut then it's about a quarter of a million pounds to put the new roof on.

发言人 4  02:13:47

Yeah. Itsa trade off, but let let the we we can do the plan and let the high court. To make decision, yeah

发言人 1  02:13:58

Yeah, they get paid the big money.

发言人 4  02:14:00

Yeah. Okay，that's all from the China side，and thank you for your time. Sorry，its very late.

发言人 1  02:14:10

No, no, it's good. Its not late for me.

发言人 4  02:14:12

Okay, yeah.

发言人 1  02:14:14

Okay, thanksa lot, guys.

发言人 4  02:14:16

Thank you.

发言人 1  02:14:17

The speech is saying. Yeah,

发言人 4  02:14:19

see you soon. Bye. Bye. 呃呃，高主管，呃，胡工，呃，咱们大家这个我们就结束了，然后就下周二的时候再跟他这个继续做一些实实际上的这种的讨论。嗯，基本上都解决好的好的啊。那个材料问题，确实现在没就电

发言人 5  02:14:40

比较难。那个材料是

发言人 4  02:14:41

它操作

发言人 5  02:14:42

工况太苛刻了，对

发言人 4  02:14:44

270度有点夸张了。我刚才也搜了一些那个。就本身材料能选的就很少，就我感觉

发言人 5  02:14:51

他呃不止他不止温度的事，就是他温度还要就是他那个腐蚀不定，如果腐蚀定了，你比如说某种金属的那个赵工他可能也能选。就是溶剂，还有各种原料它。哎，就做成一个又又不能做成一个金疙瘩似的。你比就像那个你刚才建议那个，你比如说把那个法兰做成哈c的，然后垫片做302的，可以的，这这是可以的。

发言人 5  02:15:19

太贵了，然后那个东西哈飞那个特别贵，对，就是这个

发言人 4  02:15:23

哈飞我见过那个，我我我这个不太了解，但是我见过那哈飞的房，我一个都超出想象的贵。是

发言人 6  02:15:31

是特别贵的，贵到爆炸。你这个。