## Instrument Index
Blue Text = Instruments that do not have a new CAT Assessment yet Red Text and Greyed out Field = Instruments that have been deleted
Unit | Tag No | Loop Tag | Loc | P&ID | Description | Location/Line No | System No | Loop Service | Loop Calibration Tag | Range | Tolerance | Criticality Category | Freq (Mnths) | Cal/ Func | Cal Type | Haz Cert | PCS I/O | PCS I/O | PLC I/O | I/O Code | I/O Area | Manufacturer | Model | Datasheet Reference | IS Calculation Reference | Remarks | PLC I/O | Rev | Revision
B287 | B287-WS01-WE-001 | B287-W-001 | FLD | N/A | WEIGH SCALE - LOAD CELLS | B287 G04 |  | MOBILE SCALE |  | 0.04 to 15kg | +/- 0.04Kg | GxP | 12
B287 | B287-WS01-WI-001 | B287-W-001 | FLD | N/A | INDICATOR - WEIGH | B287 G04 |  | MOBILE SCALE |  | 0.04 to 15kg | +/- 0.04Kg | GxP | 12
B902 | B902-XA-002AAA | B902-X-002AA | FLD | C&E/693 | ALARM - AUDIBLE | GP1 SERV. VOID GND FLOOR | 083.2 | B.A. ALM. GP1 SERV. VOID GND FL | 8261 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002AAA | B902-X-002AA | FLD | C&E/693 | ALARM - BEACON | GP1 SERV. VOID GND FLOOR | 083.2 | B.A. ALM. GP1 SERV. VOID GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002AAB | B902-X-002AB | FLD | C&E/693 | ALARM - AUDIBLE | GP1 PROC. AREA GND FLOOR | 083.2 | B.A. ALM. GP1 PROCESS GND FL | 8262 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002AAB | B902-X-002AB | FLD | C&E/693 | ALARM - BEACON | GP1 PROC. AREA GND FLOOR | 083.2 | B.A. ALM. GP1 PROCESS GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002AAC | B902-X-002AC | FLD | C&E/693 | ALARM - AUDIBLE | GP1/2 SERV. VOID GND FL | 083.2 | B.A. ALM. GP1/2 SERV. VOID GND FL | 8263 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002AAC | B902-X-002AC | FLD | C&E/693 | ALARM - BEACON | GP1/2 SERV. VOID GND FL | 083.2 | B.A. ALM. GP1/2 SERV. VOID GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002AAD | B902-X-002AD | FLD | C&E/693 | ALARM - AUDIBLE | GP2 PROC. AREA GND FLOOR | 083.2 | B.A. ALM. GP2 PROCESS GND FL | 8264 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002AAD | B902-X-002AD | FLD | C&E/693 | ALARM - BEACON | GP2 PROC. AREA GND FLOOR | 083.2 | B.A. ALM. GP2 PROCESS GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002BAE | B902-X-002AE | FLD | C&E/693 | ALARM - AUDIBLE | GP2 SERV. VOID GND FLOOR | 083.2 | B.A. ALM. GP2 SERV. VOID GND FL | 8265 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002BAE | B902-X-002AE | FLD | C&E/693 | ALARM - BEACON | GP2 SERV. VOID GND FLOOR | 083.2 | B.A. ALM. GP2 SERV. VOID GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002BAF | B902-X-002AF | FLD | C&E/693 | ALARM - AUDIBLE | FG1 SERV. VOID GND FLOOR | 083.2 | B.A. ALM. FG1 SERV. VOID GND FL | 8266 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002BAF | B902-X-002AF | FLD | C&E/693 | ALARM - BEACON | FG1 SERV. VOID GND FLOOR | 083.2 | B.A. ALM. FG1 SERV. VOID GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002BAG | B902-X-002AG | FLD | C&E/693 | ALARM - AUDIBLE | FG1 PROC. AREA GND FLOOR | 083.2 | B.A. ALM. FG1 PROCESS GND FL | 8267 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002BAG | B902-X-002AG | FLD | C&E/693 | ALARM - BEACON | FG1 PROC. AREA GND FLOOR | 083.2 | B.A. ALM. FG1 PROCESS GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002BAH | B902-X-002AH | FLD | C&E/693 | ALARM - AUDIBLE | FG1/C1 SERV. VOID GND FL | 083.2 | B.A. ALM. FG1/C1 SERV. VOID GND FL | 8268 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002BAH | B902-X-002AH | FLD | C&E/693 | ALARM - BEACON | FG1/C1 SERV. VOID GND FL | 083.2 | B.A. ALM. FG1/C1 SERV. VOID GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002CAJ | B902-X-002AJ | FLD | C&E/693 | ALARM - AUDIBLE | C1 PROC. AREA GND FLOOR | 083.2 | B.A. ALM. C1 PROCESS GND FL | 8269 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002CAJ | B902-X-002AJ | FLD | C&E/693 | ALARM - BEACON | C1 PROC. AREA GND FLOOR | 083.2 | B.A. ALM. C1 PROCESS GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002CAK | B902-X-002AK | FLD | C&E/693 | ALARM - AUDIBLE | C1 SERV. VOID GND FLOOR | 083.2 | B.A. ALM. C1 SERV. VOID GND FL | 8270 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002CAK | B902-X-002AK | FLD | C&E/693 | ALARM - BEACON | C1 SERV. VOID GND FLOOR | 083.2 | B.A. ALM. C1 SERV. VOID GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002CAL | B902-X-002AL | FLD | C&E/693 | ALARM - AUDIBLE | GND FLOOR CORRIDOR | 083.2 | B.A. ALM. CORRIDOR GND FL | 8271 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002CAL | B902-X-002AL | FLD | C&E/693 | ALARM - BEACON | GND FLOOR CORRIDOR | 083.2 | B.A. ALM. CORRIDOR GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002DAM | B902-X-002AM | FLD | C&E/693 | ALARM - AUDIBLE | DISPENSARY GND FLOOR | 083.2 | B.A. ALM. DISPENSARY GND FL | 8272 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002DAM | B902-X-002AM | FLD | C&E/693 | ALARM - BEACON | DISPENSARY GND FLOOR | 083.2 | B.A. ALM. DISPENSARY GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002DAN | B902-X-002AN | FLD | C&E/693 | ALARM - AUDIBLE | MILL. & BLEND GND FLOOR | 083.2 | B.A. ALM. MILL & BLEND GND FL | 8273 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002DAN | B902-X-002AN | FLD | C&E/693 | ALARM - BEACON | MILL. & BLEND GND FLOOR | 083.2 | B.A. ALM. MILL & BLEND GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002DAP | B902-X-002AP | FLD | C&E/693 | ALARM - AUDIBLE | LIBC ROOM GND FLOOR | 083.2 | B.A. ALM. LIBC ROOM GND FL | 8274 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002DAP | B902-X-002AP | FLD | C&E/693 | ALARM - BEACON | LIBC ROOM GND FLOOR | 083.2 | B.A. ALM. LIBC ROOM GND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002EBA | B902-X-002BA | FLD | C&E/693 | ALARM - AUDIBLE | GP1 SERV. VOID 1ST FLOOR | 083.2 | B.A. ALM. GP1 SERV. VOID 1ST FL | 8275 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002EBA | B902-X-002BA | FLD | C&E/693 | ALARM - BEACON | GP1 SERV. VOID 1ST FLOOR | 083.2 | B.A. ALM. GP1 SERV. VOID 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002EBB | B902-X-002BB | FLD | C&E/693 | ALARM - AUDIBLE | GP1 PROC. AREA 1ST FLOOR | 083.2 | B.A. ALM. GP1 PROCESS 1ST FL | 8276 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002EBB | B902-X-002BB | FLD | C&E/693 | ALARM - BEACON | GP1 PROC. AREA 1ST FLOOR | 083.2 | B.A. ALM. GP1 PROCESS 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002EBC | B902-X-002BC | FLD | C&E/693 | ALARM - AUDIBLE | GP1/2 SERV. VOID 1ST FL | 083.2 | B.A. ALM. GP1/2 SERV. VOID 1ST FL | 8277 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002EBC | B902-X-002BC | FLD | C&E/693 | ALARM - BEACON | GP1/2 SERV. VOID 1ST FL | 083.2 | B.A. ALM. GP1/2 SERV. VOID 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002EBD | B902-X-002BD | FLD | C&E/693 | ALARM - AUDIBLE | GP2 PROC. AREA 1ST FLOOR | 083.2 | B.A. ALM. GP2 PROCESS 1ST FL | 8278 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002EBD | B902-X-002BD | FLD | C&E/693 | ALARM - BEACON | GP2 PROC. AREA 1ST FLOOR | 083.2 | B.A. ALM. GP2 PROCESS 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002FBE | B902-X-002BE | FLD | C&E/693 | ALARM - AUDIBLE | GP2 SERV. VOID 1ST FLOOR | 083.2 | B.A. ALM. GP2 SERV. VOID 1ST FL | 8279 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002FBE | B902-X-002BE | FLD | C&E/693 | ALARM - BEACON | GP2 SERV. VOID 1ST FLOOR | 083.2 | B.A. ALM. GP2 SERV. VOID 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002FBF | B902-X-002BF | FLD | C&E/693 | ALARM - AUDIBLE | FG1 SERV. VOID 1ST FLOOR | 083.2 | B.A. ALM. FG1 SERV. VOID 1ST FL | 8280 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002FBF | B902-X-002BF | FLD | C&E/693 | ALARM - BEACON | FG1 SERV. VOID 1ST FLOOR | 083.2 | B.A. ALM. FG1 SERV. VOID 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002FBG | B902-X-002BG | FLD | C&E/693 | ALARM - AUDIBLE | FG1 PROC. AREA 1ST FLOOR | 083.2 | B.A. ALM. FG1 PROCESS 1ST FL | 8281 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002FBG | B902-X-002BG | FLD | C&E/693 | ALARM - BEACON | FG1 PROC. AREA 1ST FLOOR | 083.2 | B.A. ALM. FG1 PROCESS 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002FBH | B902-X-002BH | FLD | C&E/693 | ALARM - AUDIBLE | FG1/C1 SERV. VOID 1ST FL | 083.2 | B.A. ALM. FG1/C1 SERV. VOID 1ST FL | 8282 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002FBH | B902-X-002BH | FLD | C&E/693 | ALARM - BEACON | FG1/C1 SERV. VOID 1ST FL | 083.2 | B.A. ALM. FG1/C1 SERV. VOID 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002GBJ | B902-X-002BJ | FLD | C&E/693 | ALARM - AUDIBLE | C1 PROC. AREA 1ST FLOOR | 083.2 | B.A. ALM. C1 PROCESS 1ST FL | 8283 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002GBJ | B902-X-002BJ | FLD | C&E/693 | ALARM - BEACON | C1 PROC. AREA 1ST FLOOR | 083.2 | B.A. ALM. C1 PROCESS 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002GBK | B902-X-002BK | FLD | C&E/693 | ALARM - AUDIBLE | C1 SERV. VOID 1ST FLOOR | 083.2 | B.A. ALM. C1 SERV. VOID 1ST FL | 8516 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002GBK | B902-X-002BK | FLD | C&E/693 | ALARM - BEACON | C1 SERV. VOID 1ST FLOOR | 083.2 | B.A. ALM. C1 SERV. VOID 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002GBL | B902-X-002BL | FLD | C&E/693 | ALARM - AUDIBLE | 1ST FLOOR CORRIDOR | 083.2 | B.A. ALM. CORRIDOR 1ST FL | 8517 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002GBL | B902-X-002BL | FLD | C&E/693 | ALARM - BEACON | 1ST FLOOR CORRIDOR | 083.2 | B.A. ALM. CORRIDOR 1ST FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002HCA | B902-X-002CA | FLD | C&E/693 | ALARM - AUDIBLE | GP1 SERV. VOID 2ND FLOOR | 083.2 | B.A. ALM. GP1 SERV. VOID 2ND FL | 8518 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002HCA | B902-X-002CA | FLD | C&E/693 | ALARM - BEACON | GP1 SERV. VOID 2ND FLOOR | 083.2 | B.A. ALM. GP1 SERV. VOID 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002HCB | B902-X-002CB | FLD | C&E/693 | ALARM - AUDIBLE | GP1 PROC. AREA 2ND FLOOR | 083.2 | B.A. ALM. GP1 PROCESS 2ND FL | 8519 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002HCB | B902-X-002CB | FLD | C&E/693 | ALARM - BEACON | GP1 PROC. AREA 2ND FLOOR | 083.2 | B.A. ALM. GP1 PROCESS 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002HCC | B902-X-002CC | FLD | C&E/693 | ALARM - AUDIBLE | GP1/2 SERV. VOID 2ND FL | 083.2 | B.A. ALM. GP1/2 SERV. VOID 2ND FL | 8520 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002HCC | B902-X-002CC | FLD | C&E/693 | ALARM - BEACON | GP1/2 SERV. VOID 2ND FL | 083.2 | B.A. ALM. GP1/2 SERV. VOID 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002HCD | B902-X-002CD | FLD | C&E/693 | ALARM - AUDIBLE | GP2 PROC. AREA 2ND FLOOR | 083.2 | B.A. ALM. GP2 PROCESS 2ND FL | 8521 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002HCD | B902-X-002CD | FLD | C&E/693 | ALARM - BEACON | GP2 PROC. AREA 2ND FLOOR | 083.2 | B.A. ALM. GP2 PROCESS 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002JCE | B902-X-002CE | FLD | C&E/693 | ALARM - AUDIBLE | GP2 SERV. VOID 2ND FLOOR | 083.2 | B.A. ALM. GP2 SERV. VOID 2ND FL | 8522 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002JCE | B902-X-002CE | FLD | C&E/693 | ALARM - BEACON | GP2 SERV. VOID 2ND FLOOR | 083.2 | B.A. ALM. GP2 SERV. VOID 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002JCF | B902-X-002CF | FLD | C&E/693 | ALARM - AUDIBLE | FG1 SERV. VOID 2ND FLOOR | 083.2 | B.A. ALM. FG1 SERV. VOID 2ND FL | 8523 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002JCF | B902-X-002CF | FLD | C&E/693 | ALARM - BEACON | FG1 SERV. VOID 2ND FLOOR | 083.2 | B.A. ALM. FG1 SERV. VOID 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002JCG | B902-X-002CG | FLD | C&E/693 | ALARM - AUDIBLE | FG1 PROC. AREA 2ND FLOOR | 083.2 | B.A. ALM. FG1 PROCESS 2ND FL | 8524 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002JCG | B902-X-002CG | FLD | C&E/693 | ALARM - BEACON | FG1 PROC. AREA 2ND FLOOR | 083.2 | B.A. ALM. FG1 PROCESS 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002JCH | B902-X-002CH | FLD | C&E/693 | ALARM - AUDIBLE | FG1/C1 SERV. VOID 2ND FL | 083.2 | B.A. ALM. FG1/C1 SERV. VOID 2ND FL | 8525 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002JCH | B902-X-002CH | FLD | C&E/693 | ALARM - BEACON | FG1/C1 SERV. VOID 2ND FL | 083.2 | B.A. ALM. FG1/C1 SERV. VOID 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002KCJ | B902-X-002CJ | FLD | C&E/693 | ALARM - AUDIBLE | C1 PROC. AREA 2ND FLOOR | 083.2 | B.A. ALM. C1 PROCESS 2ND FL | 8526 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002KCJ | B902-X-002CJ | FLD | C&E/693 | ALARM - BEACON | C1 PROC. AREA 2ND FLOOR | 083.2 | B.A. ALM. C1 PROCESS 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002KCK | B902-X-002CK | FLD | C&E/693 | ALARM - AUDIBLE | C1 SERV. VOID 2ND FLOOR | 083.2 | B.A. ALM. C1 SERV. VOID 2ND FL | 8527 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002KCK | B902-X-002CK | FLD | C&E/693 | ALARM - BEACON | C1 SERV. VOID 2ND FLOOR | 083.2 | B.A. ALM. C1 SERV. VOID 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002KCL | B902-X-002CL | FLD | C&E/693 | ALARM - AUDIBLE | 2ND FLOOR CORRIDOR | 083.2 | B.A. ALM. CORRIDOR 2ND FL | 8528 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002KCL | B902-X-002CL | FLD | C&E/693 | ALARM - BEACON | 2ND FLOOR CORRIDOR | 083.2 | B.A. ALM. CORRIDOR 2ND FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002KCM | B902-X-002CM | CCR | C&E/693 | ALARM - AUDIBLE | CONTROL ROOM | 083.2 | B.A. ALM. CONTROL ROOM | 8529 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 42 | SGS | [6 empty] | 01
B902 | B902-XA-002LDA | B902-X-002DA | HCR | C&E/693 | ALARM - AUDIBLE | HYDROG. CONTROL ROOM | 083.2 | B.A. ALM. HYDROG CONTROL ROOM | 8530 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24C |  | TI702-SP-5081 |  |  | 01
B902 | B902-XA-002LDB | B902-X-002DB | FLD | C&E/693 | ALARM - AUDIBLE | HYDROG. PROCESS AREA | 083.2 | B.A. ALM. HYDROG PROCESS | 8531 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24C |  | TI702-SP-5081 |  |  | 01
B902 | B902-XL-002LDB | B902-X-002DB | FLD | C&E/693 | ALARM - BEACON | HYDROG. PROCESS AREA | 083.2 | B.A. ALM. HYDROG PROCESS |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002LDD | B902-X-002DD | FLD | C&E/693 | ALARM - AUDIBLE | ADJ TO SC03 | 083.2 | B.A. ALM. SCRUBBER SC03 3RD FL | 8532 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
B902 | B902-XL-002LDD | B902-X-002DD | FLD | C&E/693 | ALARM - BEACON | ADJ TO SC03 | 083.2 | B.A. ALM. SCRUBBER SC03 3RD FL |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
B902 | B902-XA-002MEA | B902-X-002EA | FLD | C&E/693 | ALARM - AUDIBLE | ADJ TO ST01 & ST02 | 083.2 | B.A. ALM. SOLVENT WASTE TANKS | 8533 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5093 |  |  | 01
B902 | B902-XL-002MEA | B902-X-002EA | FLD | C&E/693 | ALARM - BEACON | ADJ TO ST01 & ST02 | 083.2 | B.A. ALM. SOLVENT WASTE TANKS |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5092 |  |  | 01
B902 | B902-XA-002MEB | B902-X-002EB | FLD | C&E/693 | ALARM - AUDIBLE | ADJ TO SC01, SC02 & SC04 | 083.2 | B.A. ALM. SCRUBBERS SC01/2/4 | 8534 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B-D |  | TI702-SP-5094 |  |  | 01
B902 | B902-XL-002MEB | B902-X-002EB | FLD | C&E/693 | ALARM - BEACON | ADJ TO SC01, SC02 & SC04 | 083.2 | B.A. ALM. SCRUBBERS SC01/2/4 |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5092 |  |  | 01
B902 | B902-XA-002MEC | B902-X-002EC | FLD | C&E/693 | ALARM - AUDIBLE | ADJ TO TT01, TT02 & TT03 | 083.2 | B.A. ALM. TEST TANKS | 8535 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B-D |  | TI702-SP-5094 |  |  | 01
B902 | B902-XL-002MEC | B902-X-002EC | FLD | C&E/693 | ALARM - BEACON | ADJ TO TT01, TT02 & TT03 | 083.2 | B.A. ALM. TEST TANKS |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5092 |  |  | 01
B902 | B902-XA-002MED | B902-X-002ED | FLD | C&E/693 | ALARM - AUDIBLE | ADJ TO ET01 & ET02 | 083.2 | B.A. ALM. AQUEOUS EFFLUENT PIT | 8536 | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5093 |  |  | 01
B902 | B902-XL-002MED | B902-X-002ED | FLD | C&E/693 | ALARM - BEACON | ADJ TO ET01 & ET02 | 083.2 | B.A. ALM. AQUEOUS EFFLUENT PIT |  | - | - | SHE | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5092 |  |  | 01
BA1 | BA1-PRV-001 | BA1-P-001 | FLD | 108-BA | CONTROL VALVE SELF ACTUATING | 50-BA-SS1U-0-9027900 | 042.3 | 4 BARG BREATHING AIR |  | 4.0 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
BA1 | BA1-PRV-002 | BA1-P-002 | FLD | 108-BA | CONTROL VALVE SELF ACTUATING | 50-BA-SS1U-0-9027900 | 042.3 | 4 BARG BREATHING AIR |  | 4.0 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
BA1 | BA1-PSV-003 | BA1-P-003 | FLD | 108-BA | PRESSURE RELIEF VALVE | 50-BA-SS1U-0-9027900 | 042.3 | B.A. PRESSURE |  |  |  | REF | REQ | [8 empty] | SPIRAX SARCO | SVL488SS |  |  |  |  | 01
BA1 | BA1-PSV-004 | BA1-P-004 | FLD | 108-BA | PRESSURE RELIEF VALVE | 50-BA-SS1U-0-9027900 | 042.3 | B.A. PRESSURE |  |  |  | REF | REQ | [8 empty] | SPIRAX SARCO | SVL488SS |  |  |  |  | 01
BA1 | BA1-PI-005 | BA1-P-005 | FLD | 108-BA | PRESSURE GAUGE | 50-BA-SS1U-0-9027900 | 042.3 | B.A. PRESSURE |  |  | +/- 5% | REF | REQ | [8 empty] | BUDENBERG | 966GP |  |  |  |  | 01
BA1 | BA1-PI-006 | BA1-P-006 | FLD | 108-BA | PRESSURE GAUGE | 50-BA-SS1U-0-9027900 | 042.3 | B.A. PRESSURE |  |  | +/- 5% | REF | REQ | [8 empty] | BUDENBERG | 966GP |  |  |  |  | 01
BA1 | BA1-PI-007 | BA1-P-007 | FLD | 108-BA | PRESSURE GAUGE | 50-BA-SS1U-0-9027900 | 042.3 | B.A. PRESSURE |  |  | +/- 5% | REF | REQ | [8 empty] | BUDENBERG | 966GP |  |  |  |  | 01
BEMS | BEMS-HS-004A | BEMS-H-004 | FLD | 107-JL | SWITCH - HAND OP. | C1 MODULE GND FLOOR | 008.4 | CONTAINMENT SPILLAGE | 8537 | - | - |  | REQ | F |  | N.I.S |  |  |  | 35 | [5 empty] | INPUT TO BEMS SYSTEM | DI | 01
BEMS | BEMS-HS-004B | BEMS-H-004 | FLD | 107-JL | SWITCH - HAND OP. | C1 MODULE 1ST FLOOR | 008.4 | CONTAINMENT SPILLAGE |  | - | - |  | REQ | F |  | N.I.S |  |  |  | 35 | [5 empty] | INPUT TO BEMS SYSTEM | DI | 01
BEMS | BEMS-HS-004C | BEMS-H-004 | FLD | 107-JL | SWITCH - HAND OP. | C1 MODULE 2ND FLOOR | 008.4 | CONTAINMENT SPILLAGE |  | - | - |  | REQ | F |  | N.I.S |  |  |  | 35 | [5 empty] | INPUT TO BEMS SYSTEM | DI | 01
BEMS | BEMS-XA-004A | BEMS-H-004 | PKG | 107-JL | ALARM - TOXIC SPILLAGE | BEMS CONTROL SYSTEM | 008.4 | CONTAINMENT SPILLAGE |  | - | - |  | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL |  |  |  |  | BEMS HVAC INTERLOCK |  | 01
BEMS | BEMS-XA-004B | BEMS-H-004 | PCS | 107-JL | ALARM - TOXIC SPILLAGE |  |  | CONTAINMENT SPILLAGE | [11 empty] | 0 | [7 empty] | 01
BEMS | BEMS-XS-001 | BEMS-X-001 | FLD | N/A | SWITCH - MISC. ALARM | BEMS SYSTEM | 025.0 | HVAC COMMON ALARM | 8538 | - | - |  | 12 | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
BEMS | BEMS-XA-006 | BEMS-X-006 | PCS | N/A | ALARM - OUTPUT |  | 025.0 | PUR. WATER PKG. COM. ALARM | 8539 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 43 | UTIL | [6 empty] | 01
BMS | BMS-BXA-900 | BMS-B-900 | PLC | N/A | ALARM - BMS | HVAC MCC |  | FIRE ALARM FROM FIRE SYSTEM | 8739 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-906 | BMS-B-906 | PLC | N/A | ALARM - BMS | HVAC MCC |  | MDC COMMON FAULT | 8740 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-907 | BMS-B-907 | PLC | N/A | ALARM - BMS | HVAC MCC |  | MDC FEEDER TO MCC-P TRIPPED | 8741 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-908 | BMS-B-908 | PLC | N/A | ALARM - BMS | HVAC MCC |  | MDC FEEDER TO MCC-PE TRIPPED | 8744 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-909 | BMS-B-909 | PLC | N/A | ALARM - BMS | HVAC MCC |  | MDC FEEDER TO MCC HVAC TRIPPED | 8747 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-910 | BMS-B-910 | PLC | N/A | ALARM - BMS | HVAC MCC |  | TRANSFORMER #1 COMMON FAULT | 8750 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-911 | BMS-B-911 | PLC | N/A | ALARM - BMS | HVAC MCC |  | TRANSFORMER #2 COMMOM FAULT | 8753 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-912 | BMS-B-912 | PLC | N/A | ALARM - BMS | HVAC MCC |  | TRANSFORMER #3 COMMON FAULT | 8756 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-913 | BMS-B-913 | PLC | N/A | ALARM - BMS | HVAC MCC |  | GENERATOR COMMON FAULT | 8770 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-915 | BMS-B-915 | PLC | N/A | ALARM - BMS | HVAC MCC |  | UPS COMMON FAULT | 8778 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-916 | BMS-B-916 | PLC | N/A | ALARM - BMS | HVAC MCC |  | LIGHTING INVERTER COMMON FAULT | 8800 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-917 | BMS-B-917 | PLC | N/A | ALARM - BMS | HVAC MCC |  | MDC TRIPPING UNIT COMMON FAULT | 8809 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BMS | BMS-BXA-918 | BMS-B-918 | PLC | N/A | ALARM - BMS | HVAC MCC |  | TRACE HEATING COMMON ALARM | 8819 | [6 empty] | N.I.S |  |  |  | 0 | [6 empty] | DI | 01
BS01 | BS01-DIC-001 | BS01-D-001 | PCS | 108-EA | INDICATING CONTR. - MOTOR DRIVE |  |  | UTILITY WATER PUMP | [11 empty] | 0 | [7 empty] | 01
BS01 | BS01-DS-001 | BS01-D-001 | MCC | 108-EA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | UTILITY WATER PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
BS01 | BS01-DY-001 | BS01-D-001 | MCC | 108-EA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | UTILITY WATER PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
BS01 | BS01-DYC-001 | BS01-D-001 | MCC | 108-EA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 044.1 | UTILITY WATER PUMP | 8540 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
BS01 | BS01-DIC-002 | BS01-D-002 | PCS | 108-EA | INDICATING CONTR. - MOTOR DRIVE |  |  | UTILITY WATER PUMP | [11 empty] | 0 | [7 empty] | 01
BS01 | BS01-DS-002 | BS01-D-002 | MCC | 108-EA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | UTILITY WATER PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
BS01 | BS01-DY-002 | BS01-D-002 | MCC | 108-EA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | UTILITY WATER PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
BS01 | BS01-DYC-002 | BS01-D-002 | MCC | 108-EA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 044.1 | UTILITY WATER PUMP | 8541 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
BS01 | BS01-LAL-001 | BS01-L-001 | PCS | 108-EA | ALARM - LEVEL - LOW |  |  | BREAK TANK LOW LEVEL | [11 empty] | 0 | [7 empty] | 01
BS01 | BS01-LSL-001 | BS01-L-001 | PKG | 108-EA | SWITCH - LEVEL - LOW | BS01-BT | 044.1 | BREAK TANK LOW LEVEL | 8542 | Fixed | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | S440PA/F84 |  | TI702-SP-5104 |  |  | 01
BS01 | BS01-LSL-002 | BS01-L-002 | FLD | 108-EA | SWITCH - LEVEL - OVERFLOW | BS01-BT | 044.1 |  |  |  |  | REF | REQ | F | [7 empty] | GEMS SENSORS | ELS-1100 |  |  |  |  | 01
BS01 | BS01-LSL-003 | BS01-L-003 | FLD | 108-EA | SWITCH - LEVEL - BUND | BUND | 044.1 |  |  |  |  | REF | REQ | F | [7 empty] | GEMS SENSORS | ELS-1100-FLG |  |  |  |  | 01
BS01 | BS01-PI-001 | BS01-P-001 | FLD | 108-EA | PRESSURE GAUGE | 50-PW-CS1B-0-9026501 | 044.1 | BS01-P1 DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 (Note 2) | KP0006/3 |  |  |  | 01
BS01 | BS01-PI-002 | BS01-P-002 | FLD | 108-EA | PRESSURE GAUGE | 50-PW-CS1B-0-9026500 | 044.1 | BS01-P2 DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 (Note 2) | KP0006/3 |  |  |  | 01
BS01 | BS01-PAH-003 | BS01-P-003 | PCS | 108-EA | ALARM - PRESSURE - HIGH |  |  | BS01-P1 & P2 DISCHARGE | [11 empty] | 0 | [7 empty] | 01
BS01 | BS01-PAL-003 | BS01-P-003 | PCS | 108-EA | ALARM - PRESSURE - LOW |  |  | BS01-P1 & P2 DISCHARGE | [11 empty] | 0 | [7 empty] | 01
BS01 | BS01-PSH-003 | BS01-P-003 | FLD | 108-EA | SWITCH - PRESSURE - HIGH | 50-PW-CS1B-0-9026500 | 044.1 | BS01-P1 & P2 DISCHARGE | 8253 | set @ 5.0 barg | +/- 5% | REF | REQ | C |  | I.S | DI |  |  | 32 | UTIL | DELTA CONTROLS LTD | W28102XX04D301262 | KP0012 | TI702-SP-5085 |  |  | 01
BS01 | BS01-PSL-003 | BS01-P-003 | FLD | 108-EA | SWITCH - PRESSURE - LOW | 50-PW-CS1B-0-9026500 | 044.1 | BS01-P1 & P2 DISCHARGE |  | set @ 2 barg | +/- 5% | REF | REQ | C |  | I.S | DI |  |  | 32 | UTIL | DELTA CONTROLS LTD | W28102XX04D301262 | KP0012 | TI702-SP-5085 | HOUSED WITH BS01-PSH-003 |  | 01
BS01 | BS01-PI-004 | BS01-P-004 | FLD | 108-EA | PRESSURE GAUGE | 50-PW-CS1B-0-9026500 | 044.2 | BS01-P1 & P2 DISCHARGE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 233.50.100 | KP0006/P3 |  |  |  | 01
BS01 | BS01-PRV-005 | BS01-P-005 | FLD | 108-EA | PRESSURE REDUCING VALVE | BS01-BT | 044.1 |  |  |  |  | REF | REQ | C | [7 empty] | Broady | D Series |  |  |  |  | 01
BS01 | BS01-YS-001 | BS01-Y-001 | FLD | 108-EA | ALARM - OVERFLOW | ADJ TO BS01 & BS02 | 044.1 |  | L14836 |  |  | REF | REQ | C | [7 empty] | TAYWEST | 62230 |  |  |  |  | 01
BS02 | BS02-DIC-001 | BS02-D-001 | PCS | 108-EA | INDICATING CONTR. - MOTOR DRIVE |  |  | SAFETY WATER PUMP | [11 empty] | 0 | [7 empty] | 01
BS02 | BS02-DS-001 | BS02-D-001 | MCC | 108-EA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | SAFETY WATER PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
BS02 | BS02-DY-001 | BS02-D-001 | MCC | 108-EA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | SAFETY WATER PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
BS02 | BS02-DYC-001 | BS02-D-001 | MCC | 108-EA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 044.2 | SAFETY WATER PUMP | 8544 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
BS02 | BS02-DIC-002 | BS02-D-002 | PCS | 108-EA | INDICATING CONTR. - MOTOR DRIVE |  |  | SAFETY WATER PUMP | [11 empty] | 0 | [7 empty] | 01
BS02 | BS02-DS-002 | BS02-D-002 | MCC | 108-EA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | SAFETY WATER PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
BS02 | BS02-DY-002 | BS02-D-002 | MCC | 108-EA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | SAFETY WATER PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
BS02 | BS02-DYC-002 | BS02-D-002 | MCC | 108-EA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 044.2 | SAFETY WATER PUMP | 8545 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
BS02 | BS02-LAL-001 | BS02-L-001 | PCS | 108-EA | ALARM - LEVEL - LOW |  |  | BREAK TANK LOW LEVEL | [11 empty] | 0 | [7 empty] | 01
BS02 | BS02-LSL-001 | BS02-L-001 | PKG | 108-EA | SWITCH - LEVEL - LOW | BS02-BT | 044.2 | BREAK TANK LOW LEVEL | 8546 | Fixed | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | S440PA/F84 |  | TI702-SP-5104 |  |  | 01
BS02 | BS02-LSL-002 | BS02-L-002 | FLD | 108-EA | SWITCH - LEVEL - OVERFLOW | BS02-BT | 044.2 |  |  |  |  | REF | REQ | C | [7 empty] | GEMS SENSORS | ELS-1100 |  |  |  |  | 01
BS02 | BS02-PI-001 | BS02-P-001 | FLD | 108-EA | PRESSURE GAUGE | 50-SW-GA1A-0-9026509 | 044.2 | BS02-P1 DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 (Note 2) | KP0006/3 |  |  |  | 01
BS02 | BS02-PI-002 | BS02-P-002 | FLD | 108-EA | PRESSURE GAUGE | 50-SW-GA1A-0-9026508 | 044.2 | BS02-P2 DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 (Note2) | KP0006/3 |  |  |  | 01
BS02 | BS02-PAH-003 | BS02-P-003 | PCS | 108-EA | ALARM - PRESSURE - HIGH |  |  | BS02-P1 & P2 DISCHARGE |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
BS02 | BS02-PAL-003 | BS02-P-003 | PCS | 108-EA | ALARM - PRESSURE - LOW |  |  | BS02-P1 & P2 DISCHARGE |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
BS02 | BS02-PSH-003 | BS02-P-003 | FLD | 108-EA | SWITCH - PRESSURE - HIGH | 50-SW-GA1A-0-9026523 | 044.2 | BS02-P1 & P2 DISCHARGE | 8254 | set @ 5.0 barg | +/- 5% | REF | REQ | C |  | I.S | DI |  |  | 32 | UTIL | DELTA CONTROLS LTD | W28102XX04D301262 | KP0012 | TI702-SP-5085 |  |  | 01
BS02 | BS02-PSL-003 | BS02-P-003 | FLD | 108-EA | SWITCH - PRESSURE - LOW | 50-SW-GA1A-0-9026523 | 044.2 | BS02-P1 & P2 DISCHARGE |  | set @ 2 barg | +/- 5% | REF | REQ | C |  | I.S | DI |  |  | 32 | UTIL | DELTA CONTROLS LTD | W28102XX04D301262 | KP0012 | TI702-SP-5085 | HOUSED WITH BS02-PSH-003 |  | 01
BS02 | BS02-PI-004 | BS02-P-004 | FLD | 108-EA | PRESSURE GAUGE | 50-SW-GA1A-0-9026508 | 044.2 | BS02-P1 & P2 DISCHARGE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 233.50.100 | KP0006/P3 |  |  |  | 01
BS02 | BS02-PRV-005 | BS02-P-005 | FLD | 108-EA | PRESSURE REDUCING VALVE | BS02-BT | 044.2 |  |  |  |  | REF | REQ | C | [7 empty] | Broady | D Series |  |  |  |  | 01
C01 | C01-AE-001 | C01-A-001 | PKG | 107-BU | ELEMENT - ANALYSIS | 50-RV-PT1A-0-9021912 | 009.0 | O2 MEASURING | 7061 | 0 - 25% Oxygen | +/- 1% | GxP/SHE | 6 | C |  | I.S |  |  |  | 11 |  | TELEDYNE | 301DTAC |  |  |  | AI | 01
C01 | C01-AIT-001 | C01-A-001 | PLC | 107-BU | INDICATOR - ANALYSIS | CENTRIFUGE CONTROL PANEL | 009.0 | O2 MEASURING |  | 0 - 25% Oxygen | +/- 1% | GxP/SHE | 6 | C | [5 empty] | 0 |  | TELEDYNE | 301DTAC |  |  |  |  | 01
C01 | C01-CV-001 | C01-C-001 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021827 | 101.0 | FEED VALVE | 7036 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-001 | C01-C-001 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | FEED VALVE |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-001 | C01-C-001 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | FEED VALVE |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-001 | C01-C-001 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | FEED VALVE |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-002 | C01-C-002 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 40-SO-PT1A-0-9021917 | 101.0 | WASH VALVE | 7037 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-002 | C01-C-002 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | WASH VALVE |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-002 | C01-C-002 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | WASH VALVE |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-ZSO-002 | C01-C-002 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | WASH VALVE |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-CV-003 | C01-C-003 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-9021919 | 101.0 | CIP VALVE 1 | 7038 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-003 | C01-C-003 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | CIP VALVE 1 |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-003 | C01-C-003 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CIP VALVE 1 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-003 | C01-C-003 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CIP VALVE 1 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-004 | C01-C-004 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-9021918 | 101.0 | CIP VALVE 2 | 7039 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-004 | C01-C-004 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | CIP VALVE 2 |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-004 | C01-C-004 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CIP VALVE 2 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-ZSO-004 | C01-C-004 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CIP VALVE 2 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-CV-005 | C01-C-005 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-9021924 | 101.0 | CIP VALVE 3 | 7040 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-005 | C01-C-005 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | CIP VALVE 3 |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-005 | C01-C-005 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CIP VALVE 3 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-ZSO-005 | C01-C-005 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CIP VALVE 3 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-CV-006 | C01-C-006 | PKG | 107-BU | BUTTERFLY VALVE - ON/OFF - F.C. | 100-C01-OUTLET | 101.0 | PRODUCT DISCHARGE | 7041 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
C01 | C01-CY-006 | C01-C-006 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | PRODUCT DISCHARGE | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-006 | C01-C-006 | PKG | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PRODUCT DISCHARGE | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-006 | C01-C-006 | PKG | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PRODUCT DISCHARGE | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-007 | C01-C-007 | FLD | 107-BU | BALL VALVE - ON/OFF - F.O. | 80-P-PT1A-0-9021901 | 101.0 | FLOODING VALVE | 7042 | - | - | REF | REQ | F | [5 empty] | 0 |  | TBA | VTA | KV0007 |  |  |  | 01
C01 | C01-CY-007 | C01-C-007 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | FLOODING VALVE | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-007 | C01-C-007 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | FLOODING VALVE | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-007 | C01-C-007 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | FLOODING VALVE | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-008 | C01-C-008 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-9021944 | 101.0 | RINSE VALVE UFKR | 7043 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-008 | C01-C-008 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | RINSE VALVE UFKR |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-008 | C01-C-008 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RINSE VALVE UFKR |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-008 | C01-C-008 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RINSE VALVE UFKR |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-009 | C01-C-009 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9021945 | 043.4 | N2 - CIP VALVE 1 | 7044 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-009 | C01-C-009 | FLD | 107-BU | SOLENOID VALVE | MTD. ON VALVE |  | N2 - CIP VALVE 1 |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-009 | C01-C-009 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 - CIP VALVE 1 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-ZSO-009 | C01-C-009 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 - CIP VALVE 1 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-CV-010 | C01-C-010 | FLD | 107-BU | BALL VALVE - ON/OFF - F.O. | 25-P-PT1A-0-9021940 | 043.4 | N2 - CIP VALVE 2 | 7045 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-010 | C01-C-010 | FLD | 107-BU | SOLENOID VALVE | MTD. ON VALVE |  | N2 - CIP VALVE 2 |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-010 | C01-C-010 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 - CIP VALVE 2 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-ZSO-010 | C01-C-010 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 - CIP VALVE 2 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-CV-011 | C01-C-011 | FLD | 107-BU | BALL VALVE - ON/OFF - F.O. | 80-P-SS1C-E-9021922 | 101.0 | VENT INERTING | 7046 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
C01 | C01-CY-011 | C01-C-011 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | VENT INERTING | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-011 | C01-C-011 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | VENT INERTING | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-011 | C01-C-011 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | VENT INERTING | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-012 | C01-C-012 | FUT | 107-BU | BALL VALVE - ON/OFF - F.C. | 40-SO-PT1A-0-9021826 | 101.0 | CIP VALVE 5 | 7047 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-012 | C01-C-012 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | CIP VALVE 5 | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-012 | C01-C-012 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CIP VALVE 5 | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-012 | C01-C-012 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CIP VALVE 5 | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-013 | C01-C-013 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 40-SO-PT1A-0-9021826 | 101.0 | CIP VALVE 6 | 7048 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-013 | C01-C-013 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | CIP VALVE 6 |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-013 | C01-C-013 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CIP VALVE 6 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-013 | C01-C-013 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CIP VALVE 6 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-014 | C01-C-014 | FLD | 107-BU | BALL VALVE - ON/OFF - F.O. | 40-SO-PT1A-0-9021826 | 101.0 | VENT HCR | 7049 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
C01 | C01-CY-014 | C01-C-014 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | VENT HCR | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-014 | C01-C-014 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | VENT HCR | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-014 | C01-C-014 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | VENT HCR | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-015 | C01-C-015 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-9021923 | 101.0 | CIP VALVE 7 | 7050 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-015 | C01-C-015 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | CIP VALVE 7 |  |  |  | SHE |  |  |  | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-015 | C01-C-015 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CIP VALVE 7 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-015 | C01-C-015 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CIP VALVE 7 |  |  |  | SHE |  |  |  | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-016 | C01-C-016 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 40-SO-PT1A-0-9021923 | 043.2 | HEEL CAKE REMOVAL | 7051 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-016 | C01-C-016 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | HEEL CAKE REMOVAL | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-016 | C01-C-016 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HEEL CAKE REMOVAL | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-ZSO-016 | C01-C-016 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HEEL CAKE REMOVAL | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-CV-019 | C01-C-019 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021910 | 101.0 | TP1 FILTRATE OUT | 7052 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-019 | C01-C-019 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | TP1 FILTRATE OUT | [7 empty] | I.S | DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
C01 | C01-ZSC-019 | C01-C-019 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TP1 FILTRATE OUT | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
C01 | C01-ZSO-019 | C01-C-019 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TP1 FILTRATE OUT | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
C01 | C01-CV-021 | C01-C-021 | FLD | 107-BU | BALL VALVE - ON/OFF - F.O. | 25-N-PT1A-0-9021938 | 101.0 | CLOSE INERT | 7053 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-021 | C01-C-021 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | CLOSE INERT | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-021 | C01-C-021 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CLOSE INERT | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-021 | C01-C-021 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CLOSE INERT | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-022 | C01-C-022 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9021932 | 101.0 | THOTTLE FEEDING | 7054 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-022 | C01-C-022 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | THOTTLE FEEDING | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-022 | C01-C-022 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | THOTTLE FEEDING | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-ZSO-022 | C01-C-022 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | THOTTLE FEEDING | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  | DI | 01
C01 | C01-CV-023 | C01-C-023 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021928 | 101.0 | SLURRY RECYCLE | 7055 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-023 | C01-C-023 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | SLURRY RECYCLE | [7 empty] | I.S | DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
C01 | C01-ZSC-023 | C01-C-023 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRY RECYCLE | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
C01 | C01-ZSO-023 | C01-C-023 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRY RECYCLE | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
C01 | C01-CV-024 | C01-C-024 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 25-P-SS1C-0-9021948 | 101.0 | BYPASS O2 MEASURING | 7056 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-024 | C01-C-024 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | BYPASS O2 MEASURING | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-024 | C01-C-024 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BYPASS O2 MEASURING | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-024 | C01-C-024 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BYPASS O2 MEASURING | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-025 | C01-C-025 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 25-RV-GR1A-0-9021912 | 042.2 | O2 MEASURING | 7057 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-025 | C01-C-025 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | O2 MEASURING | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-025 | C01-C-025 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | O2 MEASURING | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-ZSO-025 | C01-C-025 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | O2 MEASURING | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-026 | C01-C-026 | FLD | 107-BU | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9021947 | 043.4 | N2 - FEED LINE | 7058 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-CY-026 | C01-C-026 | FLD | 107-BU | SOLENOID VALVE | RACK MOUNTED |  | N2 - FEED LINE | [7 empty] | I.S |  |  |  | 41 | GP1 | [5 empty] | DO | 01
C01 | C01-ZSC-026 | C01-C-026 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 - FEED LINE | [7 empty] | I.S |  |  |  | 31 | GP1 | [5 empty] | DI | 01
C01 | C01-ZSO-026 | C01-C-026 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 - FEED LINE | [7 empty] | I.S |  |  |  | 31 | GP1 | [5 empty] | DI | 01
C01 | C01-CV-027 | C01-C-027 | PKG | 107-BU | HYDRAULIC VALVE | C01 CENTRIFUGE | 101.0 | HEEL CAKE REMOVAL PIPE | 7059 | - | - | REF | REQ | F | [5 empty] | 0 |  | KRAUSS MAFFEI AG | [5 empty] | 01
C01 | C01-CY-027 | C01-C-027 | PKG | 107-BU | SOLENOID VALVE | C01 CENTRIFUGE |  | HEEL CAKE REMOVAL PIPE | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-027 | C01-C-027 | PKG | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HEEL CAKE REMOVAL PIPE | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-ZSO-027 | C01-C-027 | PKG | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HEEL CAKE REMOVAL PIPE | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-CV-028 | C01-C-028 | PKG | 107-BU | HYDRAULIC VALVE - STAYPUT | C01 CENTRIFUGE | 101.0 | HOUSING CLOSURE | 7060 | - | - | REF | REQ | F | [5 empty] | 0 |  | KRAUSS MAFFEI AG | [5 empty] | 01
C01 | C01-CY-028A | C01-C-028 | PKG | 107-BU | SOLENOID VALVE | C01 CENTRIFUGE |  | HOUSING CLOSURE | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-CY-028B | C01-C-028 | PKG | 107-BU | SOLENOID VALVE | C01 CENTRIFUGE |  | HOUSING CLOSURE | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-028 | C01-C-028 | PKG | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSING CLOSURE | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-ZSO-028 | C01-C-028 | PKG | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSING CLOSURE | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-CV-029 | C01-C-029 | PKG | 107-BU | HYDRAULIC VALVE - STAYPUT | C01 CENTRIFUGE | 101.0 | PEELER KNIFE | 7064 | - | - | REF | REQ | F | [5 empty] | 0 |  | KRAUSS MAFFEI AG | [5 empty] | 01
C01 | C01-CY-029A | C01-C-029 | PKG | 107-BU | SOLENOID VALVE | C01 CENTRIFUGE |  | PEELER KNIFE | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-CY-029B | C01-C-029 | PKG | 107-BU | SOLENOID VALVE | C01 CENTRIFUGE |  | PEELER KNIFE | [7 empty] | I.S |  |  |  | 41 | [6 empty] | DO | 01
C01 | C01-ZSC-029 | C01-C-029 | PKG | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PEELER KNIFE | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-ZSM-029 | C01-C-029 | PKG | 107-BU | PROXIMITY SENSOR - MID POSN | MTD. ON VALVE |  | PEELER KNIFE | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-ZSO-029 | C01-C-029 | PKG | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PEELER KNIFE | [7 empty] | I.S |  |  |  | 31 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-CY-030A | C01-C-030 | PKG | 107-BU | SOLENOID VALVE | C01 INERTING UNIT | 101.0 | INERTING | 6604 | - | - | REF | REQ | F |  | N.I.S |  |  |  | 43 | GP1 | [5 empty] | DO | 01
C01 | C01-CY-030B | C01-C-030 | PKG | 107-BU | SOLENOID VALVE | C01 INERTING UNIT | 101.0 | INERTING |  | - | - | REF | REQ | F |  | N.I.S |  |  |  | 43 | GP1 | [5 empty] | DO | 01
C01 | C01-DIC-002 | C01-D-002 | PLC | 107-BU | INDICATING CONTR. - MOTOR DRIVE |  |  | HYDRAULIC PUMP |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
C01 | C01-DY-002 | C01-D-002 | PKG | 107-BU | DRIVE - RUNNING | C01 INVERTER PANEL |  | HYDRAULIC PUMP |  |  |  | SHE |  |  |  | N.I.S |  |  |  | 35 | GP1 | [5 empty] | DI | 01
C01 | C01-DYC-002 | C01-D-002 | PKG | 107-BU | DRIVE - START/STOP | C01 INVERTER PANEL | 101.0 | HYDRAULIC PUMP | 7063 | - | - | SHE | REQ | F |  | N.I.S |  |  |  | 42 | GP1 | [5 empty] | DO | 01
C01 | C01-DIC-004 | C01-D-004 | PCS | 107-BU | INDICATING CONTR. - MOTOR DRIVE |  |  | TP1 FILTRATE PUMP |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
C01 | C01-DS-004 | C01-D-004 | MCC | 107-BU | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TP1 FILTRATE PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | GP1 | [6 empty] | 01
C01 | C01-DY-004 | C01-D-004 | MCC | 107-BU | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TP1 FILTRATE PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | GP1 | [6 empty] | 01
C01 | C01-DYC-004 | C01-D-004 | MCC | 107-BU | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 101.0 | TP1 FILTRATE PUMP | 8548 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
C01 | C01-FQ-001 | C01-F-001 | PLC | 107-BU | FLOW TOTALISOR- HIGH |  |  | WASH FLOW/CIP LINE | [11 empty] | 0 | [7 empty] | 01
C01 | C01-FT-001 | C01-F-001 | FLD | 107-BU | TRANSMITTER - FLOW | 40-SO-PT1A-0-9021917 | 101.0 | WASH FLOW/CIP LINE | 6461 | 0 - 12 m3/hr | +/- 1% | SHE | 5 YR | C |  | N.I.S |  |  |  | 36 |  | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 1 litre/pulse | DI | 01
C01 | C01-FAL-002 | C01-F-002 | PLC | 107-BU | ALARM - FLOW - LOW |  |  | FLOW - N2 PURGING |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
C01 | C01-FSL-002 | C01-F-002 | PKG | 107-BU | SWITCH - FLOW - LOW | 50-P-SS1C-E-9021922 | 101.0 | FLOW - N2 PURGING | 7062 | set@0.1 Nm3/hr | +/- 5% | GxP/SHE | 12 | C |  | I.S |  |  |  | 32 | [6 empty] | DI | 01
C01 | C01-FI-003 | C01-F-003 | LCP | 107-BU | INDICATOR - FLOW | N2 DISTRIBUTION PANEL | 101.0 | INERTING |  | 100 - 1000 l/hr | +/- 5% |  | REQ | F | [5 empty] | 0 | [7 empty] | 01
C01 | C01-HV-001 | C01-H-001 | FLD | 107-BU | HAND VALVE | 25-SO-PT1A-0-9021933 | 101.0 | RINSE GLASSES | 7065 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
C01 | C01-HZSC-001 | C01-H-001 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RINSE GLASSES | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-HZSO-001 | C01-H-001 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RINSE GLASSES | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-HV-002 | C01-H-002 | FLD | 107-BU | HAND VALVE | 25-N-SS1U-0-9021936 | 043.2 | N2 INERTING UNIT | 7066 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
C01 | C01-HZSC-002 | C01-H-002 | FLD | 107-BU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 INERTING UNIT | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-HZSO-002 | C01-H-002 | FLD | 107-BU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 INERTING UNIT | [7 empty] | I.S |  |  |  | 31 | [6 empty] | DI | 01
C01 | C01-HS-003 | C01-H-003 | PKG | 107-BU | SWITCH - HAND OP. | C01 LOCAL PANEL | 101.0 | EMERGENCY STOP | 7067 | - | - | GxP/SHE | REQ | F |  | N.I.S |  |  |  | 32 | GP1 | [5 empty] | DI | 01
C01 | C01-HS-004 | C01-H-004 | PKG | 107-BU | SWITCH - HAND OP. | C01 LOCAL PANEL | 101.0 | MAINTANENCE KEYSWITCH | 7076 | - |  |  | REQ | F |  | N.I.S |  |  |  | 32 | GP1 | [5 empty] | DI | 01
C01 | C01-LAH-001 | C01-L-001 | PCS | 107-BU | ALARM - LEVEL - HIGH |  |  | RC1 HIGH LEVEL |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
C01 | C01-LE-001 | C01-L-001 | FLD | 107-BU | ELEMENT - LEVEL | 80-P-PT1A-0-9021937 | 101.0 | RC1 HIGH LEVEL |  | Fixed | - | SHE | 12 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
C01 | C01-LSH-001 | C01-L-001 | CPR | 107-BU | SWITCH - LEVEL - HIGH | 80-P-PT1A-0-9021937 | 101.0 | RC1 HIGH LEVEL | 6630 | - | - | SHE | 12 | F |  | N.I.S | DI |  |  | 35 | GP1 | ENDRESS + HAUSER | FDL31-GYY9AC70 | KL0014 |  |  |  | 01
C01 | C01-LIC-002 | C01-L-002 | PCS | 107-BU | INDICATING CONTROLLER - LEVEL |  |  | RC1 LEVEL | [11 empty] | 0 | [7 empty] | 01
C01 | C01-LT-002 | C01-L-002 | FLD | 107-BU | TRANSMITTER - LEVEL | C01-RC1/N2/100 | 101.0 | RC1 LEVEL | 6466 | 0 to 300 l | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ENDRESS + HAUSER | FMR245 note2 | KL0028/P2 | TI702-SP-5026 |  |  | 01
C01 | C01-LE-007 | C01-L-007 | PKG | 107-BU | ELEMENT - LEVEL | DELETED | 101.0 | DELETED | 7069 |  |  |  | REQ | F |  | I.S |  |  |  | 33 | [5 empty] | DELETED | DI | 01
C01 | C01-LT-007 | C01-L-007 | CPR | 107-BU | TRANSMITTER - LEVEL | DELETED | 101.0 | DELETED |  | 0 to 100% | +/- 2% |  | REQ | C | [5 empty] | 0 |  | HYDRORANGER 1 |  |  |  | DELETED |  | 01
C01 | C01-PSV-001 | C01-P-001 | FLD | 107-BU | PRESSURE RELIEF VALVE | 80-P-SS1C-E-9021922 | 101.0 | INERTING RELIEF |  | 300 mbar | +/- 10% |  | 24 | C | [5 empty] | 0 |  | A.G.MARVAC | TYPE 910 | KS0001 |  |  |  | 01
C01 | C01-PSV-002 | C01-P-002 | FLD | 107-BU | PRESSURE RELIEF VALVE | 80-RV-PT1A-0-9021937 | 101.0 | RC1 RELIEF |  | 1 barg | +/- 10% |  | 24 | C | [5 empty] | 0 |  | BROADY | 2511G-Hast-N000 | KS0001 |  |  |  | 01
C01 | C01-PSH-003 | C01-P-003 | PKG | 107-BU | SWITCH - PRESSURE - HIGH | C01 CENTRIFUGE | 101.0 | CENTRIFUGE PRESSURE | 7070 | set @ 40 mbarg | +/- 5% | GxP/SHE | 12 | C |  | I.S |  |  |  | 31 | [5 empty] | WITH PSL-003 | DI | 01
C01 | C01-PSL-003 | C01-P-003 | PKG | 107-BU | SWITCH - PRESSURE - LOW | C01 CENTRIFUGE | 101.0 | CENTRIFUGE PRESSURE |  | set @ 10 mbarg | +/- 5% | GxP/SHE | 12 | C |  | I.S |  |  |  | 31 | [5 empty] | WITH PSH-003 | DI | 01
C01 | C01-PI-006 | C01-P-006 | FLD | 107-BU | PRESSURE GAUGE - DIAPHRAGM | 80-P-PT1A-N-9021937 | 101.0 | RC1 PRESSURE |  | 0 to 0.6 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
C01 | C01-PI-007 | C01-P-007 | FLD | 107-BU | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-0-9021910 | 101.0 | TP1 DISCHARGE PRESSURE |  | 0 to 6 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
C01 | C01-PI-008 | C01-P-008 | LCP | 107-BU | PRESSURE GAUGE | N2 DISTRIBUTION PANEL | 101.0 | INERT PRESSURE |  | 0 to 1 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
C01 | C01-PI-009 | C01-P-009 | LCP | 107-BU | PRESSURE GAUGE | N2 DISTRIBUTION PANEL | 101.0 | SHAFT SEAL PRESSURE |  | 0 to 1 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
C01 | C01-PI-010 | C01-P-010 | LCP | 107-BU | PRESSURE GAUGE | N2 DISTRIBUTION PANEL | 101.0 | INERT PRESSURE |  | 0 to 1 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
C01 | C01-PI-011 | C01-P-011 | LCP | 107-BU | PRESSURE GAUGE | N2 DISTRIBUTION PANEL | 101.0 | INERT PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
C01 | C01-PAL-020 | C01-P-020 | PLC | 107-BU | ALARM - PRESSURE - LOW |  |  | MIN. PRESSURE TANK |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
C01 | C01-PSL-020 | C01-P-020 | FLD | 107-BU | SWITCH - PRESSURE - LOW | 40-N-SS1U-0-9021925 | 043.2 | MIN. PRESSURE TANK | 6657 | set @ 3.3 barg | +/- 2% | SHE | 12 | C |  | I.S |  |  |  | 32 |  | DELTA CONTROLS LTD | WS210GDEH2X300ANA | KP0012 |  |  | DI | 01
C01 | C01-RO-001 | C01-R-001 | FLD | 107-BU | RESTRICTION ORIFICE PLATE | 25-N-SS1U-0-9028645 | 043.2 | N2 TO HEEL CAKE REMOVAL |  | 500 Nm3/hr | - | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
C01 | C01-SE-001 | C01-S-001 | PKG | 107-BU | ELEMENT - SPEED | CO1 CENTRIFUGE | 101.0 | SPEED MONITORING | 7071 |  |  | SHE | 12 | C |  | I.S |  |  |  | 33 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-SSH-001 | C01-S-001 | CPR | 107-BU | SWITCH - SPEED - HIGH | C01 CENTRIFUGE | 101.0 | SPEED MONITORING | 7071 | BY K.M. | +/- 5% | SHE | 12 | C |  | I.S |  |  |  | 0 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-SSL-001 | C01-S-001 | CPR | 107-BU | SWITCH - SPEED - LOW | C01 CENTRIFUGE | 101.0 | SPEED MONITORING |  | BY K.M. | +/- 5% | SHE | 12 | C |  | I.S |  |  |  | 0 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-SE-002 | C01-S-002 | PKG | 107-BU | ELEMENT - SPEED | C01 CENTRIFUGE | 101.0 | STAND STILL | 7072 |  |  |  | 12 | C |  | I.S |  |  |  | 33 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-SS-002 | C01-S-002 | CPR | 107-BU | SWITCH - SPEED - LOW | C01 CENTRIFUGE | 101.0 | STAND STILL |  | STOPPED | +/- 5% |  | 12 | C |  | I.S |  |  |  | 0 |  | PEPPERL + FUCHS |  |  |  |  | DI | 01
C01 | C01-SIC-003 | C01-S-003 | PLC | 107-BU | INDICATING CONTROLLER - SPEED | C01 CENTRIFUGE | 101.0 | DRIVE CENTRIFUGE | 7068 | 0 to 2270 rpm | - | REF | 12 | C | [5 empty] | 0 | [7 empty] | 01
C01 | C01-VE-001 | C01-V-001 | PKG | 107-BU | SWITCH - VIBRATION | C01 CENTRIFUGE | 101.0 | IMBALANCE MONITORING | 7073 | - | - |  | 12 | C |  | I.S |  |  |  | 33 | [6 empty] | DI | 01
C01 | C01-VT-001 | C01-V-001 | CPR | 107-BU | TRANSMITTER - VIBRATION | C01 CONTROL PANEL | 101.0 | IMBALANCE MONITORING |  | 0 to 20mm/sec | - |  | 12 | C |  | I.S |  |  |  | 11 | [6 empty] | DI | 01
C01 | C01-WE-001 | C01-W-001 | DEL | 107-BU | WEIGH CELLS | DELETED |  | DELETED | 7074 | [10 empty] | 0 | [5 empty] | DELETED |  | 01
C01 | C01-WI-001 | C01-W-001 | DEL | 107-BU | INDICATOR - WEIGH | DELETED |  | DELETED | [11 empty] | 0 | [5 empty] | DELETED |  | 01
C01 | C01-LI-003 | C01-Y-001 | PKG | 107-BU | INDICATOR - LEVEL GAUGE | C01-TP1 SEAL POT | 101.0 | TP1 SEAL POT FAILURE |  | Fixed | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
C01 | C01-LSH-004 | C01-Y-001 | PKG | 107-BU | SWITCH - LEVEL - HIGH | C01-TP1 SEAL POT | 101.0 | TP1 SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
C01 | C01-LSL-005 | C01-Y-001 | PKG | 107-BU | SWITCH - LEVEL - LOW | C01-TP1 SEAL POT | 101.0 | TP1 SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
C01 | C01-PI-004 | C01-Y-001 | PKG | 107-BU | PRESSURE GAUGE | C01-TP1 SEAL POT | 101.0 | TP1 SEAL POT FAILURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
C01 | C01-PSL-010 | C01-Y-001 | PKG | 107-BU | SWITCH - PRESSURE - LOW | C01-TP1 SEAL POT | 101.0 | TP1 SEAL POT FAILURE |  | set @ 4 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | [7 empty] | 01
C01 | C01-TI-002 | C01-Y-001 | PKG | 107-BU | INDICATOR - TEMPERATURE | C01-TP1 SEAL POT | 101.0 | TP1 SEAL POT FAILURE |  | 0 to 120 degC | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
C01 | C01-YA-001 | C01-Y-001 | PCS | 107-BU | ALARM - SEAL POT FAIL |  |  | TP1 SEAL POT FAILURE |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
C01 | C01-YS-001 | C01-Y-001 | PKG | 107-BU | SWITCH - COMMON ALARM | C01-TP1 SEAL POT | 101.0 | TP1 SEAL POT FAILURE | 7075 | - | - | SHE | REQ | F |  | I.S | DI |  |  | 32 | GP1 | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
C01 | C01-YS-002A | C01-Y-002 | PKG | 107-BU | SWITCH - COMMON ALARM | C01 CENTRIFUGE | 101.0 | HOUSING POSITION | 7076 | - | - | GxP/SHE | REQ | F |  | I.S |  |  |  | 32 | [6 empty] | DI | 01
C01 | C01-YS-002B | C01-Y-002 | PKG | 107-BU | SWITCH - HOUSING CLOSED | C01 CENTRIFUGE | 101.0 | HOUSING POSITION |  | - | - | GxP/SHE | REQ | F |  | I.S |  |  |  | 32 | [6 empty] | DI | 01
C01 | C01-YS-003 | C01-Y-003 | PKG | 107-BU | SWITCH - HOUSING LOCKED | C01 CENTRIFUGE | 101.0 | HOUSING LOCKED | 6351 | - | - |  | REQ | F |  | I.S |  |  |  | 32 | [6 empty] | DI | 01
C01 | C01-LSH-006 | C01-Y-004 | PKG | 107-BU | SWITCH - LEVEL - HIGH | C01 CENTRIFUGE | 101.0 | HYDRAULIC OIL | 7077 | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 32 | [6 empty] | DI | 01
C01 | C01-LSL-006 | C01-Y-004 | PKG | 107-BU | SWITCH - LEVEL - LOW | C01 CENTRIFUGE | 101.0 | HYDRAULIC OIL | 7077 | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 32 | [6 empty] | DI | 01
C01 | C01-PDSH-004 | C01-Y-004 | PKG | 107-BU | SWITCH - PRESSURE - HIGH | C01 CENTRIFUGE | 101.0 | HYDRAULIC OIL | 7077 |  | +/- ___% | REF | REQ | C |  | I.S |  |  |  | 32 | [6 empty] | DI | 01
C01 | C01-TSH-001 | C01-Y-004 | PKG | 107-BU | SWITCH - TEMPERATURE - HIGH | C01 CENTRIFUGE | 101.0 | HYDRAULIC OIL | 7077 |  | +/- ___% | REF | REQ | C |  | I.S |  |  |  | 32 | [6 empty] | DI | 01
C01 | C01-YS-004 | C01-Y-004 | PKG | 107-BU | SWITCH - COMMON ALARM | C01 CENTRIFUGE | 101.0 | HYDRAULIC OIL | 7077 | - | - |  | REQ | F |  | I.S |  |  |  | 32 | [6 empty] | DI | 01
C1 | C1-FQIC-001 | C1-F-001 | FLD | 107-EB | MOBILE WATER BATCH METER | 25-P-SS1C-0-9024263 | 041.0 | PURIFIED WATER TO R19/20/21/22 |  | 15 to 117 l/min | +/- 0.5% | REF | REQ | C | [5 empty] | 0 |  | ROSEMOUNT | 9455FB7C1A2R | KF0018 |  | COMMON FOR MODULE C1 |  | 01
C1 | C1-FQIC-001A | C1-F-001 | FLD | 107-EB | TURBINE WATER METER/TOTALISER | 25-P-SS1C-0-9024263 | 041.0 | PURIFIED WATER TO R19/20/21/22 |  | 0 to 100L per min | +/-5% | REF | By request | C |  | I.S |  |  |  | 0 |  | NIXON | BNO 500 | KF0018/P |  | COMMON FOR MODULE C1 |  | 01
C1 | C1-PI-011 | C1-P-011 | FLD | 108-CD | PRESSURE GAUGE | 40-CA-SS1U-0-9028453 | 042.2 | MODULE C1 AIR PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
C1 | C1-PI-012 | C1-P-012 | FLD | 108-CD | PRESSURE GAUGE | 40-CA-SS1U-0-9028454 | 042.2 | MODULE C1 AIR PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
C1 | C1TS1-PI-002 | C1TS1-P-002 | FLD | 107-ET | PRESSURE GAUGE - DIAPHRAGM | 40-SV-GR1A-0-9024866 | 008.3 | SCRUBBER SUCTION PRESSURE |  | 0 to 6 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
C1 | C1-HS-003AJ | C1-X-003AJ | FLD | C&E/693 | SWITCH - PUSHBUTTON | C1 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. C1 PROCESS GND FL | 8087 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
C1 | C1-XA-003AJ | C1-X-003AJ | FLD | C&E/693 | ALARM - AUDIBLE | C1 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. C1 PROCESS GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
C1 | C1-XL-003AJ | C1-X-003AJ | FLD | C&E/693 | ALARM - BEACON | C1 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. C1 PROCESS GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
C1 | C1-HS-003BJ | C1-X-003BJ | FLD | C&E/693 | SWITCH - PUSHBUTTON | C1 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. C1 PROCESS 1ST FL | 8093 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
C1 | C1-XA-003BJ | C1-X-003BJ | FLD | C&E/693 | ALARM - AUDIBLE | C1 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. C1 PROCESS 1ST FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
C1 | C1-XL-003BJ | C1-X-003BJ | FLD | C&E/693 | ALARM - BEACON | C1 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. C1 PROCESS 1ST FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
C1 | C1-HS-003CJ | C1-X-003CJ | FLD | C&E/693 | SWITCH - PUSHBUTTON | C1 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. C1 PROCESS 2ND FL | 8097 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
C1 | C1-XA-003CJ | C1-X-003CJ | FLD | C&E/693 | ALARM - AUDIBLE | C1 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. C1 PROCESS 2ND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
C1 | C1-XL-003CJ | C1-X-003CJ | FLD | C&E/693 | ALARM - BEACON | C1 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. C1 PROCESS 2ND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
C1 | C1- FSL-002 | C1-X-010 | CPR |  | TRIPAMP | C1 COMMONEXTRACT |  | C1 EXTRACT LOW AIR FLOW | 13???? |  |  |  | 12 | C | SHE | [12 empty] | 01
C1 | C1-FE-002 | C1-X-010 | FLD |  | AVERAGING PITOT TUBE | C1 COMMONEXTRACT |  | C1 EXTRACT LOW AIR FLOW | 13???? | [12 empty] | TORBAR | 401 | KF0027/P3 |  |  |  | 01
C1 | C1-FT-002 | C1-X-010 | FLD |  | TRANSMITTER-PRESSURE | C1 COMMONEXTRACT |  | C1 EXTRACT LOW AIR FLOW | 13???? | 0 to 1 mbarg |  |  | 12 | C | SHE | I.S | [5 empty] | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 01
C1 | C1-HS-010 | C1-X-010 | LCP |  | HAND SWITCH | C1 COMMONEXTRACT |  | C1 EXTRACT LOW AIR FLOW | 13???? |  |  |  | 12 | F | SHE | I.S | [11 empty] | 01
C1 | C1-XA-010 | C1-X-010 | LCP |  | ALARM SOUNDER | C1 COMMONEXTRACT |  | C1 EXTRACT LOW AIR FLOW | 13???? |  |  |  | 12 | F | SHE | I.S | [11 empty] | 01
C1 | C1-XL-010A | C1-X-010 | LCP |  | INDICATOR LAMP | C1 COMMONEXTRACT |  | C1 EXTRACT LOW AIR FLOW | 13???? |  |  |  | 12 | F | SHE | I.S | [11 empty] | 01
C1 | C1-XL-010B | C1-X-010 | LCP |  | INDICATOR LAMP | C1 COMMONEXTRACT |  | C1 EXTRACT LOW AIR FLOW | 13???? |  |  |  | 12 | F | SHE | I.S | [11 empty] | 01
CD01 | CD01-DIC-001 | CD01-D-001 | PCS | 107-JK | INDICATING CONTROLLER - SPEED |  |  | P1 ALKALI DOSING PUMP | [11 empty] | 0 | [7 empty] | 01
CD01 | CD01-DS-001 | CD01-D-001 | MCC | 107-JK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P1 ALKALI DOSING PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CD01 | CD01-DY-001 | CD01-D-001 | MCC | 107-JK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P1 ALKALI DOSING PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CD01 | CD01-DYC-001 | CD01-D-001 | MCC | 107-JK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 045.1 | P1 ALKALI DOSING PUMP | 8550 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
CD01 | CD01-DIC-002 | CD01-D-002 | PCS | 107-JK | INDICATING CONTROLLER - SPEED |  |  | P2 ALKALI DOSING PUMP | [11 empty] | 0 | [7 empty] | 01
CD01 | CD01-DS-002 | CD01-D-002 | MCC | 107-JK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P2 ALKALI DOSING PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CD01 | CD01-DY-002 | CD01-D-002 | MCC | 107-JK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P2 ALKALI DOSING PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CD01 | CD01-DYC-002 | CD01-D-002 | MCC | 107-JK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 045.1 | P2 ALKALI DOSING PUMP | 8551 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
CD01 | CD01-LI-001 | CD01-L-001 | PCS | 107-JK | INDICATOR - LEVEL |  |  | ST1 LEVEL | [11 empty] | 0 | [7 empty] | 01
CD01 | CD01-LT-001 | CD01-L-001 | PKG | 107-JK | TRANSMITTER - LEVEL | CD01-ST1 | 045.1 | ST1 LEVEL | 8554 | 0 to 1500 l | +/- 5% | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | PROSONIC T FMU130E-BB32 |  | TI702-SP-5165 |  |  | 01
CD01 | CD01-LAH-002 | CD01-L-002 | PCS | 107-JK | ALARM - LEVEL - HIGH |  |  | ST1 HIGH LEVEL |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
CD01 | CD01-LE-002 | CD01-L-002 | PKG | 107-JK | ELEMENT - LEVEL | CD01-ST1 | 045.1 | ST1 HIGH LEVEL |  | Fixed | - | SHE | 12 | F |  | I.S |  |  |  | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD01 | CD01-LSH-002 | CD01-L-002 | CPR | 107-JK | SWITCH - LEVEL - HIGH |  | 045.1 | ST1 HIGH LEVEL | 8552 | - | - | SHE | 12 | F |  | N.I.S | DI |  |  | 35 | UTIL | VENDOR SUPPLY |  |  |  | CAL 6 MNTH FROM CD01-LSH-004 |  | 03
CD01 | CD01-LI-003 | CD01-L-003 | PKG | 107-JK | INDICATOR - LEVEL GAUGE | CD01-ST1 | 045.1 | ST1 LEVEL |  | - | - | REF | REQ | F | [5 empty] | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD01 | CD01-LAH-004 | CD01-L-004 | PCS | 107-JK | ALARM - LEVEL - HIGH |  |  | BUND HIGH LEVEL |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
CD01 | CD01-LE-004 | CD01-L-004 | PKG | 107-JK | ELEMENT - LEVEL | CD01-ST1 | 045.1 | BUND HIGH LEVEL |  | Fixed | - | SHE | 12 | F |  | I.S |  |  |  | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD01 | CD01-LSH-004 | CD01-L-004 | CPR | 107-JK | SWITCH - LEVEL - HIGH |  | 045.1 | BUND HIGH LEVEL | 8553 | - | - | SHE | 12 | F |  | N.I.S | DI |  |  | 35 | UTIL | ENDRESS + HAUSER | FDL30-6YY9A70 |  | TI702-SP-5045 | CAL 6 MNTH FROM CD01-LSH-002 |  | 03
CD01 | CD01-PI-001 | CD01-P-001 | PKG | 107-JK | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-W-9025822 | 045.1 | P1 DISCHARGE PRESSURE |  | 0 to 16 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD01 | CD01-PSV-002 | CD01-P-002 | PKG | 107-JK | PRESSURE RELIEF VALVE |  | 045.1 | P1 BYPASS RELIEF |  | 7 barg | +/- 10% |  | 24 | C | [5 empty] | 0 | [7 empty] | 01
CD01 | CD01-PI-003 | CD01-P-003 | PKG | 107-JK | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-W-9025823 | 045.1 | P2 DISCHARGE PRESSURE |  | 0 to16 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD01 | CD01-PSV-004 | CD01-P-004 | PKG | 107-JK | PRESSURE RELIEF VALVE |  | 045.1 | P2 BYPASS RELIEF |  | 7 barg | +/- 10% |  | 24 | C | [5 empty] | 0 | [7 empty] | 01
CD01 | CD01-PRV-005 | CD01-P-005 | PKG | 107-JK | CONTROL VALVE SELF ACTUATING | 40-P-PT1A-W-9025822 | 045.1 | P1 DISCHARGE |  |  | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CD01 | CD01-PRV-006 | CD01-P-006 | PKG | 107-JK | CONTROL VALVE SELF ACTUATING | 40-P-PT1A-W-9025823 | 045.1 | P2 DISCHARGE |  |  | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CD02 | CD02-DIC-001 | CD02-D-001 | PCS | 107-JK | INDICATING CONTROLLER - SPEED |  |  | P1 ACID DOSING PUMP | [11 empty] | 0 | [7 empty] | 01
CD02 | CD02-DS-001 | CD02-D-001 | MCC | 107-JK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P1 ACID DOSING PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CD02 | CD02-DY-001 | CD02-D-001 | MCC | 107-JK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P1 ACID DOSING PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CD02 | CD02-DYC-001 | CD02-D-001 | MCC | 107-JK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 045.2 | P1 ACID DOSING PUMP | 8555 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
CD02 | CD02-DIC-002 | CD02-D-002 | PCS | 107-JK | INDICATING CONTROLLER - SPEED |  |  | P2 ACID DOSING PUMP | [11 empty] | 0 | [7 empty] | 01
CD02 | CD02-DS-002 | CD02-D-002 | MCC | 107-JK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P2 ACID DOSING PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CD02 | CD02-DY-002 | CD02-D-002 | MCC | 107-JK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P2 ACID DOSING PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CD02 | CD02-DYC-002 | CD02-D-002 | MCC | 107-JK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 045.2 | P2 ACID DOSING PUMP | 8556 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
CD02 | CD02-LI-001 | CD02-L-001 | PCS | 107-JK | INDICATOR - LEVEL |  |  | ST1 LEVEL | [11 empty] | 0 | [7 empty] | 01
CD02 | CD02-LT-001 | CD02-L-001 | PKG | 107-JK | TRANSMITTER - LEVEL | CD02-ST1 | 045.2 | ST1 LEVEL | 8559 | 0 to 1500 l | +/- 5% | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | FMU40-1RB2A2 | TI702-SP-5105 | TI702-SP-5105 |  |  | 01
CD02 | CD02-LAH-002 | CD02-L-002 | PCS | 107-JK | ALARM - LEVEL - HIGH |  |  | ST1 HIGH LEVEL |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
CD02 | CD02-LE-002 | CD02-L-002 | PKG | 107-JK | ELEMENT - LEVEL | CD02-ST1 | 045.2 | ST1 HIGH LEVEL |  | Fixed | - | SHE | 12 | F |  | I.S |  |  |  | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD02 | CD02-LSH-002 | CD02-L-002 | CPR | 107-JK | SWITCH - LEVEL - HIGH |  | 045.2 | ST1 HIGH LEVEL | 8557 | - | - | SHE | 12 | F |  | N.I.S | DI |  |  | 35 | UTIL | ENDRESS + HAUSER | FTL51-GYY9BE7G4A |  |  | CAL 6 MNTH FROM CD02-LSH-004 |  | 03
CD02 | CD02-LI-003 | CD02-L-003 | PKG | 107-JK | INDICATOR - LEVEL GAUGE | CD02-ST1 | 045.2 | ST1 LEVEL |  | - | - | REF | REQ | F | [5 empty] | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD02 | CD02-LAH-004 | CD02-L-004 | PCS | 107-JK | ALARM - LEVEL - HIGH |  |  | BUND HIGH LEVEL |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
CD02 | CD02-LE-004 | CD02-L-004 | PKG | 107-JK | ELEMENT - LEVEL | CD02-ST1 | 045.2 | BUND HIGH LEVEL |  | Fixed | - | SHE | 12 | F |  | I.S |  |  |  | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD02 | CD02-LSH-004 | CD02-L-004 | CPR | 107-JK | SWITCH - LEVEL - HIGH |  | 045.2 | BUND HIGH LEVEL | 8558 | - | - | SHE | 12 | F |  | N.I.S | DI |  |  | 35 | UTIL | ENDRESS + HAUSER | FTL51-GYY9DE7G4A |  |  | CAL 6 MNTH FROM CD02-LSH-002 |  | 03
CD02 | CD02-PI-001 | CD02-P-001 | PKG | 107-JK | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-W-9025820 | 045.2 | P1 DISCHARGE PRESSURE |  | 0 to 16 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD02 | CD02-PSV-002 | CD02-P-002 | PKG | 107-JK | PRESSURE RELIEF VALVE |  | 045.2 | P1 BYPASS RELIEF |  | 7 barg | +/- 10% |  | 24 | C | [5 empty] | 0 | [7 empty] | 01
CD02 | CD02-PI-003 | CD02-P-003 | PKG | 107-JK | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-W-9025821 | 045.2 | P2 DISCHARGE PRESSURE |  | 0 to 16 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | VENDOR SUPPLY | [5 empty] | 01
CD02 | CD02-PSV-004 | CD02-P-004 | PKG | 107-JK | PRESSURE RELIEF VALVE |  | 045.2 | P2 BYPASS RELIEF |  | 7 barg | +/- 10% |  | 24 | C | [5 empty] | 0 | [7 empty] | 01
CD02 | CD02-PRV-005 | CD02-P-005 | PKG | 107-JK | CONTROL VALVE SELF ACTUATING | 40-P-PT1A-W-9025820 | 045.2 | P1 DISCHARGE |  |  | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CD02 | CD02-PRV-006 | CD02-P-006 | PKG | 107-JK | CONTROL VALVE SELF ACTUATING | 40-P-PT1A-W-9025821 | 045.2 | P2 DISCHARGE |  |  | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CD02 | CD02-RV-001 | CD02-R-001 | PKG | 107-JK | VACUUM BREATHER VALVE | CD02-ST1 | 045.2 | ST1 RELIEF |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-AE-001 | CMP-A-001 | PKG | 107-QA | ELEMENT - ANALYSIS - H2O | CMP | 042.1 | AIR DEWPOINT |  | - | - | SHE | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-AI-001 | CMP-A-001 | PCS | 107-QA | INDICATOR - ANALYSIS |  |  | AIR DEWPOINT |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 01
CMP | CMP-AT-001 | CMP-A-001 | PKG | 107-QA | TRANSMITTER - ANALYSIS - H2O | CMP | 042.1 | AIR DEWPOINT | 8560 | -80 to 20 d.pt | +/- 1% | SHE | By request | C |  | N.I.S | AI |  |  | 12 | UTIL | MITCHELL | CERMET |  |  | DEWPOINT |  | 44
CMP | CMP-AI-002 | CMP-A-002 | PCS | 107-QA | INDICATOR - ANALYSIS |  |  | AIR DEWPOINT |  |  |  | REF | By request | [6 empty] | 0 |  | MITCHELL | EA2-TX-100 |  |  | DEWPOINT |  | 44
CMP | CMP-AI-003 | CMP-A-003 | PCS | 107-QA | INDICATOR - ANALYSIS |  |  | AIR DEWPOINT |  |  |  | REF | By request | [6 empty] | 0 |  | MITCHELL | EA2-TX-100 |  |  | DEWPOINT |  | 44
CMP | CMP-CV-008 | CMP-C-008 | FLD | 107-QA | BALL VALVE - ON/OFF - F.C. | 40-IA-SS1U-0-9027902 | 042.1 | INSTRUMENT AIR SUPPLY | 7097 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CMP | CMP-CY-008 | CMP-C-008 | FLD | 107-QA | SOLENOID VALVE | RACK MOUNTED |  | INSTRUMENT AIR SUPPLY | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
CMP | CMP-ZSC-008 | CMP-C-008 | FLD | 107-QA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | INSTRUMENT AIR SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
CMP | CMP-ZSO-008 | CMP-C-008 | FLD | 107-QA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | INSTRUMENT AIR SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
CMP | CMP-CV-009 | CMP-C-009 | FLD | 107-QA | BALL VALVE - ON/OFF - F.C. | 40-CA-SS1U-0-9027904 | 042.1 | PLANT AIR SUPPLY | 7098 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CMP | CMP-CY-009 | CMP-C-009 | FLD | 107-QA | SOLENOID VALVE | RACK MOUNTED |  | PLANT AIR SUPPLY | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
CMP | CMP-ZSC-009 | CMP-C-009 | FLD | 107-QA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PLANT AIR SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
CMP | CMP-ZSO-009 | CMP-C-009 | FLD | 107-QA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PLANT AIR SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
CMP | CMP-DS-001 | CMP-D-001 | LCP | 107-QA | DRIVE - AVAILABLE | CMP CONTROL PANEL | 042.1 | CMP01 COMPRESSOR |  | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CMP | CMP-DY-001 | CMP-D-001 | LCP | 107-QA | DRIVE - RUNNING | CMP CONTROL PANEL | 042.1 | CMP01 COMPRESSOR | 8561 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CMP | CMP-DS-002 | CMP-D-002 | LCP | 107-QA | DRIVE - AVAILABLE | CMP CONTROL PANEL | 042.1 | CMP02 COMPRESSOR |  | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CMP | CMP-DY-002 | CMP-D-002 | LCP | 107-QA | DRIVE - RUNNING | CMP CONTROL PANEL | 042.1 | CMP02 COMPRESSOR | 8562 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CMP | CMP-PT-001 | CMP-P-001 | PKG | 107-QA | TRANSMITTER - PRESSURE | CMP-01 | 042.1 | COMPRESSOR PRESSURE CONTROL |  | 0 to 16 barg | +/- 2% | SHE | 12 | C | [5 empty] | 0 |  | METACENTRE | Y04CM29.00 |  |  |  |  | 44
CMP | CMP-PI-003 | CMP-P-003 | PKG | 107-QA | PRESSURE GAUGE | CMP-GR2 | 042.1 | GR2 PRESSURE |  | 0 to 16 barg | +/- 1% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PSV-004 | CMP-P-004 | PKG | 107-QA | PRESSURE RELIEF VALVE | CMP | 042.1 | GR2 RELIEF |  | 11.55 barg | +/- 10% |  | 24 | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PDAH-005 | CMP-P-005 | PCS | 107-QA | ALARM - PRESSURE - DIFF - HIGH |  | 042.1 | DD1 DIFF PRESSURE |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
CMP | CMP-PDSH-005 | CMP-P-005 | PKG | 107-QA | SWITCH - PRESSURE - DIFF - HIGH | CMP | 042.1 | DD1 DIFF PRESSURE | 8563 | set @ 1 bar | +/- 1% | SHE | By request | C |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CMP | CMP-PI-005 | CMP-P-005 | PCS | 107-QA | INDICATOR - PRESSURE | CMP01-GR1 AIR VESSEL | 042.1 | DD1 DIFF PRESSURE |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 44
CMP | CMP-PI-006 | CMP-P-006 | PCS | 107-QA | INDICATOR - PRESSURE | CMP01-GR1 AIR VESSEL | 042.1 | GR1 PRESSURE |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 44
CMP | CMP-PT-006 | CMP-P-006 | FLD | 107-QA | TRANSMITTER - PRESSURE | CMP01-GR1 AIR VESSEL | 042.1 | GR1 PRESSURE | 8564 | 0 to 16 barg | +/- 2% | SHE | 24 | C |  | N.I.S | AI |  |  | 12 | UTIL | ROSEMOUNT | 3051TG3A2B21BI1 | PFIZER |  |  |  | 44
CMP | CMP-PI-007 | CMP-P-007 | PKG | 107-QA | PRESSURE GAUGE | CMP01-GR1 AIR VESSEL | 042.1 | GR1 PRESSURE |  | 0 to 16 barg | +/- 1% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PSV-008 | CMP-P-008 | PKG | 107-QA | PRESSURE RELIEF VALVE | CMP01-GR1 AIR VESSEL | 042.1 | GR1 RELIEF |  | 10 barg | +/- 10% |  | 24 | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PRV-009 | CMP-P-009 | PKG | 107-QA | CONTROL VALVE SELF ACTUATING | CMP | 042.1 | AIR SYSTEM 6.5 BARG |  | set @ 6.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PSV-010 | CMP-P-010 | PKG | 107-QA | PRESSURE RELIEF VALVE | CMP | 042.1 | AIR SYSTEM RELIEF |  | 7 barg | +/- 10% |  | 24 | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PI-011 | CMP-P-011 | PCS | 107-QA | INDICATOR - PRESSURE |  | 042.1 | BREATH. AIR PRESSURE | [11 empty] | 0 | [7 empty] | 01
CMP | CMP-PT-011 | CMP-P-011 | PKG | 107-QA | TRANSMITTER - PRESSURE | 50-BA-SS1U-0-9027910 | 042.1 | BREATH. AIR PRESSURE | 8565 | 0 to 16 barg | +/- 1% | SHE | 12 | C |  | N.I.S | AI |  |  | 12 | UTIL | [6 empty] | 44
CMP | CMP-PDI-012 | CMP-P-012 | PKG | 107-QA | INDICATOR - DIFF PRESSURE | CMP | 042.1 | AF1 DIFF PRESSURE |  | 0 to 0.7 bar | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PDI-013 | CMP-P-013 | PKG | 107-QA | INDICATOR - DIFF PRESSURE | CMP | 042.1 | AF3 DIFF PRESSURE |  | 0 to 0.7 bar | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PDI-014 | CMP-P-014 | PKG | 107-QA | INDICATOR - DIFF PRESSURE | CMP | 042.1 | AF2 DIFF PRESSURE |  | 0 to 0.7 bar | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PDI-015 | CMP-P-015 | PKG | 107-QA | INDICATOR - DIFF PRESSURE | CMP | 042.1 | AF4 DIFF PRESSURE |  | 0 to 0.7 bar | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PDI-016 | CMP-P-016 | PKG | 107-QA | INDICATOR - DIFF PRESSURE | CMP | 042.1 | AF9 DIFF PRESSURE |  | 0 to 0.7 bar | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PDI-017 | CMP-P-017 | PKG | 107-QA | INDICATOR - DIFF PRESSURE | CMP | 042.1 | AF5 DIFF PRESSURE |  | 0 to 0.7 bar | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PDI-018 | CMP-P-018 | PKG | 107-QA | INDICATOR - DIFF PRESSURE | CMP | 042.1 | AF6 DIFF PRESSURE |  | 0 to 0.7 bar | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PDI-019 | CMP-P-019 | PKG | 107-QA | INDICATOR - DIFF PRESSURE | CMP | 042.1 | AF7 DIFF PRESSURE |  | 0 to 0.7 bar | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PDI-020 | CMP-P-020 | PKG | 107-QA | INDICATOR - DIFF PRESSURE | CMP | 042.1 | AF8 DIFF PRESSURE |  | 0 to 0.7 bar | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PRV-021 | CMP-P-021 | PKG | 107-QA | CONTROL VALVE SELF ACTUATING | CMP | 042.1 | AIR SYSTEM 6.5 BARG |  | set @ 6.0 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PAL-022 | CMP-P-022 | PCS | 107-QA | ALARM - PRESSURE - LOW |  |  | BREATH. AIR LOW PRESSURE |  |  |  | SHE | 12 | [6 empty] | 0 | [7 empty] | 44
CMP | CMP-PSL-022 | CMP-P-022 | FLD | 107-QA | SWITCH - PRESSURE - LOW | 50-BA-SS1U-0-9027900 | 042.3 | BREATH. AIR LOW PRESSURE | 8115 | set @ 5barg | +/- 1% | SHE | 12 | C | SIL | I.S |  | DI |  | 32 | SIS | DELTA CONTROLS LTD | WS210GEAH2X300APB | KP0012 | TI702-SP-5119 |  |  | 01
CMP | CMP-PI-023 | CMP-P-023 | PKG | 107-QA | PRESSURE GAUGE | CMP | 042.1 | PRV-009 PRESSURE |  | 0 to 10 barg | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PI-024 | CMP-P-024 | PKG | 107-QA | PRESSURE GAUGE | CMP | 042.1 | PRV-021 PRESSURE |  | 0 to 10 barg | +/- 5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PI-025 | CMP-P-025 | PKG | 107-QA | PRESSURE GAUGE | CMP | 042.1 | CMP01 PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PI-026 | CMP-P-026 | PKG | 107-QA | PRESSURE GAUGE | CMP | 042.1 | CMP02 PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PRV-027 | CMP-P-027 | PKG | 107-QA | CONTROL VALVE SELF ACTUATING | CMP | 042.1 | AIR SYSTEM 6.5 BARG |  | set @ 6.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CMP | CMP-PRV-028 | CMP-P-028 | PKG | 107-QA | CONTROL VALVE SELF ACTUATING | CMP | 042.1 | AIR SYSTEM 6.5 BARG |  | set @ 6.5 barg | +/- 5% | REF | REQ | C | [13 empty] | 01
CMP | CMP-PT-028 | CMP-P-028 | FLD | 107-QA | TRANSMITTER - PRESSURE | CMP01-GR1 AIR VESSEL | 042.1 | GR1 PRESSURE | 13420 | 0 to 16 barg | +/- 2% | SHE | 24 | C |  | N.I.S | AI |  |  | 12 | UTIL | ROSEMOUNT | 3051TG3A2B21BI1 |  | TI702-SP-5046 |  |  | 44
CMP | CMP-PT-029 | CMP-P-029 | FLD | 107-QA | TRANSMITTER - PRESSURE | CMP01-GR1 AIR VESSEL | 042.1 | GR1 PRESSURE | 13421 | 0 to 16 barg | +/- 2% | SHE | 24 | C |  | N.I.S | AI |  |  | 12 | UTIL | ROSEMOUNT | 3051TG3A2B21BI1 |  | TI702-SP-5046 |  |  | 44
CMP | CMP-YA-001 | CMP-Y-001 | LCP | 107-QA | ALARM - COMMON | CMP CONTROL PANEL | 042.1 | COMMON ALARM | 8566 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CP01 | CP01-CV-001 | CP01-C-001 | FLD | 107-BK | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029312 | 039.1 | COLD HTF SUPPLY | 7524 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP01 | CP01-CY-001 | CP01-C-001 | FLD | 107-BK | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | [7 empty] | I.S | DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
CP01 | CP01-ZSC-001 | CP01-C-001 | FLD | 107-BK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP01 | CP01-ZSO-001 | CP01-C-001 | FLD | 107-BK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP01 | CP01-CV-002 | CP01-C-002 | FLD | 107-BK | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029104 | 039.1 | HOT HTF SUPPLY | 7114 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP01 | CP01-ZSC-002 | CP01-C-002 | FLD | 107-BK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP01 | CP01-ZSO-002 | CP01-C-002 | FLD | 107-BK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP01 | CP01-CV-003 | CP01-C-003 | FLD | 107-BK | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9021701 | 039.1 | COLD HTF RTN | 6398 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP01 | CP01-DIC-001 | CP01-D-001 | PCS | 107-BK | INDICATING CONTR. - MOTOR DRIVE |  |  | TEMPERED HTF PUMP | [11 empty] | 0 | [7 empty] | 01
CP01 | CP01-DS-001 | CP01-D-001 | MCC | 107-BK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP1 | [6 empty] | 01
CP01 | CP01-DY-001 | CP01-D-001 | MCC | 107-BK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP1 | [6 empty] | 01
CP01 | CP01-DYC-001 | CP01-D-001 | MCC | 107-BK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 039.1 | TEMPERED HTF PUMP | 8567 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
CP01 | CP01-PI-001 | CP01-P-001 | FLD | 107-BK | PRESSURE GAUGE - DIAPHRAGM | 100-HT-CS3A-C-9021700 | 039.1 | PUMP SUCTION PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP01 | CP01-PI-002 | CP01-P-002 | FLD | 107-BK | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9021700 | 039.1 | PUMP DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP01 | CP01-RO-001 | CP01-R-001 | FLD | 107-BK | RESTRICTION ORIFICE PLATE | 40-HT-CS3A-C-9021700 | 039.1 | TEMPERD HTF RECIRC |  | 10 m3/hr |  | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
CP01 | CP01-TE-001 | CP01-T-001 | FLD | 107-BK | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9021700 |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP01 | CP01-TIC-001 | CP01-T-001 | PCS | 107-BK | INDICATING CONTROLLER - TEMPERATURE |  |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP01 | CP01-TT-001 | CP01-T-001 | FLD | 107-BK | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 039.1 | TEMPERED HTF TEMPERATURE | 6586 | -30 to 70 degC | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
CP02 | CP02-CV-001 | CP02-C-001 | FLD | 107-BL | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029414 | 039.2 | COLD HTF SUPPLY | 7525 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP02 | CP02-CY-001 | CP02-C-001 | FLD | 107-BL | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | [7 empty] | I.S | DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
CP02 | CP02-ZSC-001 | CP02-C-001 | FLD | 107-BL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP02 | CP02-ZSO-001 | CP02-C-001 | FLD | 107-BL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP02 | CP02-CV-002 | CP02-C-002 | FLD | 107-BL | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029153 | 039.2 | HOT HTF SUPPLY | 7116 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP02 | CP02-ZSC-002 | CP02-C-002 | FLD | 107-BL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP02 | CP02-ZSO-002 | CP02-C-002 | FLD | 107-BL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP02 | CP02-CV-003 | CP02-C-003 | FLD | 107-BL | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9021741 | 039.2 | COLD HTF RTN | 6399 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP02 | CP02-DIC-001 | CP02-D-001 | PCS | 107-BL | INDICATING CONTR. - MOTOR DRIVE |  |  | TEMPERED HTF PUMP | [11 empty] | 0 | [7 empty] | 01
CP02 | CP02-DS-001 | CP02-D-001 | MCC | 107-BL | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP1 | [6 empty] | 01
CP02 | CP02-DY-001 | CP02-D-001 | MCC | 107-BL | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP1 | [6 empty] | 01
CP02 | CP02-DYC-001 | CP02-D-001 | MCC | 107-BL | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 039.2 | TEMPERED HTF PUMP | 8568 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
CP02 | CP02-PI-001 | CP02-P-001 | FLD | 107-BL | PRESSURE GAUGE - DIAPHRAGM | 100-HT-CS3A-C-9021740 | 039.2 | PUMP SUCTION PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP02 | CP02-PI-002 | CP02-P-002 | FLD | 107-BL | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9021740 | 039.2 | PUMP DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP02 | CP02-RO-001 | CP02-R-001 | FLD | 107-BL | RESTRICTION ORIFICE PLATE | 40-HT-CS3A-C-9021740 | 039.2 | TEMPERED HTF RECIRC |  | 10 m3/hr | - | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
CP02 | CP02-TE-001 | CP02-T-001 | FLD | 107-BL | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9021740 |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP02 | CP02-TIC-001 | CP02-T-001 | PCS | 107-BL | INDICATING CONTROLLER - TEMPERATURE |  |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP02 | CP02-TT-001 | CP02-T-001 | FLD | 107-BL | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 039.2 | TEMPERED HTF TEMPERATURE | 6585 | -30 to 70 degC | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
CP03 | CP03-CV-001 | CP03-C-001 | FLD | 107-CK | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029413 | 039.3 | COLD HTF SUPPLY | 7526 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP03 | CP03-CY-001 | CP03-C-001 | FLD | 107-CK | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
CP03 | CP03-ZSC-001 | CP03-C-001 | FLD | 107-CK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP03 | CP03-ZSO-001 | CP03-C-001 | FLD | 107-CK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP03 | CP03-CV-002 | CP03-C-002 | FLD | 107-CK | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029154 | 039.3 | HOT HTF SUPPLY | 7115 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP03 | CP03-ZSC-002 | CP03-C-002 | FLD | 107-CK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP03 | CP03-ZSO-002 | CP03-C-002 | FLD | 107-CK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP03 | CP03-CV-003 | CP03-C-003 | FLD | 107-CK | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9022701 | 039.3 | COLD HTF RTN | 6400 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP03 | CP03-DIC-001 | CP03-D-001 | PCS | 107-CK | INDICATING CONTR. - MOTOR DRIVE |  |  | TEMPERED HTF PUMP | [11 empty] | 0 | [7 empty] | 01
CP03 | CP03-DS-001 | CP03-D-001 | MCC | 107-CK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
CP03 | CP03-DY-001 | CP03-D-001 | MCC | 107-CK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
CP03 | CP03-DYC-001 | CP03-D-001 | MCC | 107-CK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 039.3 | TEMPERED HTF PUMP | 8569 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
CP03 | CP03-PI-001 | CP03-P-001 | FLD | 107-CK | PRESSURE GAUGE - DIAPHRAGM | 100-HT-CS3A-C-9022700 | 039.3 | PUMP SUCTION PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP03 | CP03-PI-002 | CP03-P-002 | FLD | 107-CK | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9022700 | 039.3 | PUMP DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP03 | CP03-RO-001 | CP03-R-001 | FLD | 107-CK | RESTRICTION ORIFICE PLATE | 40-HT-CS3A-C-9022700 | 039.3 | TEMPERED HTF RECIRC. |  | 10 m3/hr | - | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
CP03 | CP03-TE-001 | CP03-T-001 | FLD | 107-CK | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9022700 |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP03 | CP03-TIC-001 | CP03-T-001 | PCS | 107-CK | INDICATING CONTROLLER - TEMPERATURE |  |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP03 | CP03-TT-001 | CP03-T-001 | FLD | 107-CK | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 039.3 | TEMPERED HTF TEMPERATURE | 6587 | -30 to 70 degC | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
CP04 | CP04-CV-001 | CP04-C-001 | FLD | 107-CL | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029427 | 039.4 | COLD HTF SUPPLY | 7527 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP04 | CP04-CY-001 | CP04-C-001 | FLD | 107-CL | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
CP04 | CP04-ZSC-001 | CP04-C-001 | FLD | 107-CL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP04 | CP04-ZSO-001 | CP04-C-001 | FLD | 107-CL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP04 | CP04-CV-002 | CP04-C-002 | FLD | 107-CL | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029164 | 039.4 | HOT HTF SUPPLY | 7117 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP04 | CP04-ZSC-002 | CP04-C-002 | FLD | 107-CL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP04 | CP04-ZSO-002 | CP04-C-002 | FLD | 107-CL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP04 | CP04-CV-003 | CP04-C-003 | FLD | 107-CL | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9022741 | 039.4 | COLD HTF RTN | 6402 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP04 | CP04-CV-004 | CP04-C-004 | FLD | 107-CL | GLOBE VALVE - CONTROL - STAYPUT | 80-HTF-CS3A-C-9022740 | 039.4 | TEMPERED HTF RECIRC. | 6449 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP04 | CP04-DIC-001 | CP04-D-001 | PCS | 107-CL | INDICATING CONTR. - MOTOR DRIVE |  |  | TEMPERED HTF PUMP | [11 empty] | 0 | [7 empty] | 01
CP04 | CP04-DS-001 | CP04-D-001 | MCC | 107-CL | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
CP04 | CP04-DY-001 | CP04-D-001 | MCC | 107-CL | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
CP04 | CP04-DYC-001 | CP04-D-001 | MCC | 107-CL | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 039.4 | TEMPERED HTF PUMP | 8570 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
CP04 | CP04-FIC-001 | CP04-F-001 | PCS | 107-CL | INDICATING CONTROLLER - FLOW |  |  | TEMPERED HTF FLOW | [11 empty] | 0 | [7 empty] | 01
CP04 | CP04-FT-001 | CP04-F-001 | FLD | 107-CL | TRANSMITTER - FLOW | 100-HT-CS3A-C-9022740 | 039.4 | TEMPERED HTF FLOW | 8240 | 20-100 m3/hr | +/- 2% | REF | 5 YR | C |  | I.S | AI |  |  | 11 | GP2 | ENDRESS + HAUSER | 77FS1HJA211B04 | KF0008 | TI702-SP-5071 |  |  | 01
CP04 | CP04-PI-001 | CP04-P-001 | FLD | 107-CL | PRESSURE GAUGE - DIAPHRAGM | 150-HT-CS3A-C-9022740 | 039.4 | PUMP SUCTION PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP04 | CP04-PI-002 | CP04-P-002 | FLD | 107-CL | PRESSURE GAUGE - DIAPHRAGM | 100-HT-CS3A-C-9022740 | 039.4 | PUMP DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP04 | CP04-TE-001 | CP04-T-001 | FLD | 107-CL | ELEMENT - TEMPERATURE - RTD | 100-HT-CS3A-C-9022740 |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP04 | CP04-TIC-001 | CP04-T-001 | PCS | 107-CL | INDICATING CONTROLLER - TEMPERATURE |  |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP04 | CP04-TT-001 | CP04-T-001 | FLD | 107-CL | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 039.4 | TEMPERED HTF TEMPERATURE | 6588 | -30 to 70 degC | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
CP05 | CP05-CV-001 | CP05-C-001 | FLD | 107-DK | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029519 | 039.7 | COLD HTF SUPPLY | 7528 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP05 | CP05-CY-001 | CP05-C-001 | FLD | 107-DK | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | [7 empty] | I.S | DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
CP05 | CP05-ZSC-001 | CP05-C-001 | FLD | 107-DK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP05 | CP05-ZSO-001 | CP05-C-001 | FLD | 107-DK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP05 | CP05-CV-002 | CP05-C-002 | FLD | 107-DK | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029202 | 039.7 | HOT HTF SUPPLY | 7129 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP05 | CP05-ZSC-002 | CP05-C-002 | FLD | 107-DK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP05 | CP05-ZSO-002 | CP05-C-002 | FLD | 107-DK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP05 | CP05-CV-003 | CP05-C-003 | FLD | 107-DK | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9023741 | 039.7 | COLD HTF RTN | 6404 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP05 | CP05-CV-004 | CP05-C-004 | FLD | 107-DK | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9023740 | 039.7 | TEMPERED HTF RECIRC. | 8184 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP05 | CP05-DIC-001 | CP05-D-001 | PCS | 107-DK | INDICATING CONTR. - MOTOR DRIVE |  |  | TEMPERED HTF PUMP | [11 empty] | 0 | [7 empty] | 01
CP05 | CP05-DS-001 | CP05-D-001 | MCC | 107-DK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | FG1 | [6 empty] | 01
CP05 | CP05-DY-001 | CP05-D-001 | MCC | 107-DK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | FG1 | [6 empty] | 01
CP05 | CP05-DYC-001 | CP05-D-001 | MCC | 107-DK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 039.7 | TEMPERED HTF PUMP | 8571 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
CP05 | CP05-FIC-001 | CP05-F-001 | PCS | 107-DK | INDICATING CONTROLLER - FLOW |  |  | TEMPERED HTF FLOW | [11 empty] | 0 | [7 empty] | 01
CP05 | CP05-FT-001 | CP05-F-001 | FLD | 107-DK | TRANSMITTER - FLOW | 100-HT-CS3A-C-9023740 | 039.7 | TEMPERED HTF FLOW | 8244 | 20-100 m3/hr | +/- 2% | REF | 5 YR | C |  | I.S | AI |  |  | 11 | FG1 | ENDRESS + HAUSER | 77FS1HJA211B04 | KF0008 | TI702-SP-5071 |  |  | 01
CP05 | CP05-PI-001 | CP05-P-001 | FLD | 107-DK | PRESSURE GAUGE - DIAPHRAGM | 150-HT-CS3A-C-9023740 | 039.7 | PUMP SUCTION PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP05 | CP05-PI-002 | CP05-P-002 | FLD | 107-DK | PRESSURE GAUGE - DIAPHRAGM | 100-HT-CS3A-C-9023740 | 039.7 | PUMP DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP05 | CP05-RO-001 | CP05-R-001 | DEL | 107-DK | RESTRICTION ORIFICE PLATE | DELETED |  |  |  | 10 m3/hr | * | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  | DELETED |  | 01
CP05 | CP05-TE-001 | CP05-T-001 | FLD | 107-DK | ELEMENT - TEMPERATURE - RTD | 100-HT-CS3A-C-9023740 |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP05 | CP05-TIC-001 | CP05-T-001 | PCS | 107-DK | INDICATING CONTROLLER - TEMPERATURE |  |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP05 | CP05-TT-001 | CP05-T-001 | FLD | 107-DK | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 039.7 | TEMPERED HTF TEMPERATURE | 8143 | -30 to 70 degC | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
CP06 | CP06-CV-001 | CP06-C-001 | FLD | 107-DL | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029511 | 039.5 | COLD HTF SUPPLY | 7529 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP06 | CP06-CY-001 | CP06-C-001 | FLD | 107-DL | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | [7 empty] | I.S | DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
CP06 | CP06-ZSC-001 | CP06-C-001 | FLD | 107-DL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP06 | CP06-ZSO-001 | CP06-C-001 | FLD | 107-DL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP06 | CP06-CV-002 | CP06-C-002 | FLD | 107-DL | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029256 | 039.5 | HOT HTF SUPPLY | 7118 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP06 | CP06-ZSC-002 | CP06-C-002 | FLD | 107-DL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP06 | CP06-ZSO-002 | CP06-C-002 | FLD | 107-DL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP06 | CP06-CV-003 | CP06-C-003 | FLD | 107-DL | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9023701 | 039.5 | COLD HTF RTN | 6401 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP06 | CP06-DIC-001 | CP06-D-001 | PCS | 107-DL | INDICATING CONTR. - MOTOR DRIVE |  |  | TEMPERED HTF PUMP | [11 empty] | 0 | [7 empty] | 01
CP06 | CP06-DS-001 | CP06-D-001 | MCC | 107-DL | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | FG1 | [6 empty] | 01
CP06 | CP06-DY-001 | CP06-D-001 | MCC | 107-DL | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | FG1 | [6 empty] | 01
CP06 | CP06-DYC-001 | CP06-D-001 | MCC | 107-DL | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 039.5 | TEMPERED HTF PUMP | 8572 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
CP06 | CP06-PI-001 | CP06-P-001 | FLD | 107-DL | PRESSURE GAUGE - DIAPHRAGM | 100-HT-CS3A-C-9023700 | 039.5 | PUMP SUCTION PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP06 | CP06-PI-002 | CP06-P-002 | FLD | 107-DL | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9023700 | 039.5 | PUMP DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP06 | CP06-RO-001 | CP06-R-001 | FLD | 107-DL | RESTRICTION ORIFICE PLATE | 40-HT-CS3A-C-9023700 | 039.5 | TEMPERED HTF RECIRC. |  | 10 m3/hr | - | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
CP06 | CP06-TE-001 | CP06-T-001 | FLD | 107-DL | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9023700 |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP06 | CP06-TIC-001 | CP06-T-001 | PCS | 107-DL | INDICATING CONTROLLER - TEMPERATURE |  |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP06 | CP06-TT-001 | CP06-T-001 | FLD | 107-DL | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 039.5 | TEMPERED HTF TEMPERATURE | 6589 | -30 to 70 degC | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
CP07 | CP07-CV-001 | CP07-C-001 | FLD | 107-EK | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029609 | 039.6 | COLD HTF SUPPLY | 7530 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP07 | CP07-CY-001 | CP07-C-001 | FLD | 107-EK | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
CP07 | CP07-ZSC-001 | CP07-C-001 | FLD | 107-EK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP07 | CP07-ZSO-001 | CP07-C-001 | FLD | 107-EK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP07 | CP07-CV-002 | CP07-C-002 | FLD | 107-EK | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029259 | 039.6 | HOT HTF SUPPLY | 7119 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
CP07 | CP07-ZSC-002 | CP07-C-002 | FLD | 107-EK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP07 | CP07-ZSO-002 | CP07-C-002 | FLD | 107-EK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
CP07 | CP07-CV-003 | CP07-C-003 | FLD | 107-EK | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9024701 | 039.6 | COLD HTF RTN | 6403 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP07 | CP07-CV-004 | CP07-C-004 | FLD | 107-EK | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9024700 | 039.6 | TEMPERED HTF RECIRC. | 6450 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
CP07 | CP07-DIC-001 | CP07-D-001 | PCS | 107-EK | INDICATING CONTR. - MOTOR DRIVE |  |  | TEMPERED HTF PUMP | [11 empty] | 0 | [7 empty] | 01
CP07 | CP07-DS-001 | CP07-D-001 | MCC | 107-EK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | C1 | [6 empty] | 01
CP07 | CP07-DY-001 | CP07-D-001 | MCC | 107-EK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TEMPERED HTF PUMP | [7 empty] | N.I.S | DI |  |  | 35 | C1 | [6 empty] | 01
CP07 | CP07-DYC-001 | CP07-D-001 | MCC | 107-EK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 039.6 | TEMPERED HTF PUMP | 8573 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
CP07 | CP07-FIC-001 | CP07-F-001 | PCS | 107-EK | INDICATING CONTROLLER - FLOW |  |  | TEMPERED HTF FLOW | [11 empty] | 0 | [7 empty] | 01
CP07 | CP07-FT-001 | CP07-F-001 | FLD | 107-EK | TRANSMITTER - FLOW | 100-HT-CS3A-C-9024700 | 039.6 | TEMPERED HTF FLOW | 8241 | 20-100 m3/hr | +/- 2% | REF | 5 YR | C |  | I.S | AI |  |  | 11 | C1 | ENDRESS + HAUSER | 77FS1HJA211B04 | KF0008 | TI702-SP-5071 |  |  | 01
CP07 | CP07-PI-001 | CP07-P-001 | FLD | 107-EK | PRESSURE GAUGE - DIAPHRAGM | 150-HT-CS3A-C-9024700 | 039.6 | PUMP SUCTION PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP07 | CP07-PI-002 | CP07-P-002 | FLD | 107-EK | PRESSURE GAUGE - DIAPHRAGM | 100-HT-CS3A-C-9024700 | 039.6 | PUMP DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
CP07 | CP07-TE-001 | CP07-T-001 | FLD | 107-EK | ELEMENT - TEMPERATURE - RTD | 100-HT-CS3A-C-9024700 |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP07 | CP07-TIC-001 | CP07-T-001 | PCS | 107-EK | INDICATING CONTROLLER - TEMPERATURE |  |  | TEMPERED HTF TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
CP07 | CP07-TT-001 | CP07-T-001 | FLD | 107-EK | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 039.6 | TEMPERED HTF TEMPERATURE | 6590 | -30 to 70 degC | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
CR01 | CR01-LI-001 | CR01-L-001 | PKG | 108-AA | INDICATOR - LEVEL GAUGE | CR01-ST1 | 022.0 | CR01-ST1 LEVEL |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
CR01 | CR01-LC-002 | CR01-L-002 | LCP | 108-AA | CONTROLLER - LEVEL | ADJ CR01-CP1/CP2 | 022.0 | CR01-ST1 LEVEL CONTROL |  | - | - | REF | REQ | F | [5 empty] | 0 | [5 empty] | LEVEL CONTROLS |  | 01
CR01 | CR01-LSH-002 | CR01-L-002 | PKG | 108-AA | SWITCH - LEVEL - HIGH | CR01-ST1 | 022.0 | CR01-ST1 LEVEL CONTROL |  | Fixed | - | REF | REQ | F | [5 empty] | 0 | [5 empty] | TO LOCAL CONTROL PANEL |  | 01
CR01 | CR01-LSL-002 | CR01-L-002 | PKG | 108-AA | SWITCH - LEVEL - LOW | CR01-ST1 | 022.0 | CR01-ST1 LEVEL CONTROL |  | Fixed | - | REF | REQ | F | [5 empty] | 0 | [5 empty] | TO LOCAL CONTROL PANEL |  | 01
CR01 | CR01-LSHH-003 | CR01-L-003 | PKG | 108-AA | SWITCH - LEVEL - HI HI | CR01-ST1 | 022.0 | CR01-ST1 HIGH HIGH ALARM |  | Fixed | - | REF | REQ | F | [5 empty] | 0 | [5 empty] | TO LOCAL CONTROL PANEL |  | 01
CR01 | CR01-YA-001 | CR01-Y-001 | PCS | 108-AA | ALARM - COMMON |  |  | CR01 COMMOM ALARM | [11 empty] | 0 | [7 empty] | 01
CR01 | CR01-YS-001 | CR01-Y-001 | LCP | 108-AA | SWITCH - COMMON ALARM | LOCAL CONTROL PANEL | 022.0 | CR01 COMMOM ALARM | 8939 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
CR | CR-HS-002CM | CR-H-002 | CCR | C&E/693 | SWITCH - PUSHBUTTON | CR ALARM ANNUN. | 083.2 | BREATH. AIR ALM. ACKNOWLEDGE | 8574 | - | - | REF | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
CR | CR-HS-003CM | CR-H-003 | CCR | C&E/693 | SWITCH - PUSHBUTTON | CR ALARM ANNUN. | 083.2 | GEN. ALM. ACKN. (CONT. ROOM) | 8575 | - | - | REF | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
CR | CR-HS-004CM | CR-H-004 | CCR | C&E/693 | SWITCH - PUSHBUTTON | CR ALARM ANNUN. | 083.2 | GEN. ALM. ACKN. (BUILDING) | 8576 | - | - | REF | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
CR | CR-HS-007CM | CR-H-007 | CCR | C&E/693 | SWITCH - PUSHBUTTON | CR ALARM ANNUN. | 083.2 | ANNUNCIATOR LAMP TEST | 8577 | - | - | REF | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
CR | CR-XA-003CM | CR-X-003 | CCR | C&E/693 | ALARM - AUDIBLE | CONTROL ROOM | 083.2 | GEN. ALM. CONTROL ROOM | 8578 | - | - | REF | REQ | F |  | I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-101 | CR-X-101 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | H2 LEAK - 1% LEL | 8579 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-102 | CR-X-102 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | H2 LEAK - 10% LEL | 8580 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-103 | CR-X-103 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | BREATHING AIR LOW PRESSURE | 8581 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-104 | CR-X-104 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | PCS GENERAL ALARM | 8582 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-105 | CR-X-105 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | PLANT SPILLAGE ALARM | 8583 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-106 | CR-X-106 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | FIRE ALARM | 8584 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-107 | CR-X-107 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | PCS FAULT | 8585 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-108 | CR-X-108 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | SGS FAULT | 8586 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-109 | CR-X-109 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | FIRE EVACUATE | 8587 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-110 | CR-X-110 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | FIRE SYSTEM FAULT | 8588 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-111 | CR-X-111 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. |  | SPARE(FUTURE) | [7 empty] | N.I.S |  | DO |  | 42 | SGS |  |  |  |  | SPARE WINDOW |  | 01
CR | CR-XL-111 | CR-X-111 | SGS |  | Ammonia high high level alarm SGS annunciator lamp | SGS/Control room |  | Ammonia high high level alarm annunciator | 13079 | [12 empty] | MOORE INDUSTRIES | APACS |  |  |  |  | 01
CR | CR-XL-112 | CR-X-112 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. |  | SPARE(FUTURE) | [7 empty] | N.I.S |  | DO |  | 42 | SGS |  |  |  |  | SPARE WINDOW |  | 01
CR | CR-XL-112 | CR-X-112 | SGS |  | Ammonia critical level alarm SGS annunciator lamp | SGS/Control room |  | Ammonia critical level alarm annunciator | 13080 | [12 empty] | MOORE INDUSTRIES | APACS |  |  |  |  | 01
CR | CR-XL-113 | CR-X-113 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | LOOP REACTOR HYDROGEN SHUTOFF |  |  | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-114 | CR-X-114 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. | 083.2 | LOOP REACTOR CRASH COOL |  |  | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
CR | CR-XL-115 | CR-X-115 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. |  | SPARE(FUTURE) | [7 empty] | N.I.S |  | DO |  | 42 | SGS |  |  |  |  | SPARE WINDOW |  | 01
CR | CR-XL-116 | CR-X-116 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. |  | SPARE(FUTURE) | [7 empty] | N.I.S |  | DO |  | 42 | SGS |  |  |  |  | SPARE WINDOW |  | 01
CR | CR-XL-117 | CR-X-117 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. |  | SPARE(FUTURE) | [7 empty] | N.I.S |  | DO |  | 42 | SGS |  |  |  |  | SPARE WINDOW |  | 01
CR | CR-XL-118 | CR-X-118 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. |  | SPARE(FUTURE) | [7 empty] | N.I.S |  | DO |  | 42 | SGS |  |  |  |  | SPARE WINDOW |  | 01
CR | CR-XL-119 | CR-X-119 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. |  | SPARE(FUTURE) | [7 empty] | N.I.S |  | DO |  | 42 | SGS |  |  |  |  | SPARE WINDOW |  | 01
CR | CR-XL-120 | CR-X-120 | CCR | C&E/693 | ANNUNCIATOR - LAMP | CR ALARM ANNUN. |  | SPARE(FUTURE) | [7 empty] | N.I.S |  | DO |  | 42 | SGS |  |  |  |  | SPARE WINDOW |  | 01
CT01 | CT01-LAH-001 | CT01-L-001 | PCS | 107-KD | ALARM - LEVEL - HIGH |  |  | LEVEL | [11 empty] | 0 | [7 empty] | 01
CT01 | CT01-LE-001 | CT01-L-001 | FLD | 107-KD | ELEMENT - LEVEL | 50-RV-CS1A-0-9026841 | 009.0 | LEVEL |  | Fixed | - | REF | 12 | F |  | I.S |  |  |  | 0 |  | ENDRESS + HAUSER | [5 empty] | 01
CT01 | CT01-LSH-001 | CT01-L-001 | CPR | 107-KD | SWITCH - LEVEL - HIGH | CT01 DRAIN | 009.0 | LEVEL | 6465 | - | - | REF | 12 | F |  | N.I.S | DI |  |  | 35 | UTIL | ENDRESS + HAUSER | FDL31-GAE2AA7O | KL0014 |  |  |  | 01
CT01 | CT01-LI-002 | CT01-L-002 | FLD | 107-KD | INDICATOR - LEVEL GAUGE | CT01/LG1/LG2 | 009.0 | LEVEL |  | 0 to 1900mm | +/- 10% | REF | REQ | F | [5 empty] | 0 |  | KLINGER | 154692/A | KL0007 |  |  |  | 01
CT01 | CT01-PAH-001 | CT01-P-001 | PCS | 107-KD | ALARM - PRESSURE - HIGH |  |  | HEADER PRESSURE | [11 empty] | 0 | [7 empty] | 01
CT01 | CT01-PSH-001 | CT01-P-001 | FLD | 107-KD | SWITCH - PRESSURE - HIGH | 150-RV-CS1A-0-9026720 | 009.0 | HEADER PRESSURE | 6709 | set @ 0.05 barg | +/- 5% | REF | REQ | C |  | I.S | DI |  |  | 32 | UTIL | DELTA CONTROLS LTD | WS210GCCH2X300ANA | KP0012 | TI702-SP-5070 |  |  | 01
CT03 | CT03-LAH-001 | CT03-L-001 | PCS | 107-KD | ALARM - LEVEL - HIGH |  |  | LEVEL | [11 empty] | 0 | [7 empty] | 01
CT03 | CT03-LE-001 | CT03-L-001 | FLD | 107-KD | ELEMENT - LEVEL | CT03/L1 | 010.0 | LEVEL |  | Fixed | - | REF | 12 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
CT03 | CT03-LSH-001 | CT03-L-001 | CPR | 107-KD | SWITCH - LEVEL - HIGH | CT03/L/50 | 010.0 | LEVEL | 8102 | - | - | REF | 12 | F |  | N.I.S | DI |  |  | 35 | UTIL | ENDRESS + HAUSER | FDL31-GAE2AA70 | KL0014 |  |  |  | 01
CT03 | CT03-LI-002 | CT03-L-002 | FLD | 107-KD | INDICATOR - LEVEL GAUGE | CT03/LG1/LG2 | 010.0 | LEVEL |  | 0 to 850mm | +/- 10% | REF | REQ | F | [5 empty] | 0 |  | KLINGER | 154692/B | KL0007 |  |  |  | 01
CT03 | CT03-PAH-001 | CT03-P-001 | PCS | 107-KD | ALARM - PRESSURE - HIGH |  |  | HEADER PRESSURE | [11 empty] | 0 | [7 empty] | 01
CT03 | CT03-PSH-001 | CT03-P-001 | FLD | 107-KD | SWITCH - PRESSURE - HIGH | 150-RV-CS1A-0-9026767 | 010.0 | HEADER PRESSURE | 6710 | set @ 0.05 barg | +/- 5% | REF | REQ | C |  | I.S | DI |  |  | 32 | UTIL | DELTA CONTROLS LTD | WS210GCCH2X300ANA | KP0012 | TI702-SP-5070 |  |  | 01
CW | CW-FQI-001 | CW-F-001 | CPR | 108-AB | INDICATOR - FLOW | BEMS SYSTEM |  | COOLING WATER FLOW | [11 empty] | 0 | [7 empty] | 01
CW | CW-FT-001 | CW-F-001 | FLD | 108-AB | TRANSMITTER - FLOW | 200-CWF-CS1B-0-9028100 | 111.0 | COOLING WATER FLOW |  | 67 - 7500 l/min | +/- 5% | REF | REQ | C |  | N.I.S |  |  |  | 36 |  | MEINECKE | MEIN150WPD | KF0018 |  | INPUT TO BEMS SYSTEM | DI | 01
CW | CW-PDI-001 | CW-P-001 | PKG | 108-AB | INDICATOR - DIFF PRESSURE | DUPLEX FILTERS | 111.0 | COOLING WATER FILTERS dP |  | 0 to 15 psi | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
CW | CW-RO-001 | CW-R-001 | FLD | 108-AB | RESTRICTION ORIFICE PLATE | 80-CWR-CS1B-AC-9028100 | 111.0 | COOLING WATER BYPASS |  | 1.5 m3/hr | - | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
CW | CW-RO-002 | CW-R-002 | FLD | 108-AB | RESTRICTION ORIFICE PLATE | 25-CWF-CS1B-0-9028101 | 111.0 | COOLING WATER BYPASS |  | 1.5 m3/hr | - | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
| CW-RO-003 | CW-R-003 | FLD | 108-JA | RESTRICTION ORIFICE PLATE | 40-CWF-SS1C-0-9028950 | 111.0 | COOLING WATER BYPASS |  | 1.5 m3/hr | - | REF | REQ | F | [5 empty] | 0 |  |  | ZT4608.00
DHC01 | DHC01-HS-001 | DHC01-H-001 | PKG | 108-AA | PUSH BUTTON STATION | DHC01 | 144.1 | FAN START/STOP - MCC |  |  |  | REF | REQ | F | [13 empty] | 01
DHC01 | DHC01-P1-001 | DHC01-P-001 | FLD | 108-AA | PRESSURE GAUGE | 25-SLP-CS1A-H-9028007 | 144.1 | STEAM SUPPLY PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | F | [13 empty] | 01
DHC01 | DHC01-TCV-001 | DHC01-T-001 | PKG | 108-AA | TEMPERATURE CONTROL VALVE | 25-SLP-CS1A-H-9028007 | 144.1 | TEMPERATURE CONTROL |  | set @ ??? degC | +/- 5% | SHE | REQ | C | [11 empty] | SETTING TO SUIT Ops |  | 01
DHC01 | DHC01-TI-002 | DHC01-T-002 | PKG | 108-AA | TEMPERATURE INDICATOR | DHC01 | 144.1 | TEMPERATURE |  | 0 to 200 degC | +/- 5% | SHE | REQ | C | [13 empty] | 01
DISP | DISP-HS-003AM | DISP-X-003 | FLD | C&E/693 | SWITCH - PUSHBUTTON | DISPENSARY GND FLOOR | 083.2 | GEN. ALM. DISPENSARY GND FL | 8088 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
DISP | DISP-XA-003AM | DISP-X-003 | FLD | C&E/693 | ALARM - AUDIBLE | DISPENSARY GND FLOOR | 083.2 | GEN. ALM. DISPENSARY GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
DISP | DISP-XL-003AM | DISP-X-003 | FLD | C&E/693 | ALARM - BEACON | DISPENSARY GND FLOOR | 083.2 | GEN. ALM. DISPENSARY GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
DP05 | DP05-CV-001 | DP05-C-001 | FLD | 107-PF | BALL VALVE - ON/OFF - F.C. | 25-CA-SS1U-0-9028562 | 042.2 | AIR TO PUMP | 7090 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
DP05 | DP05-CY-001 | DP05-C-001 | FLD | 107-PF | SOLENOID VALVE | RACK MOUNTED |  | AIR TO PUMP | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
DP05 | DP05-ZSC-001 | DP05-C-001 | FLD | 107-PF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AIR TO PUMP | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
DP05 | DP05-ZSO-001 | DP05-C-001 | FLD | 107-PF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AIR TO PUMP | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
DP05 | DP05-FIT-001 | DP05-F-001 | FLD | 107-PF | TRANSMITTER - FLOW | 25-50-SS1C-0-902871 | 082.5 | PUMP OUTLET FLOW | 6462 | 0 - 8 m3/hr | +/- 0.25% | SHE | 5 YR | C |  | N.I.S | DI |  |  | 36 | UTIL | ENDRESS + HAUSER | NOTE2 | KF0002 |  | 0 to 400 hz |  | 01
DP05 | DP05-FQIC-001 | DP05-F-001 | PCS | 107-PF | INDICATING CONTROLLER - FLOW |  |  | PUMP OUTLET FLOW | [11 empty] | 0 | [7 empty] | 01
DP05 | DP05-PRV-001 | DP05-P-001 | PKG | 107-PF | CONTROL VALVE SELF ACTUATING | WITH DP05 | 082.5 | AIR TO DP05 |  | set @ commish. | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP01 | DVP01-CV-001 | DVP01-C-001 | PKG | 107-GG | V-BALL VALVE - CONTROL - F.C. | DVP01 | 036.1 | HEADER INLET | 8589 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | [6 empty] | 01
DVP01 | DVP01-CY-001 | DVP01-C-001 | PKG | 107-GG | SOLENOID VALVE | MTD. ON VALVE |  | HEADER INLET | [7 empty] | I.S | DO |  |  | 41 | UTIL | [6 empty] | 01
DVP01 | DVP01-ZSC-001 | DVP01-C-001 | PKG | 107-GG | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HEADER INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP01 | DVP01-ZSO-001 | DVP01-C-001 | PKG | 107-GG | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HEADER INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP01 | DVP01-CV-002 | DVP01-C-002 | FLD | 107-GG | BALL VALVE - ON/OFF - F.C. | 15-N-SS1U-0-9025368 | 043.4 | N2 TO INLET | 7082 | - | - | REF | REQ | F | [5 empty] | 0 | 043.4 |  |  | KV0017 |  |  |  | 01
DVP01 | DVP01-CY-002 | DVP01-C-002 | FLD | 107-GG | SOLENOID VALVE | RACK MOUNTED |  | N2 TO INLET | [7 empty] | I.S | DO |  |  | 41 | UTIL | [6 empty] | 01
DVP01 | DVP01-ZSC-002 | DVP01-C-002 | FLD | 107-GG | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP01 | DVP01-ZSO-002 | DVP01-C-002 | FLD | 107-GG | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP01 | DVP01-CV-003 | DVP01-C-003 | FLD | 107-GG | BALL VALVE - ON/OFF - F.O. | 25-N-SS1U-0-9028717 | 043.4 | NITROGEN SUPPLY | 7085 | - | - | REF | REQ | F | [5 empty] | 0 | 043.4 |  |  | KV0017 |  |  |  | 01
DVP01 | DVP01-CY-003 | DVP01-C-003 | FLD | 107-GG | SOLENOID VALVE | RACK MOUNTED |  | NITROGEN SUPPLY | [7 empty] | I.S | DO |  |  | 41 | UTIL | [6 empty] | 01
DVP01 | DVP01-ZSC-003 | DVP01-C-003 | FLD | 107-GG | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | NITROGEN SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP01 | DVP01-ZSO-003 | DVP01-C-003 | FLD | 107-GG | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | NITROGEN SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP01 | DVP01-CV-004 | DVP01-C-004 | FLD | 107-GG | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9025360 | 008.1 | VC1 TO SCRUBBER SELECT | 7096 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
DVP01 | DVP01-CY-004A | DVP01-C-004 | FLD | 107-GG | SOLENOID VALVE | RACK MOUNTED |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 | TO ACID SCRUBBER |  | 01
DVP01 | DVP01-CY-004B | DVP01-C-004 | FLD | 107-GG | SOLENOID VALVE | RACK MOUNTED |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 | TO ALKALI SCRUBBER |  | 01
DVP01 | DVP01-ZSC-004 | DVP01-C-004 | FLD | 107-GG | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | OPEN TO ALKALI GAS SCRUBBER |  | 01
DVP01 | DVP01-ZSO-004 | DVP01-C-004 | FLD | 107-GG | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | OPEN TO ACID GAS SCRUBBER |  | 01
DVP01 | DVP01-DIC-001 | DVP01-D-001 | PCS | 107-GG | INDICATING CONTR. - MOTOR DRIVE |  |  | VACUUM PUMP |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
DVP01 | DVP01-DS-001 | DVP01-D-001 | MCC | 107-GG | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | VACUUM PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
DVP01 | DVP01-DY-001 | DVP01-D-001 | MCC | 107-GG | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | VACUUM PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
DVP01 | DVP01-DYC-001 | DVP01-D-001 | MCC | 107-GG | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 036.1 | VACUUM PUMP | 8590 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
DVP01 | DVP01-FI-001 | DVP01-F-001 | PKG | 107-GG | INDICATOR - FLOW | 25-CWR-CS1B-AC-9025366 | 036.1 | COOLING WATER RTN |  | Fixed | - | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP01 | DVP01-FI-002 | DVP01-F-002 | PKG | 107-GG | INDICATOR - FLOW | DVP01 | 036.1 | N2 SUPPLY |  | 40 to 440 l/min | +/- 2% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP01 | DVP01-LAH-001 | DVP01-L-001 | PCS | 107-GG | ALARM - LEVEL - HIGH |  |  | K.O. POT HIGH LEVEL | [11 empty] | 0 | [7 empty] | 01
DVP01 | DVP01-LSH-001 | DVP01-L-001 | PKG | 107-GG | SWITCH - LEVEL - HIGH | DVP01-KP1 | 036.1 | K.O. POT HIGH LEVEL | 8591 | Fixed | - | REF | 12 | F |  | I.S | DI |  |  | 32 | UTIL | [6 empty] | 01
DVP01 | DVP01-LAH-002 | DVP01-L-002 | PCS | 107-GG | ALARM - LEVEL - HIGH |  |  | RECEIVER HIGH LEVEL | [11 empty] | 0 | [7 empty] | 01
DVP01 | DVP01-LSH-002 | DVP01-L-002 | PKG | 107-GG | SWITCH - LEVEL - HIGH | DVP01-RC1 | 036.1 | RECEIVER HIGH LEVEL | 8592 | Fixed | - | REF | 12 | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | TD1AC1AAB |  |  |  |  | 02
DVP01 | DVP01-PI-001 | DVP01-P-001 | FLD | 107-GG | PRESSURE GAUGE | 15-N-SS1U-0-9028717 | 043.4 | N2 SUPPLY |  | -1 to 1.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | 043.4 | WIKA | 232.50.100 | KP0006 |  |  |  | 01
DVP01 | DVP01-PSV-002 | DVP01-P-002 | FLD | 107-GG | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9025370 | 040.2 | VC1 HTF RELIEF |  | 10 barg | +/- 10% |  | 24 | C | [5 empty] | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
DVP01 | DVP01-PI-003 | DVP01-P-003 | PKG | 107-GG | PRESSURE GAUGE | DVP01 | 036.1 | INLET PRESSURE |  | -1 to 0 barg | +/- 5% | SHE | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP01 | DVP01-RO-001 | DVP01-R-001 | PKG | 107-GG | RESTRICTION ORIFICE PLATE | DVP01 | 036.1 | N2 TO INLET |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
DVP01 | DVP01-TI-001 | DVP01-T-001 | FLD | 107-GG | INDICATOR - TEMPERATURE | 25-CWR-CS1B-A-9025366 | 111.0 | COOLING WATER RTN |  | 0 to 60 degC | +/- 2% | REF | REQ | C | [5 empty] | 0 |  | WIKA | S5550/4 | KT0003 |  |  |  | 01
DVP01 | DVP01-TAH-002 | DVP01-T-002 | PCS | 107-GG | ALARM - TEMPERATURE - HI HI |  |  | PUMP HIGH TEMPERATURE |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
DVP01 | DVP01-TSH-002 | DVP01-T-002 | PKG | 107-GG | SWITCH - TEMPERATURE - HI HI | DVP01 | 036.1 | PUMP HIGH TEMPERATURE | 8593 | set @ 170 degC | +/- 3% | SHE | 12 | C |  | I.S | DI |  |  | 32 | UTIL | [6 empty] | 01
DVP01 | DVP01-TRV-003 | DVP01-T-003 | PKG | 107-GG | TEMPERATURE REGULATING VALVE | DVP01 | 036.1 | TEMPERATURE CONTROL |  | set @ 170 degC | +/- 3% | SHE | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP02 | c03-at-003 | DVP02-C-001 | PKG | 107-GH | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ST1 LIQUID OUTLET |  |  |  | REF |  |  |  | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
DVP02 | DVP02-CV-001 | DVP02-C-001 | PKG | 107-GH | BALL VALVE - ON/OFF - F.C. | DVP02 | 037.0 | ST1 LIQUID OUTLET | 8594 | - | - |  | REQ | F | [5 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-CY-001 | DVP02-C-001 | FLD | 107-GH | SOLENOID VALVE | RACK MOUNTED |  | ST1 LIQUID OUTLET | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
DVP02 | DVP02-ZSO-001 | DVP02-C-001 | PKG | 107-GH | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ST1 LIQUID OUTLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
DVP02 | DVP02-CV-005 | DVP02-C-005 | FLD | 107-GH | BALL VALVE - ON/OFF - F.C. | 50-SV-SS1C-0-9025443 | 008.3 | TO SCRUBBER 03 | 7102 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
DVP02 | DVP02-CY-005 | DVP02-C-005 | FLD | 107-GH | SOLENOID VALVE | RACK MOUNTED |  | TO SCRUBBER 03 | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
DVP02 | DVP02-ZSC-005 | DVP02-C-005 | FLD | 107-GH | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO SCRUBBER 03 | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
DVP02 | DVP02-ZSO-005 | DVP02-C-005 | FLD | 107-GH | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO CONT. SCRUBBER | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
DVP02 | DVP02-DIC-001 | DVP02-D-001 | PCS | 107-GH | INDICATING CONTR. - MOTOR DRIVE |  |  | VACUUM PUMP |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-DS-001 | DVP02-D-001 | MCC | 107-GH | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | VACUUM PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
DVP02 | DVP02-DY-001 | DVP02-D-001 | MCC | 107-GH | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | VACUUM PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
DVP02 | DVP02-DYC-001 | DVP02-D-001 | MCC | 107-GH | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 037.0 | VACUUM PUMP | 8595 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
DVP02 | DVP02-FI-001 | DVP02-F-001 | PKG | 107-GH | VA FLOW METER | DVP02 | 037.0 | SEAL FLUID FLOW |  | - | - | REF | REQ | F | [5 empty] | 0 |  | KROHNE | H250/RR/M9 | KF0027/P |  |  |  | 01
DVP02 | DVP02-HV-001 | DVP02-H-001 | PKG | 107-GH | V BALL HAND VALVE | DVP02 |  |  |  | - | - | [8 empty] | 0 |  | HABONIM | 31 Series V-FLOW |  |  |  |  | 01
DVP02 | DVP02-LAH-001 | DVP02-L-001 | [7 empty] | - | - | REF | REQ
DVP02 | DVP02-LAHH-001 | DVP02-L-001 | PCS | 107-GH | ALARM - LEVEL - HI HI |  |  | ST1 HI-HI LEVEL | [11 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-LSHH-001 | DVP02-L-001 | PKG | 107-GH | SWITCH - LEVEL - HI HI | DVP02-ST1 | 037.0 | ST1 HI-HI LEVEL |  | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
DVP02 | DVP02-LAH-002 | DVP02-L-002 | PCS | 107-GH | ALARM - LEVEL - HIGH |  |  | ST1 HIGH LEVEL | L15874 | On/Off | On/Off | SHE | 24 | [6 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-LSH-002 | DVP02-L-002 | PKG | 107-GH | SWITCH - LEVEL - HIGH | DVP02-ST1 | 037.0 | ST1 HIGH LEVEL | L15874 | On/Off | On/Off | SHE | 24 | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
DVP02 | DVP02-LAL-003 | DVP02-L-003 | PCS | 107-GH | ALARM - LEVEL - LOW |  |  | ST1 LOW LEVEL |  |  |  | SHE | REQ | [6 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-LSL-003 | DVP02-L-003 | PKG | 107-GH | SWITCH - LEVEL - LOW | DVP02-ST1 | 037.0 | ST1 LOW LEVEL |  | - | - | SHE | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
DVP02 | DVP02-LI-004 | DVP02-L-004 | PKG | 107-GH | INDICATOR - LEVEL GAUGE | DVP02-ST1 | 037.0 | ST1 LEVEL |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-PI-001 | DVP02-P-001 | [7 empty] | - | - | REF | REQ
DVP02 | DVP02-PIC-001 | DVP02-P-001 | PCS | 107-GH | DVP02-P-001 |  |  | HEADER PRESSURE | [11 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-PIT-001 | DVP02-P-001 | FLD | 107-GH | DVP02-T-002 | 40-VP-PT1A-0-9024922 | 037.0 | HEADER PRESSURE |  | - | - | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
DVP02 | DVP02-PSV-002 | DVP02-P-002 | FLD | 107-GH | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9025450 | 040.2 | ST1 HTF RELIEF |  | 10 barg | +/- 10% |  | 24 | C | [5 empty] | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
DVP02 | DVP02-PI-003 | DVP02-P-003 | PCS | 107-GH | INDICATOR - PRESSURE |  |  | VACUUM PUMP VENT PRESSURE |  | -1 to 4 barg | +/- 1% | SHE | 12 | C |  | I.S | AI | [11 empty] | v18.0
DVP02 | DVP02-PIT-003 | DVP02-P-003 | FLD | 107-GH | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-SS1C-0-9025443 | 037.0 | VACUUM PUMP VENT PRESSURE |  | -1 to 4 barg | +/- 1% | SHE | 12 | C |  |  | DI |  |  |  |  | ROSEMOUNT | 3051S | [5 empty] | v18.0
DVP02 | DVP02-PSH-003 | DVP02-P-003 | FLD | 107-GH | SWITCH - PRESSURE - HIGH | RACK MOUNTED | 037.0 | VACUUM PUMP VENT PRESSURE |  | 0.3 barg rising | +/- 1% | SHE | 12 | F | [14 empty] | v18.0
DVP02 | DVP02-TE-001 | DVP02-T-001 | PKG | 107-GH | ELEMENT - TEMPERATURE - RTD | DVP02-ST1 |  | ST1 TEMPERATURE | L8599 | -50 to 50 degC | +/- 2 degC | SHE | 24 | [6 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-TI-001 | DVP02-T-001 | PCS | 107-GH | INDICATOR - TEMPERATURE |  |  | ST1 TEMPERATURE | L8599 | -50 to 50 degC | +/- 2 degC | SHE | 24 | [6 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-TT-001 | DVP02-T-001 | PKG | 107-GH | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 037.0 | ST1 TEMPERATURE | L8599 | -50 to 50 degC | +/- 2 degC | SHE | 24 | C |  | I.S | AI |  |  | 11 | UTIL | BOURDON SEDEME | Y76TR |  | TI702-SP-5075 |  |  | 01
DVP02 | DVP02-TE-002 | DVP02-T-002 | FLD | 107-GH | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9025440 |  | HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-TI-002 | DVP02-T-002 | [7 empty] | - | - | REF | REQ
DVP02 | DVP02-TIC-002 | DVP02-T-002 | PCS | 107-GH | INDICATING CONTROLLER - TEMPERATURE |  |  | HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
DVP02 | DVP02-TT-002 | DVP02-T-002 | FLD | 107-GH | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.2 | HTF RTN TEMPERATURE |  | - | - | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
DVP03 | DVP03-CV-001 | DVP03-C-001 | PKG | 107-GJ | V-BALL VALVE - CONTROL - F.C. | DVP03 | 038.0 | HEADER INLET | 8600 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | [6 empty] | 01
DVP03 | DVP03-CY-001 | DVP03-C-001 | PKG | 107-GJ | SOLENOID VALVE | MTD. ON VALVE |  | HEADER INLET | [7 empty] | I.S | DO |  |  | 41 | UTIL | [6 empty] | 01
DVP03 | DVP03-ZSC-001 | DVP03-C-001 | PKG | 107-GJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HEADER INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP03 | DVP03-ZSO-001 | DVP03-C-001 | PKG | 107-GJ | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HEADER INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP03 | DVP03-CV-002 | DVP03-C-002 | FLD | 107-GJ | BALL VALVE - ON/OFF - F.C. | 15-N-SS1U-0-9025410 | 043.4 | N2 TO INLET | 7083 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
DVP03 | DVP03-CY-002 | DVP03-C-002 | FLD | 107-GJ | SOLENOID VALVE | RACK MOUNTED |  | N2 TO INLET | [7 empty] | I.S | DO |  |  | 41 | UTIL | [6 empty] | 01
DVP03 | DVP03-ZSC-002 | DVP03-C-002 | FLD | 107-GJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP03 | DVP03-ZSO-002 | DVP03-C-002 | FLD | 107-GJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP03 | DVP03-CV-003 | DVP03-C-003 | FLD | 107-GJ | BALL VALVE - ON/OFF - F.O. | 25-N-SS1U-0-9028784 | 043.4 | NITROGEN SUPPLY | 7086 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
DVP03 | DVP03-CY-003 | DVP03-C-003 | FLD | 107-GJ | SOLENOID VALVE | RACK MOUNTED |  | NITROGEN SUPPLY | [7 empty] | I.S | DO |  |  | 41 | UTIL | [6 empty] | 01
DVP03 | DVP03-ZSC-003 | DVP03-C-003 | FLD | 107-GJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | NITROGEN SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP03 | DVP03-ZSO-003 | DVP03-C-003 | FLD | 107-GJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | NITROGEN SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP03 | DVP03-CV-004 | DVP03-C-004 | FLD | 107-GJ | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9025400 | 008.1 | VC1 TO SCRUBBER SELECT | 7120 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
DVP03 | DVP03-CY-004A | DVP03-C-004 | FLD | 107-GJ | SOLENOID VALVE | RACK MOUNTED |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 | TO ACID SCRUBBER |  | 01
DVP03 | DVP03-CY-004B | DVP03-C-004 | FLD | 107-GJ | SOLENOID VALVE | RACK MOUNTED |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 | TO ALKALI SCRUBBER |  | 01
DVP03 | DVP03-ZSC-004 | DVP03-C-004 | FLD | 107-GJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | OPEN TO ALKALI GAS SCRUBBER |  | 01
DVP03 | DVP03-ZSO-004 | DVP03-C-004 | FLD | 107-GJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | OPEN TO ACID GAS SCRUBBER |  | 01
DVP03 | DVP03-DIC-001 | DVP03-D-001 | PCS | 107-GJ | INDICATING CONTR. - MOTOR DRIVE |  |  | VACUUM PUMP |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
DVP03 | DVP03-DS-001 | DVP03-D-001 | MCC | 107-GJ | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | VACUUM PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
DVP03 | DVP03-DY-001 | DVP03-D-001 | MCC | 107-GJ | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | VACUUM PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
DVP03 | DVP03-DYC-001 | DVP03-D-001 | MCC | 107-GJ | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 038.0 | VACUUM PUMP | 8601 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
DVP03 | DVP03-FI-001 | DVP03-F-001 | PKG | 107-GJ | INDICATOR - FLOW | 25-CWR-CS1B-AC-9025406 | 038.0 | COOLING WATER RTN |  | - | - | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP03 | DVP03-FI-002 | DVP03-F-002 | PKG | 107-GJ | INDICATOR - FLOW | DVP03 | 038.0 | N2 SUPPLY |  | 40 to 440 l/min | +/- 2% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP03 | DVP03-LAH-001 | DVP03-L-001 | PCS | 107-GJ | ALARM - LEVEL - HIGH |  |  | K.O. POT HIGH LEVEL | [11 empty] | 0 | [7 empty] | 01
DVP03 | DVP03-LSH-001 | DVP03-L-001 | PKG | 107-GJ | SWITCH - LEVEL - HIGH | DVP03-KP1 | 038.0 | K.O. POT HIGH LEVEL | 8602 | Fixed | - | REF | 12 | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 75BTXSC0010 |  |  |  |  | 01
DVP03 | DVP03-LAH-002 | DVP03-L-002 | PCS | 107-GJ | ALARM - LEVEL - HIGH |  |  | RECEIVER HIGH LEVEL | [11 empty] | 0 | [7 empty] | 01
DVP03 | DVP03-LSH-002 | DVP03-L-002 | PKG | 107-GJ | SWITCH - LEVEL - HIGH | DVP03-RC1 | 038.0 | RECEIVER HIGH LEVEL | 8603 | Fixed | - | REF | 12 | F |  | I.S | DI |  |  | 32 | UTIL | [6 empty] | 01
DVP03 | DVP03-PI-001 | DVP03-P-001 | FLD | 107-GJ | PRESSURE GAUGE | 15-N-SS1U-0-9028784 | 043.4 | N2 SUPPLY |  | -1 to 1.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 | KP0006 |  |  |  | 01
DVP03 | DVP03-PSV-002 | DVP03-P-002 | FLD | 107-GJ | PRESSURE RELIEF VALVE | 25-HT-CS3A-0-9025412 | 040.2 | VC1 HTF RELIEF |  | 10 barg | +/- 10% |  | 24 | C | [5 empty] | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
DVP03 | DVP03-PI-003 | DVP03-P-003 | PKG | 107-GJ | PRESSURE GAUGE | DVP03 | 038.0 | INLET PRESSURE |  | -1 to 0 barg | +/- 5% | SHE | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP03 | DVP03-RO-001 | DVP03-R-001 | PKG | 107-GJ | RESTRICTION ORIFICE PLATE | DVP03 | 038.0 | N2 TO INLET |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
DVP03 | DVP03-TI-001 | DVP03-T-001 | FLD | 107-GJ | INDICATOR - TEMPERATURE | 25-CWR-CS1B-A-9025406 | 111.0 | COOLING WATER RTN |  | 0 to 60 degC | +/- 2% | REF | REQ | C | [5 empty] | 0 |  | WIKA | S5550/4 | KT0003 |  |  |  | 01
DVP03 | DVP03-TAH-002 | DVP03-T-002 | PCS | 107-GJ | ALARM - TEMPERATURE - HI HI |  |  | PUMP HIGH TEMPERATURE |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
DVP03 | DVP03-TSH-002 | DVP03-T-002 | PKG | 107-GJ | SWITCH - TEMPERATURE - HI HI | DVP03 | 038.0 | PUMP HIGH TEMPERATURE | 8604 | set @ 170 degC | +/- 3% | SHE | 12 | C |  | I.S | DI |  |  | 32 | UTIL | [6 empty] | 01
DVP03 | DVP03-TRV-003 | DVP03-T-003 | PKG | 107-GJ | TEMPERATURE REGULATING VALVE | DVP03 | 038.0 | TEMPERATURE CONTROL |  | set @ 170 degC | +/- 3% | SHE | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP04 | DVP04-CV-001 | DVP04-C-001 | PKG | 107-GK | V-BALL VALVE - CONTROL - F.C. | DVP04 | 036.2 | HEADER INLET | 8605 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | [6 empty] | 01
DVP04 | DVP04-CY-001 | DVP04-C-001 | PKG | 107-GK | SOLENOID VALVE | MTD. ON VALVE |  | HEADER INLET | [7 empty] | I.S | DO |  |  | 41 | UTIL | [6 empty] | 01
DVP04 | DVP04-ZSC-001 | DVP04-C-001 | PKG | 107-GK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HEADER INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP04 | DVP04-ZSO-001 | DVP04-C-001 | PKG | 107-GK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HEADER INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP04 | DVP04-CV-002 | DVP04-C-002 | FLD | 107-GK | BALL VALVE - ON/OFF - F.C. | 15-N-SS1U-0-9027708 | 043.4 | N2 TO INLET | 7084 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
DVP04 | DVP04-CY-002 | DVP04-C-002 | FLD | 107-GK | SOLENOID VALVE | RACK MOUNTED |  | N2 TO INLET | [7 empty] | I.S | DO |  |  | 41 | UTIL | [6 empty] | 01
DVP04 | DVP04-ZSC-002 | DVP04-C-002 | FLD | 107-GK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP04 | DVP04-ZSO-002 | DVP04-C-002 | FLD | 107-GK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO INLET | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP04 | DVP04-CV-003 | DVP04-C-003 | FLD | 107-GK | BALL VALVE - ON/OFF - F.O. | 25-N-SS1U-0-9028718 | 043.4 | NITROGEN SUPPLY | 7087 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
DVP04 | DVP04-CY-003 | DVP04-C-003 | FLD | 107-GK | SOLENOID VALVE | RACK MOUNTED |  | NITROGEN SUPPLY | [7 empty] | I.S | DO |  |  | 41 | UTIL | [6 empty] | 01
DVP04 | DVP04-ZSC-003 | DVP04-C-003 | FLD | 107-GK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | NITROGEN SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP04 | DVP04-ZSO-003 | DVP04-C-003 | FLD | 107-GK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | NITROGEN SUPPLY | [7 empty] | I.S | DI |  |  | 31 | UTIL | [6 empty] | 01
DVP04 | DVP04-CV-004 | DVP04-C-004 | FLD | 107-GK | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9027700 | 008.1 | VC1 TO SCRUBBER SELECT | 7121 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
DVP04 | DVP04-CY-004A | DVP04-C-004 | FLD | 107-GK | SOLENOID VALVE | RACK MOUNTED |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 | TO ACID SCRUBBER |  | 01
DVP04 | DVP04-CY-004B | DVP04-C-004 | FLD | 107-GK | SOLENOID VALVE | RACK MOUNTED |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 | TO ALKALI SCRUBBER |  | 01
DVP04 | DVP04-ZSC-004 | DVP04-C-004 | FLD | 107-GK | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | OPEN TO ALKALI GAS SCRUBBER |  | 01
DVP04 | DVP04-ZSO-004 | DVP04-C-004 | FLD | 107-GK | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | VC1 TO SCRUBBER SELECT | [7 empty] | I.S | DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | OPEN TO ACID GAS SCRUBBER |  | 01
DVP04 | DVP04-DIC-001 | DVP04-D-001 | PCS | 107-GK | INDICATING CONTR. - MOTOR DRIVE |  |  | VACUUM PUMP |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
DVP04 | DVP04-DS-001 | DVP04-D-001 | MCC | 107-GK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | VACUUM PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
DVP04 | DVP04-DY-001 | DVP04-D-001 | MCC | 107-GK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | VACUUM PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
DVP04 | DVP04-DYC-001 | DVP04-D-001 | MCC | 107-GK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 036.2 | VACUUM PUMP | 8606 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
DVP04 | DVP04-FI-001 | DVP04-F-001 | PKG | 107-GK | INDICATOR - FLOW | 25-CWR-CS1B-AG-9027706 | 036.2 | COOLING WATER RTN |  | Fixed | - | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP04 | DVP04-FI-002 | DVP04-F-002 | PKG | 107-GK | INDICATOR - FLOW | DVP04 | 036.2 | N2 SUPPLY |  | 40 to 440 l/min | +/- 2% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP04 | DVP04-LAH-001 | DVP04-L-001 | PCS | 107-GK | ALARM - LEVEL - HIGH |  |  | K.O. POT HIGH LEVEL | [11 empty] | 0 | [7 empty] | 01
DVP04 | DVP04-LSH-001 | DVP04-L-001 | PKG | 107-GK | SWITCH - LEVEL - HIGH | DVP04-KP1 | 036.2 | K.O. POT HIGH LEVEL | 8607 | Fixed | - | REF | 12 | F |  | I.S | DI |  |  | 32 | UTIL | [6 empty] | 01
DVP04 | DVP04-LAH-002 | DVP04-L-002 | PCS | 107-GK | ALARM - LEVEL - HIGH |  |  | RECEIVER HIGH LEVEL | [11 empty] | 0 | [7 empty] | 01
DVP04 | DVP04-LSH-002 | DVP04-L-002 | PKG | 107-GK | SWITCH - LEVEL - HIGH | DVP04-RC1 | 036.2 | RECEIVER HIGH LEVEL | 8608 | Fixed | - | REF | 12 | F |  | I.S | DI |  |  | 32 | UTIL | [6 empty] | 01
DVP04 | DVP04-PI-001 | DVP04-P-001 | FLD | 107-GK | PRESSURE GAUGE | 15-N-SS1U-0-9028718 | 043.4 | N2 SUPPLY |  | -1 to 1.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 | KP0006 |  |  |  | 01
DVP04 | DVP04-PSV-002 | DVP04-P-002 | FLD | 107-GK | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9027710 | 040.2 | VC1 HTF RELIEF |  | 10 barg | +/- 10% |  | 24 | C | [5 empty] | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
DVP04 | DVP04-PI-003 | DVP04-P-003 | PKG | 107-GK | PRESSURE GAUGE | DVP04 | 036.2 | INLET PRESSURE |  | -1 to 0 barg | +/- 5% | SHE | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP04 | DVP04-RO-001 | DVP04-R-001 | PKG | 107-GK | RESTRICTION ORIFICE PLATE | DVP04 | 036.2 | N2 TO INLET |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
DVP04 | DVP04-TI-001 | DVP04-T-001 | FLD | 107-GK | INDICATOR - TEMPERATURE | 25-CWR-CS1B-A-9027706 | 111.0 | COOLING WATER RTN |  | 0 to 60 degC | +/- 2% | REF | REQ | C | [5 empty] | 0 |  | WIKA | S5550/4 | KT0003 |  |  |  | 01
DVP04 | DVP04-TAH-002 | DVP04-T-002 | PCS | 107-GK | ALARM - TEMPERATURE - HI HI |  |  | PUMP HIGH TEMPERATURE |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
DVP04 | DVP04-TSH-002 | DVP04-T-002 | PKG | 107-GK | SWITCH - TEMPERATURE - HI HI | DVP04 | 036.2 | PUMP HIGH TEMPERATURE | 8609 | set @ 170 degC | +/- 3% | SHE | 12 | C |  | I.S | DI |  |  | 32 | UTIL | [6 empty] | 01
DVP04 | DVP04-TRV-003 | DVP04-T-003 | PKG | 107-GK | TEMPERATURE REGULATING VALVE | DVP04 | 036.2 | TEMPERATURE CONTROL |  | set @ 170 degC | +/- 3% | SHE | REQ | C | [5 empty] | 0 | [7 empty] | 01
DVP05 | DVP05-CV-001 | DVP05-C-001 | PKG | 107-GL | BALL VALVE - ON/OFF - F.C. | DVP05 | 172.0 | HEADER INLET |  |  | - | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-CV-002 | DVP05-C-002 | PKG | 107-GL | BALL VALVE - ON/OFF - F.C. | DVP05 | 172.0 | FLAME ARRESTOR BYPASS |  | - | - | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-CV-003 | DVP05-C-003 | PKG | 107-GL | BALL VALVE - ON/OFF - F.C. | 25-N-SSIU-O-9028891 | 172.0 | NITROGEN SUPPLY |  | - | - | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-CV-004 | DVP05-C-004 | FLD | 107-GL | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9025421 | 172.0 | VC1 TO SCRUBBER SELECT | 13165 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
DVP05 | DVP05-CY-004A | DVP05-C-004 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED | 172.0 | VC1 TO SCRUBBER SELECT | 13165 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
DVP05 | DVP05-CY-004B | DVP05-C-004 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED | 172.0 | VC1 TO SCRUBBER SELECT | 13165 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
DVP05 | DVP05-ZSC-004 | DVP05-C-004 | FLD | 107-GL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 172.0 | VC1 TO SCRUBBER SELECT | 13165 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
DVP05 | DVP05-ZSO-004 | DVP05-C-004 | FLD | 107-GL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 172.0 | VC1 TO SCRUBBER SELECT | 13165 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
DVP05 | DVP05-CV-005 | DVP05-C-005 | PKG | 107-GL | BALL VALVE - ON/OFF - F.C. | DVP05 | 172.0 | NITROGEN |  | - | - | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-CV-006 | DVP05-C-006 | PKG | 107-GL | BALL VALVE - ON/OFF - F.C. | 25-CWF-CS1B-AC-9025425 | 172.0 | NITROGEN |  | - | - | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-CV-007 | DVP05-C-007 | FLD | 107-GL | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9025421 | 172 | CARBON DRUM DIVERT | L15689 | - | - | REF | REQ | F | [5 empty] | 0 |  | ATOMAC | AMP3 | KV0007/P6 |  |  |  | 23
DVP05 | DVP05-CY-007A | DVP05-C-007 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
DVP05 | DVP05-CY-007B | DVP05-C-007 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  |  |  | REF |  |  |  | I.S |  | DO |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004
DVP05 | DVP05-ZSC-007 | DVP05-C-007 | FLD | 107-GL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM DIVERT |  |  |  | REF |  |  |  | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
DVP05 | DVP05-ZSO-007 | DVP05-C-007 | FLD | 107-GL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
DVP05 | DVP05-CV-008 | DVP05-C-008 | FLD | 107-GL | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9025421 | 172 | CARBON DRUM DIVERT | L15690 | - | - | REF | REQ | F | [5 empty] | 0 |  | ATOMAC | AMP3 | KV0007/P6 |  |  |  | 23
DVP05 | DVP05-CY-008A | DVP05-C-008 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
DVP05 | DVP05-CY-008B | DVP05-C-008 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  |  |  | REF |  |  |  | I.S |  | DO |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004
DVP05 | DVP05-ZSC-008 | DVP05-C-008 | FLD | 107-GL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM DIVERT |  |  |  | REF |  |  |  | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
DVP05 | DVP05-ZSO-008 | DVP05-C-008 | FLD | 107-GL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
DVP05 | DVP05-CV-009 | DVP05-C-009 | FLD | 107-GL | BALL VALVE - ON/OFF - F.C. | 15-P-PT1A-0-9025421 | 172 | CARBON DRUM NITROGEN PURGE | L15691 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
DVP05 | DVP05-CY-009 | DVP05-C-009 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM NITROGEN PURGE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
DVP05 | DVP05-ZSC-009 | DVP05-C-009 | FLD | 107-GL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM NITROGEN PURGE |  |  |  | REF |  |  |  | I.S | DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
DVP05 | DVP05-ZSO-009 | DVP05-C-009 | FLD | 107-GL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM NITROGEN PURGE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
DVP05 | DVP05-DIC-001 | DVP05-D-001 | PCS | 107-GL | INDICATING CONTR. - MOTOR DRIVE | DVP05 | 172.0 | VACUUM PUMP |  |  |  | SHE | - | - | - | [12 empty] | 01
DVP05 | DVP05-DY-001 | DVP05-D-001 | PKG | 107-GL | DRIVE - RUNNING | MOTOR CONTROL CENTRE | 172.0 | VACUUM PUMP | 13166 |  |  | SHE | - | - | - | N.I.S | DI | 1 |  | 35 | UTIL | [6 empty] | 01
DVP05 | DVP05-DYC-001 | DVP05-D-001 | PKG | 107-GL | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 172.0 | VACUUM PUMP | 13166 | - | - | SHE | REQ | F | Ops | N.I.S | DO | 1 |  | 42 | UTIL | [6 empty] | 01
DVP05 | DVP05-FI-001 | DVP05-F-001 | PKG | 107-GL | INDICATOR - FLOW |  | 172.0 | N2 SUPPLY |  | - | - | REF | REQ | C | Ref | [12 empty] | 01
DVP05 | DVP05-FSL-002 | DVP05-F-002 | PKG | 107-GL | SWITCH - FLOW - LOW | 25-N-SS1U-0-9028891 | 172.0 | NITROGEN |  |  |  |  | 12 | C | SHE | [12 empty] | 01
DVP05 | DVP05-FI-003 | DVP05-F-003 | PKG | 107-GL | INDICATOR - FLOW | 15-N-SS1U-0-9028906 | 172 | N2 TO CARBON DRUM | L15718 | - | - | REF | REQ | C | Ref | [6 empty] | KROHNE | H250 | KF0027/P7 |  |  |  | 23
DVP05 | DVP05-LAH-001 | DVP05-L-001 | PCS | 107-GL | ALARM - LEVEL - HIGH |  | 172.0 | K.O. POT HIGH LEVEL |  |  |  | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-LSH-001 | DVP05-L-001 | PKG | 107-GL | SWITCH - LEVEL - HIGH | DVP05-KP1 | 172.0 | K.O. POT HIGH LEVEL | 13167 | Fixed | - | REF | 12 | F | Ops | N.I.S | DI | 1 |  | 35 | UTIL | [6 empty] | 01
DVP05 | DVP05-LAH-002 | DVP05-L-002 | PCS | 107-GL | ALARM - LEVEL - HIGH |  | 172.0 | RECEIVER HIGH LEVEL |  |  |  | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-LSH-002 | DVP05-L-002 | PKG | 107-GL | SWITCH - LEVEL - HIGH | DVP05-RC1 | 172.0 | RECEIVER HIGH LEVEL | 13168 | Fixed | - | REF | 12 | F | Ops | N.I.S | DI | 1 |  | 35 | UTIL | [6 empty] | 01
DVP05 | DVP05-PI-001 | DVP05-P-001 | FLD | 107-GL | PRESSURE GAUGE | 25-N-SS1U-0-9028891 | 172.0 | N2 SUPPLY |  | 10 barg |  | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100 | KP0006/P6 |  |  |  | 01
DVP05 | DVP05-PSV-002 | DVP05-P-002 | FLD | 107-GL | PRESSURE RELIEF VALVE | 25-HT-CS3A-0-9025417 | 172.0 | VC1 HTF RELIEF |  | 10 barg | +/- 10% | N/A | - | - | - | [6 empty] | BROADY | 2531D-C-B000 | KS0001/P |  |  |  | 01
DVP05 | DVP05-PSH-003 | DVP05-P-003 | PKG | 107-GL | SWITCH - PRESSURE - HIGH | DVP05 | 172.0 | CONDENSATE TO VC1 |  |  |  | SHE | REQ | C | Ops | [12 empty] | 01
DVP05 | DVP05-PIA-004 | DVP05-P-004 | PCS | 107-GL | INDICATOR/ALARM - PRESSURE |  | 172.0 | PRESSURE |  |  |  | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-PT-004A | DVP05-P-004 | PKG | 107-GL | TRANSMITTER - PRESSURE - DIAPHRAGM |  | 172.0 | PRESSURE | 13169 |  |  | REF | REQ | C | Ops | N.I.S | AI | 1 |  | 13 | UTIL | [6 empty] | 01
DVP05 | DVP05-PT-004B | DVP05-P-004 | PKG | 107-GL | TRANSMITTER - PRESSURE - DIAPHRAGM |  | 172.0 | PRESSURE |  |  |  | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-PRV-006 | DVP05-P-006 | PKG | 107-GL | CONTROL VALVE SELF ACTUATING |  | 172.0 | N2 SUPPLY |  | set @ ? barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
DVP05 | DVP05-PRV-007 | DVP05-P-007 | PKG | 107-GL | CONTROL VALVE SELF ACTUATING |  | 172.0 | N2 SUPPLY |  | set @ ? barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
DVP05 | DVP05-PI-009 | DVP05-P-009 | FLD | 107-GL | PRESSURE GAUGE | 40-P-PT1A-0-9025422 | 172 | CARBON DRUM INLET | L15719 | -1 TO 1 barg |  | REF | REQ | C | Ref | [6 empty] | WIKA | 233.30.063 | KP0006/P12 |  |  |  | 23
DVP05 | DVP05-RO-001 | DVP05-R-001 | PKG | 107-GL | RESTRICTION ORIFICE |  | 172.0 | TCV-005 BYPASS | [19 empty] | 01
DVP05 | DVP05-TI-001 | DVP05-T-001 | FLD | 107-GL | INDICATOR - TEMPERATURE | 25-CWR-CS1B-AC-9025424 | 172.0 | COOLING WATER RTN |  | 0 to 60 degC | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | S5550/4 | KT0003/P1 |  |  |  | 01
DVP05 | DVP05-TI-002 | DVP05-T-002 | PCS | 107-GL | INDICATOR - TEMPERATURE |  | 172.0 | TEMPERATURE |  |  |  | SHE | REQ | C | Ref | [12 empty] | 01
DVP05 | DVP05-TSH-002 | DVP05-T-002 | PKG | 107-GL | SWITCH - TEMPERATURE - HIGH |  | 172.0 | TEMPERATURE HIGH |  |  |  | SHE | 12 | C | Ops | [12 empty] | 01
DVP05 | DVP05-TT-002 | DVP05-T-002 | PKG | 107-GL | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 172.0 | TEMPERATURE | 13170 |  |  | SHE | 12 | C | Ops | N.I.S | AI | 1 |  | 13 | UTIL | [6 empty] | 01
DVP05 | DVP05-TSH-003 | DVP05-T-003 | PKG | 107-GL | SWITCH - TEMPERATURE - HIGH |  | 172.0 | TEMPERATURE HIGH |  |  |  | SHE | 12 | C | Ops | [12 empty] | 01
DVP05 | DVP05-TSH-004 | DVP05-T-004 | PKG | 107-GL | SWITCH - TEMPERATURE - HIGH |  | 172.0 | TEMPERATURE HIGH |  |  |  | REF | 12 | C | Ops | [12 empty] | 01
DVP05 | DVP05-TCV-005 | DVP05-T-005 | PKG | 107-GL | CONTROL VALVE SELF ACTUATING |  | 172.0 |  |  |  |  | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-TE-005 | DVP05-T-005 | PKG | 107-GL | ELEMENT - TEMPERATURE - CAPILLARY |  | 172.0 |  |  |  |  | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-YA-001 | DVP05-Y-001 | PCS | 107-GL | ALARM - FAULT |  | 172.0 |  |  |  |  | N/A | - | - | - | [12 empty] | 01
DVP05 | DVP05-YS-001 | DVP05-Y-001 | PKG | 107-GL | SWITCH - FAULT |  | 172.0 | FAULT | 13171 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | UTIL | [6 empty] | 01
EF20 | EF20-DPS-001 | EF20-DP-001 | FLD | HVAC | Differential pressure switch | CTC extract fan | 155.0 | CTC extract fan dP |  | 1200kPa | [11 empty] | DELTA CONTROLS LTD | N3010ICNOGA30 |  |  |  |  | 01
EH01 | EH01-FE-001 | EH01-F-001 | PKG | 107-FA | SMI - AIR FLOW SENSOR | EH01 | 029.9 | AIR FLOW |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
EH01 | EH01-FI-001 | EH01-F-001 | HCR | 107-FA | INDICATOR - FLOW | EH01 CONTROL PANEL | 029.9 | AIR FLOW |  | - | - | REF | REQ | F |  | N.I.S |  |  |  | 0 | [7 empty] | 01
EH01 | EH01-HS-001A | EH01-H-001 | HCR | 107-FA | SWITCH - PUSHBUTTON | EH01 CONTROL PANEL | 029.9 | LOW AIR MUTE |  | - | - | REF | REQ | F |  | N.I.S |  |  |  | 0 | [7 empty] | 01
EH01 | EH01-HS-001B | EH01-H-001 | LCP | 107-FA | SWITCH - PUSHBUTTON | EH01 LOCAL PANEL | 029.9 | LOW AIR MUTE |  | - | - | REF | REQ | F |  | N.I.S |  |  |  | 0 | [7 empty] | 01
EH01 | EH01-XL-001A | EH01-X-001 | HCR | 107-FA | INDICATOR - PANEL | EH01 CONTROL PANEL | 029.9 | AIR SAFE |  | - | - | REF | REQ | F |  | N.I.S |  |  |  | 0 | [7 empty] | 01
EH01 | EH01-XL-001B | EH01-X-001 | LCP | 107-FA | INDICATOR - PANEL | EH01 LOCAL PANEL | 029.9 | AIR SAFE |  | - | - | REF | REQ | F |  | N.I.S |  |  |  | 0 | [7 empty] | 01
EH01 | EH01-XA-002 | EH01-X-002 | PKG | 107-FA | ALARM - AUDIBLE | EH01 | 029.9 | AIR FAIL |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
EH01 | EH01-XL-002A | EH01-X-002 | HCR | 107-FA | INDICATOR - PANEL | EH01 CONTROL PANEL | 029.9 | AIR FAIL |  | - | - | REF | REQ | F |  | N.I.S |  |  |  | 0 | [7 empty] | 01
EH01 | EH01-XL-002B | EH01-X-002 | LCP | 107-FA | INDICATOR - PANEL | EH01 LOCAL PANEL | 029.9 | AIR FAIL |  | - | - | REF | REQ | F |  | N.I.S |  |  |  | 0 | [7 empty] | 01
EH01 | EH01-YA-001 | EH01-Y-001 | PCS | 107-FA | ALARM - COMMON |  |  | COMMON ALARM | [11 empty] | 0 | [7 empty] | 01
EH01 | EH01-YS-001 | EH01-Y-001 | HCR | 107-FA | COMMON ALARM | EH01 CONTROL PANEL | 029.9 | COMMON ALARM | 8610 | - | - |  | 12 | F |  | I.S | DI |  |  | 32 | HYD | [6 empty] | 01
EH02 | EH02-HS-001 | EH02-H-001 | PKG | 107-PA | SWITCH - HAND OP. | EH02 | 029.10 | FAN START |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [5 empty] | FAN START | DI | 01
EH02 | EH02-HS-002 | EH02-H-002 | PKG | 107-PA | SWITCH - HAND OP. | EH02 | 029.10 | FAN STOP |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [5 empty] | FAN STOP | DI | 01
EH02 | EH02-HS-003 | EH02-H-003 | PKG | 107-PA | SWITCH - HAND OP. | EH02 | 029.10 | EMERGENCY STOP |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [5 empty] | EMERGENCY STOP | DI | 01
EH02 | EH02-HS-004 | EH02-H-004 | PKG | 107-PA | SWITCH - HAND OP. | EH02 | 029.10 | PASSPORT OUTER DOOR |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-SOV-001 | EH02-H-004 | PKG | 107-PA | SOLENOID VALVE | EH02 | 029.10 | PASSPORT OUTER DOOR |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DO | 01
EH02 | EH02-YS-002 | EH02-H-004 | PKG | 107-PA | PROXIMITY SENSOR - CLOSED | EH02 | 029.10 | PASSPORT OUTER DOOR |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-HS-005 | EH02-H-005 | PKG | 107-PA | SWITCH - HAND OP. | EH02 | 029.10 | PASSPORT INNER DOOR |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-SOV-002 | EH02-H-005 | PKG | 107-PA | SOLENOID VALVE | EH02 | 029.10 | PASSPORT INNER DOOR |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DO | 01
EH02 | EH02-YS-003 | EH02-H-005 | PKG | 107-PA | PROXIMITY SENSOR - CLOSED | EH02 | 029.10 | PASSPORT INNER DOOR |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-HS-006 | EH02-H-006 | PKG | 107-PA | SWITCH - HAND OP. | EH02 | 029.10 | DRUM PORT OUTER SEAL |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-SOV-003 | EH02-H-006 | PKG | 107-PA | SOLENOID VALVE | EH02 | 029.10 | DRUM PORT OUTER SEAL |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DO | 01
EH02 | EH02-YS-004 | EH02-H-006 | PKG | 107-PA | PROXIMITY SENSOR - CLOSED | EH02 | 029.10 | DRUM PORT OUTER SEAL |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-HS-007 | EH02-H-007 | PKG | 107-PA | SWITCH - HAND OP. | EH02 | 029.10 | DRUM PORT ACCESS LID |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-SOV-004 | EH02-H-007 | PKG | 107-PA | SOLENOID VALVE | EH02 | 029.10 | DRUM PORT ACCESS LID |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DO | 01
EH02 | EH02-YS-005 | EH02-H-007 | PKG | 107-PA | PROXIMITY SENSOR - CLOSED | EH02 | 029.10 | DRUM PORT ACCESS LID |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-HS-008 | EH02-H-008 | PKG | 107-PA | SWITCH - HAND OP. | EH02 | 029.10 | WASTE PORT LID RELEASE |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-SOV-005 | EH02-H-008 | PKG | 107-PA | SOLENOID VALVE | EH02 | 029.10 | WASTE PORT LID RELEASE |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DO | 01
EH02 | EH02-YS-006 | EH02-H-008 | PKG | 107-PA | PROXIMITY SENSOR - CLOSED | EH02 | 029.10 | WASTE PORT LID RELEASE |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-PDI-002 | EH02-P-002 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | EH02 | 029.10 | PRIMARY FILTER DIFF PRESS |  | 0 to 250 pA | +/- 5% | REF | 12 | C | [5 empty] | 0 | [7 empty] | 01
EH02 | EH02-PI-003 | EH02-P-003 | PKG | 107-PA | PRESSURE GAUGE | EH02 | 029.10 | ISOLATOR PRESSURE |  | 0 to 250 pA | +/- 1% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
EH02 | EH02-PT-003 | EH02-P-003 | PKG | 107-PA | TRANSMITTER - PRESSURE | EH02 | 029.10 | ISOLATOR PRESSURE |  | 0 to 140 pA | +/- 1% |  | 12 | C |  | I.S |  |  |  | 0 | [6 empty] | AI | 01
EH02 | EH02-PDI-004 | EH02-P-004 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | EH02 | 029.10 | SECONDARY FILTER DIFF PRESS |  | 0 to 250 pA | +/- 5% | REF | 12 | C | [5 empty] | 0 | [7 empty] | 01
EH02 | EH02-PDI-005 | EH02-P-005 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | EH02 | 029.10 | EXHAUST FILTER DIFF PRESS |  | 0 to 500 pA | +/- 5% | REF | 12 | C | [5 empty] | 0 | UTIL | [6 empty] | 01
EH02 | EH02-PSL-006 | EH02-P-006 | PKG | 107-PA | SWITCH - PRESSURE - LOW | EH02 | 029.10 | ISOLATOR PRESSURE |  | set @ commish. | +/- 1% | REF | 12 | C |  | I.S |  |  |  | 0 | [6 empty] | DI | 01
EH02 | EH02-XA-001 | EH02-X-001 | PKG | 107-PA | ALARM - MISC. | EH02 | 029.10 | COMMON ALARM |  | - | - |  | 12 | F |  | I.S |  |  |  | 0 | [6 empty] | DO | 01
EH02 | EH02-XL-001 | EH02-X-001 | PKG | 107-PA | INDICATOR - LAMP | EH02 | 029.10 | COMMON ALARM |  | - | - |  | 12 | F |  | I.S |  |  |  | 0 | [6 empty] | DO | 01
EH02 | EH02-XL-002 | EH02-X-002 | PKG | 107-PA | INDICATOR - LAMP | EH02 | 029.10 | RUN INDICATION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [6 empty] | DO | 01
EH02 | EH02-YA-001 | EH02-Y-001 | PCS | 107-PA | ALARM - COMMON | EH02 |  | COMMON ALARM | [11 empty] | 0 | [7 empty] | 01
EH02 | EH02-YS-001 | EH02-Y-001 | PKG | 107-PA | COMMON ALARM | EH02 | 029.10 | COMMON ALARM | 8612 | - | - |  | 12 | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ELECT | ELECT-XA-001 | ELECT-X-001 | PCS | N/A | ALARM - MAINS FAILED |  |  | MAINS STATUS | [11 empty] | 0 | [7 empty] | 01
ELECT | ELECT-XS-001 | ELECT-X-001 | MCC | N/A | SWITCH - MAINS STATUS | SWITCHBOARD | 018.0 | MAINS STATUS | 8614 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ELECT | ELECT-XA-002 | ELECT-X-002 | PCS | N/A | ALARM - STATUS |  |  | GENERATOR STATUS | [11 empty] | 0 | [7 empty] | 01
ELECT | ELECT-XS-002 | ELECT-X-002 | MCC | N/A | SWITCH - GENERATOR STATUS | SWITCHBOARD | 018.0 | GENERATOR STATUS | 8615 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ELECT | ELECT-XA-003 | ELECT-X-003 | PCS | N/A | ALARM - STATUS |  |  | TRANSFER SWITCH STATUS | [11 empty] | 0 | [7 empty] | 01
ELECT | ELECT-XS-003 | ELECT-X-003 | MCC | N/A | SWITCH - TRANSFER STATUS | SWITCHBOARD | 018.0 | TRANSFER SWITCH STATUS | 8616 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ET01 | ET01-BD-001 | ET01-B-001 | FLD | 107-LC | RUPTURE DISC | 150-DR-PP1A-9027050 | 011.1 | BURSTING DISC | 6687 | 100 mbarg | - |  | 12 | F |  | I.S | DI |  |  | 32 | UTIL | BS&B | KBAS | KS0003 | TI702-SP-5077 |  |  | 01
ET01 | ET01-YI-001 | ET01-B-001 | PCS | 107-LC | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01
ET01 | ET01-DIC-001 | ET01-D-001 | PCS | 107-LC | INDICATING CONTR. - MOTOR DRIVE |  |  | P1 EFFLUENT PUMP | [11 empty] | 0 | [7 empty] | 01
ET01 | ET01-DS-001 | ET01-D-001 | MCC | 107-LC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P1 EFFLUENT PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ET01 | ET01-DY-001 | ET01-D-001 | MCC | 107-LC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P1 EFFLUENT PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ET01 | ET01-DYC-001 | ET01-D-001 | MCC | 107-LC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 011.1 | P1 EFFLUENT PUMP | 8617 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
ET01 | ET01-DIC-002 | ET01-D-002 | PCS | 107-LC | INDICATING CONTR. - MOTOR DRIVE |  |  | P2 EFFLUENT PUMP | [11 empty] | 0 | [7 empty] | 01
ET01 | ET01-DS-002 | ET01-D-002 | MCC | 107-LC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P2 EFFLUENT PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ET01 | ET01-DY-002 | ET01-D-002 | MCC | 107-LC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P2 EFFLUENT PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ET01 | ET01-DYC-002 | ET01-D-002 | MCC | 107-LC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 011.1 | P2 EFFLUENT PUMP | 8618 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
ET01 | ET01-LI-001 | ET01-L-001 | PCS | 107-LC | INDICATOR - LEVEL |  |  | TANK LEVEL |  |  |  |  | By request | [6 empty] | 0 | [7 empty] | 01
ET01 | ET01-LT-001 | ET01-L-001 | FLD | 107-LC | TRANSMITTER - LEVEL | ET01/N2/100 | 011.1 | TANK LEVEL |  |  |  |  | By request | C |  | I.S | AI |  |  | 11 | UTIL | VEGA | VEGASON51X | KL0025 | TI702-SP-5150 |  |  | 01
ET01 | ET01-LAH-002 | ET01-L-002 | PCS | 107-LC | ALARM - LEVEL - HIGH |  |  | TANK HIGH LEVEL | L6463 | On/Off | On/Off | SHE | 24 | [6 empty] | 0 | [7 empty] | 01
ET01 | ET01-LE-002 | ET01-L-002 | FLD | 107-LC | ELEMENT - LEVEL | ET01/N4/80 | 011.1 | TANK HIGH LEVEL | L6463 | On/Off | On/Off | SHE | 24 | F |  | I.S |  |  |  | 0 |  | ENDRESS + HAUSER | [5 empty] | 01
ET01 | ET01-LSH-002 | ET01-L-002 | CPR | 107-LC | SWITCH - LEVEL - HIGH | ET01/N4/80 | 011.1 | TANK HIGH LEVEL |  | - | - |  |  | F |  | N.I.S | DI |  |  | 35 | UTIL | ENDRESS + HAUSER | FDL31-GYY9AC70 | KL0014 |  |  |  | 01
ET01 | ET01-PI-001 | ET01-P-001 | FLD | 107-LC | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-W-9027064 | 011.1 | P1 DISCHARGE PRESSURE |  | -1 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
ET01 | ET01-PI-002 | ET01-P-002 | FLD | 107-LC | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-W-9027060 | 011.1 | P2 DISCHARGE PRESSURE |  | -1 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
ET01 | ET01-RO-002 | ET01-R-002 | FLD | 107-LC | RESTRICTION ORIFICE PLATE | 25-P-PT1A-W-9027062 | 011.1 | MINIMUM FLOW BYPASS |  | 4.0 m3/hr | - | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
ET01 | ET01-LI-003 | ET01-Y-001 | PKG | 107-LC | INDICATOR - LEVEL | ET01-P1 SEAL POT | 011.1 | COMMON ALARM |  | - | - |  | REQ | F | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-LSH-004 | ET01-Y-001 | PKG | 107-LC | SWITCH - LEVEL - HIGH | ET01-P1 SEAL POT | 011.1 | COMMON ALARM |  |  | - |  | By request | F | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-LSL-005 | ET01-Y-001 | PKG | 107-LC | SWITCH - LEVEL - LOW | ET01-P1 SEAL POT | 011.1 | COMMON ALARM |  |  | - |  | By request | F | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-PI-003 | ET01-Y-001 | PKG | 107-LC | PRESSURE GAUGE | ET01-P1 SEAL POT | 011.1 | COMMON ALARM |  | 0 to 10 barg | +/- 5% |  | REQ | C | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-PSL-005 | ET01-Y-001 | PKG | 107-LC | SWITCH - PRESSURE - LOW | ET01-P1 SEAL POT | 011.1 | COMMON ALARM | L9012 |  |  |  | By request | C | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-TI-001 | ET01-Y-001 | PKG | 107-LC | INDICATOR - TEMPERATURE | ET01-P1 SEAL POT | 011.1 | COMMON ALARM |  | 0 to 120 degC | +/- 5% |  | REQ | C | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-YA-001 | ET01-Y-001 | PCS | 107-LC | ALARM - COMMON |  |  | COMMON ALARM | [11 empty] | 0 | [5 empty] | FUTURE INSTALLATION |  | 01
ET01 | ET01-YS-001 | ET01-Y-001 | PKG | 107-LC | SWITCH - COMMON ALARM | ET01-P1 SEAL POT | 011.1 | COMMON ALARM | 9012 | - | - |  | REQ | F |  | I.S | DI |  |  | 32 | UTIL | TAV ENGINEERING LTD / ROTOTHERM HNL | F71 / 300 SERIES |  | TI702-SP-5163 | FUTURE INSTALLATION |  | 01
ET01 | ET01-LI-006 | ET01-Y-002 | PKG | 107-LC | INDICATOR - LEVEL | ET01-P2 SEAL POT | 011.1 | COMMON ALARM |  | Fixed | - |  | REQ | F | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-LSH-007 | ET01-Y-002 | PKG | 107-LC | SWITCH - LEVEL - HIGH | ET01-P2 SEAL POT | 011.1 | COMMON ALARM |  |  | - |  | By request | F | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-LSL-008 | ET01-Y-002 | PKG | 107-LC | SWITCH - LEVEL - LOW | ET01-P2 SEAL POT | 011.1 | COMMON ALARM |  |  | - |  | By request | F | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-PI-004 | ET01-Y-002 | PKG | 107-LC | PRESSURE GAUGE | ET01-P2 SEAL POT | 011.1 | COMMON ALARM |  | 0 to 10 barg | +/- 5% |  | REQ | C | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-PSL-006 | ET01-Y-002 | PKG | 107-LC | SWITCH - PRESSURE - LOW | ET01-P2 SEAL POT | 011.1 | COMMON ALARM | L9013 |  |  |  | By request | C | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-TI-002 | ET01-Y-002 | PKG | 107-LC | INDICATOR - TEMPERATURE | ET01-P2 SEAL POT | 011.1 | COMMON ALARM |  | 0 to 120 degC | +/- 5% |  | REQ | C | [5 empty] | 0 | [7 empty] | 01
ET01 | ET01-YA-002 | ET01-Y-002 | PCS | 107-LC | ALARM - COMMON |  |  | COMMON ALARM | [11 empty] | 0 | [5 empty] | FUTURE INSTALLATION |  | 01
ET01 | ET01-YS-002 | ET01-Y-002 | PKG | 107-LC | SWITCH - COMMON ALARM | ET01-P2 SEAL POT | 011.1 | COMMON ALARM | 9013 | - | - |  | REQ | F |  | I.S | DI |  |  | 32 | UTIL | TAV ENGINEERING LTD / ROTOTHERM HNL | F71 / 300 SERIES |  | TI702-SP-5163 | FUTURE INSTALLATION |  | 01
ET02 | ET02-BD-001 | ET02-B-001 | FLD | 107-LC | RUPTURE DISC | 150-DR-PP1A-9027051 | 012.0 | BURSTING DISC | 6707 | 100 mbarg | - |  | 12 | F |  | I.S | DI |  |  | 32 | UTIL | BS&B | KBAS | KS0003 | TI702-SP-5077 |  |  | 01
ET02 | ET02-YI-001 | ET02-B-001 | PCS | 107-LC | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01
ET02 | ET02-DIC-001 | ET02-D-001 | PCS | 107-LC | INDICATING CONTR. - MOTOR DRIVE |  |  | P1 EFFLUENT PUMP | [11 empty] | 0 | [7 empty] | 01
ET02 | ET02-DS-001 | ET02-D-001 | MCC | 107-LC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P1 EFFLUENT PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ET02 | ET02-DY-001 | ET02-D-001 | MCC | 107-LC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P1 EFFLUENT PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ET02 | ET02-DYC-001 | ET02-D-001 | MCC | 107-LC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 012.0 | P1 EFFLUENT PUMP | 8619 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
ET02 | ET02-DIC-002 | ET02-D-002 | PCS | 107-LC | INDICATING CONTR. - MOTOR DRIVE |  |  | P2 EFFLUENT PUMP | [11 empty] | 0 | [7 empty] | 01
ET02 | ET02-DS-002 | ET02-D-002 | MCC | 107-LC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P2 EFFLUENT PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ET02 | ET02-DY-002 | ET02-D-002 | MCC | 107-LC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P2 EFFLUENT PUMP | [7 empty] | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
ET02 | ET02-DYC-002 | ET02-D-002 | MCC | 107-LC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 012.0 | P2 EFFLUENT PUMP | 8620 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
ET02 | ET02-LI-001 | ET02-L-001 | PCS | 107-LC | INDICATING CONTROLLER - LEVEL |  |  | TANK LEVEL |  |  |  |  | By request | [6 empty] | 0 | [7 empty] | 01
ET02 | ET02-LT-001 | ET02-L-001 | FLD | 107-LC | TRANSMITTER - LEVEL | ET02/N2/100 | 012.0 | TANK LEVEL |  |  |  |  | By request | C |  | I.S | AI |  |  | 11 | UTIL | VEGA | VEGASON51X | KL0025 | TI702-SP-5150 |  |  | 01
ET02 | ET02-LAH-002 | ET02-L-002 | PCS | 107-LC | ALARM - LEVEL - HIGH |  |  | TANK HIGH LEVEL | L6464 | On/Off | On/Off | SHE | 24 | [6 empty] | 0 | [7 empty] | 01
ET02 | ET02-LE-002 | ET02-L-002 | FLD | 107-LC | ELEMENT - LEVEL | ET02/N4/80 | 012.0 | TANK HIGH LEVEL | L6463 | On/Off | On/Off | SHE | 24 | F |  | I.S |  |  |  | 0 |  | ENDRESS + HAUSER | [5 empty] | 01
ET02 | ET02-LSH-002 | ET02-L-002 | CPR | 107-LC | SWITCH - LEVEL - HIGH | ET02/N4/80 | 012.0 | TANK HIGH LEVEL |  | - | - |  |  | F |  | N.I.S | DI |  |  | 35 | UTIL | ENDRESS + HAUSER | FTL51-GYY9BE7G4Y |  |  |  |  | 39
ET02 | ET02-PI-001 | ET02-P-001 | FLD | 107-LC | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-W-9027055 | 012.0 | P1 DISCHARGE PRESSURE |  | -1 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
ET02 | ET02-PI-002 | ET02-P-002 | FLD | 107-LC | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-W-9027057 | 012.0 | P2 DISCHARGE PRESSURE |  | -1 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
ET02 | ET02-RO-002 | ET02-R-002 | FLD | 107-LC | RESTRICTION ORIFICE PLATE | 25-P-PT1A-W-9027053 | 012.0 | MINIMUM FLOW BYPASS |  | 4.0 m3/hr | - | REF | REQ | F | [5 empty] | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
ET02 | ET02-LI-003 | ET02-Y-001 | PKG | 107-LC | INDICATOR - LEVEL | ET02-P1 SEAL POT | 012.0 | COMMON ALARM |  | Fixed | - |  | REQ | F | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-LSH-004 | ET02-Y-001 | PKG | 107-LC | SWITCH - LEVEL - HIGH | ET02-P1 SEAL POT | 012.0 | COMMON ALARM |  |  | - |  | By request | F | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-LSL-005 | ET02-Y-001 | PKG | 107-LC | SWITCH - LEVEL - LOW | ET02-P1 SEAL POT | 012.0 | COMMON ALARM |  |  | - |  | By request | F | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-PI-003 | ET02-Y-001 | PKG | 107-LC | PRESSURE GAUGE | ET02-P1 SEAL POT | 012.0 | COMMON ALARM |  | 0 to 10 barg | +/- 5% |  | REQ | C | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-PSL-005 | ET02-Y-001 | PKG | 107-LC | SWITCH - PRESSURE - LOW | ET02-P1 SEAL POT | 012.0 | COMMON ALARM |  |  |  |  | By request | C | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-TI-001 | ET02-Y-001 | PKG | 107-LC | INDICATOR - TEMPERATURE | ET02-P1 SEAL POT | 012.0 | COMMON ALARM |  | 0 to 120 degC | +/- 5% |  | REQ | C | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-YA-001 | ET02-Y-001 | PCS | 107-LC | ALARM - COMMON |  |  | COMMON ALARM | [11 empty] | 0 | [5 empty] | FUTURE INSTALLATION |  | 01
ET02 | ET02-YS-001 | ET02-Y-001 | PKG | 107-LC | SWITCH - COMMON ALARM | ET02-P1 SEAL POT | 012.0 | COMMON ALARM | 9014 | - | - |  | REQ | F |  | I.S | DI |  |  | 32 | UTIL | TAV ENGINEERING LTD / ROTOTHERM HNL | F71 / 300 SERIES |  | TI702-SP-5163 | FUTURE INSTALLATION |  | 01
ET02 | ET02-LI-006 | ET02-Y-002 | PKG | 107-LC | INDICATOR - LEVEL | ET02-P2 SEAL POT | 012.0 | COMMON ALARM |  | - | - |  | REQ | F | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-LSH-007 | ET02-Y-002 | PKG | 107-LC | SWITCH - LEVEL - HIGH | ET02-P2 SEAL POT | 012.0 | COMMON ALARM |  |  | - |  | By request | F | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-LSL-008 | ET02-Y-002 | PKG | 107-LC | SWITCH - LEVEL - LOW | ET02-P2 SEAL POT | 012.0 | COMMON ALARM |  |  | - |  | By request | F | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-PI-004 | ET02-Y-002 | PKG | 107-LC | PRESSURE GAUGE | ET02-P2 SEAL POT | 012.0 | COMMON ALARM |  | 0 to 10 barg | +/- 5% |  | REQ | C | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-PSL-006 | ET02-Y-002 | PKG | 107-LC | SWITCH - PRESSURE - LOW | ET02-P2 SEAL POT | 012.0 | COMMON ALARM |  |  |  |  | By request | C | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-TI-002 | ET02-Y-002 | PKG | 107-LC | INDICATOR - TEMPERATURE | ET02-P2 SEAL POT | 012.0 | COMMON ALARM |  | 0 to 120 degC | +/- 5% |  | REQ | C | [5 empty] | 0 | [7 empty] | 01
ET02 | ET02-YA-002 | ET02-Y-002 | PCS | 107-LC | ALARM - COMMON |  |  | COMMON ALARM | [11 empty] | 0 | [5 empty] | FUTURE INSTALLATION |  | 01
ET02 | ET02-YS-002 | ET02-Y-002 | PKG | 107-LC | SWITCH - COMMON ALARM | ET02-P2 SEAL POT | 012.0 | COMMON ALARM | 9015 | - | - |  | REQ | F |  | I.S | DI |  |  | 32 | UTIL | TAV ENGINEERING LTD / ROTOTHERM HNL | F71 / 300 SERIES |  | TI702-SP-5163 | FUTURE INSTALLATION |  | 01
FD02 | FD02-BD-001 | FD02-B-001 | FLD | 107-EV | RUPTURE DISC | 40-P-PT1A-E-9024915 | 106.0 | BURSTING DISC | 6729 | 6.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | C1 | BS&B | SSR / BAS + | KS0003/P6 | TI702-SP-5077 |  |  | 01
FD02 | FD02-YI-001 | FD02-B-001 | PCS | 107-EV | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01
FD02 | FD02-BD-002 | FD02-B-002 | FLD | 107-EV | RUPTURE DISC | 40-P-PT1A-C-9024927 | 106.0 | RC1 BURSTING DISC | 6730 | 6.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | C1 | BS&B | RLS / BAS + | KS0003 | TI702-SP-5077 |  |  | 01
FD02 | FD02-YI-002 | FD02-B-002 | PCS | 107-EV | ALARM - RUPTURE DISC FAIL |  |  | RC1 BURSTING DISC | [11 empty] | 0 | [7 empty] | 01
FD02 | FD02-CV-002 | FD02-C-002 | FLD | 107-EV | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-E-9024901 | 106.0 | 0.8 BAR N2 SUPPLY | 7136 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD02 | FD02-CY-002 | FD02-C-002 | FLD | 107-EV | SOLENOID VALVE | RACK MOUNTED |  | 0.8 BAR N2 SUPPLY | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD02 | FD02-ZSC-002 | FD02-C-002 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-ZSO-002 | FD02-C-002 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-CV-003 | FD02-C-003 | FLD | 107-EV | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-E-9024902 | 106.0 | 6 BAR N2 SUPPLY | 7156 | - | - | REF | REQ | F |  | I.S | AO |  |  | 0 | C1 | XOMOX TUFLIN / FLOWSERVE | R202 / Logix 510si | KV0007 | TI702-SP-5079 |  |  | 01
FD02 | FD02-CY-003 | FD02-C-003 | FLD | 107-EV | SOLENOID VALVE | RACK MOUNTED |  | 6 BAR N2 SUPPLY | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  |  |  |  | 01
FD02 | FD02-ZSC-003 | FD02-C-003 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | [6 empty] | 01
FD02 | FD02-ZSO-003 | FD02-C-003 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | [6 empty] | 01
FD02 | FD02-CV-004 | FD02-C-004 | PKG | 107-EV | SOLENOID VALVE | FD02 | 106.0 | FILTER PULSE | 8621 | - | - | REF | REQ | F |  | I.S | DO |  |  | 41 | C1 | FLUID AUTOMATION SYSTEMS | 01-311P-00-H0 |  | TI702-SP-5152 |  |  | 01
FD02 | FD02-CV-005 | FD02-C-005 | FLD | 107-EV | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-E-9024917 | 106.0 | RECIRC | 7250 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD02 | FD02-CY-005 | FD02-C-005 | FLD | 107-EV | SOLENOID VALVE | RACK MOUNTED |  | RECIRC | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD02 | FD02-ZSC-005 | FD02-C-005 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RECIRC | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-ZSO-005 | FD02-C-005 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RECIRC | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-CV-006 | FD02-C-006 | FLD | 107-EV | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-E-9024918 | 106.0 | TO VC1 | 7307 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD02 | FD02-CY-006 | FD02-C-006 | FLD | 107-EV | SOLENOID VALVE | RACK MOUNTED |  | TO VC1 | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD02 | FD02-ZSC-006 | FD02-C-006 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO VC1 | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-ZSO-006 | FD02-C-006 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO VC1 | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N | TI702-SP-5001 | TI702-SP-5001 |  |  | 01
FD02 | FD02-CV-008 | FD02-C-008 | FLD | 107-EV | V-BALL VALVE - CONTROL - F.C. | 40-VP-PT1A-0-9024922 | 106.0 | CONT. VACUUM | 6852 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
FD02 | FD02-CV-009 | FD02-C-009 | FLD | 107-EV | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9024922 | 037.0 | CONT. VACUUM | 7281 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD02 | FD02-CY-009 | FD02-C-009 | FLD | 107-EV | SOLENOID VALVE | RACK MOUNTED |  | CONT. VACUUM | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD02 | FD02-ZSC-009 | FD02-C-009 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CONT. VACUUM | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N | TI702-SP-5001 | TI702-SP-5001 |  |  | 01
FD02 | FD02-ZSO-009 | FD02-C-009 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CONT. VACUUM | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N | TI702-SP-5001 | TI702-SP-5001 |  |  | 01
FD02 | FD02-CV-010 | FD02-C-010 | FLD | 107-EV | V-BALL VALVE - CONTROL - F.C. | 40-P-PT1A-0-9024920 | 106.0 | SCRUBBER 03 | 6818 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
FD02 | FD02-CV-011 | FD02-C-011 | FLD | 107-EV | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024920 | 008.3 | SCRUBBER 03 | 7254 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD02 | FD02-CY-011 | FD02-C-011 | FLD | 107-EV | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 03 | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD02 | FD02-ZSC-011 | FD02-C-011 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 03 | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N | TI702-SP-5001 | TI702-SP-5001 |  |  | 01
FD02 | FD02-ZSO-011 | FD02-C-011 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 03 | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N | TI702-SP-5001 | TI702-SP-5001 |  |  | 01
FD02 | FD02-CV-012 | FD02-C-012 | FLD | 107-EV | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-D-9024907 | 106.0 | COLD HTF RTN | 6771 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
FD02 | FD02-CV-014 | FD02-C-014 | FLD | 107-EV | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-E-9024916 | 106.0 | RC1 INLET | 7309 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD02 | FD02-CY-014 | FD02-C-014 | FLD | 107-EV | SOLENOID VALVE | RACK MOUNTED |  | RC1 INLET | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD02 | FD02-ZSC-014 | FD02-C-014 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RC1 INLET | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-ZSO-014 | FD02-C-014 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RC1 INLET | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-CV-017 | FD02-C-017 | FLD | 107-EV | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-C-9024933 | 106.0 | NITROGEN TO RC1 | 6839 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
FD02 | FD02-CV-018 | FD02-C-018 | FLD | 107-EV | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9024936 | 106.0 | TP1 DISCHARGE | 7162 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD02 | FD02-CY-018 | FD02-C-018 | FLD | 107-EV | SOLENOID VALVE | RACK MOUNTED |  | TP1 DISCHARGE | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD02 | FD02-ZSC-018 | FD02-C-018 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TP1 DISCHARGE | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-ZSO-018 | FD02-C-018 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TP1 DISCHARGE | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-CV-019 | FD02-C-019 | FLD | 107-EV | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029258 | 106.0 | HOT HTF SUPPLY | 7124 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
FD02 | FD02-CY-019 | FD02-C-019 | FLD | 107-EV | SOLENOID VALVE | RACK MOUNTED |  | HOT HTF SUPPLY | [7 empty] | I.S | DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD02 | FD02-ZSC-019 | FD02-C-019 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-ZSO-019 | FD02-C-019 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-CV-020 | FD02-C-020 | FLD | 107-EV | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-C-9029605 | 106.0 | COLD HTF SUPPLY | 7490 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
FD02 | FD02-ZSC-020 | FD02-C-020 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-ZSO-020 | FD02-C-020 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-CV-021 | FD02-C-021 | FLD | 107-EV | SOLENOID VALVE | ADJ TO PT-002 | 106.0 | INTERLOCK | 8626 |  |  | SHE | [9 empty] | RSG | [5 empty] | 01
FD02 | FD02-DIC-001 | FD02-D-001 | PCS | 107-EV | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01
FD02 | FD02-DS-001 | FD02-D-001 | MCC | 107-EV | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | [7 empty] | N.I.S | DI |  |  | 35 | C1 | [6 empty] | 01
FD02 | FD02-DY-001 | FD02-D-001 | MCC | 107-EV | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | [7 empty] | N.I.S | DI |  |  | 35 | C1 | [6 empty] | 01
FD02 | FD02-DYC-001 | FD02-D-001 | MCC | 107-EV | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 106.0 | JACKET PUMP | 8622 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
FD02 | FD02-DIC-002 | FD02-D-002 | PCS | 107-EV | INDICATING CONTR. - MOTOR DRIVE |  |  | TP1 TRANSFER PUMP |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
FD02 | FD02-DS-002 | FD02-D-002 | MCC | 107-EV | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | C1 | [6 empty] | 01
FD02 | FD02-DY-002 | FD02-D-002 | MCC | 107-EV | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | C1 | [6 empty] | 01
FD02 | FD02-DYC-002 | FD02-D-002 | MCC | 107-EV | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 106.0 | TP1 TRANSFER PUMP | 8623 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
FD02 | FD02-FI-001 | FD02-F-001 | FLD | 107-EV | INDICATOR - FLOW | 25-N-SSU1-0-9028838 | 043.4 | N2 SUPPLY FLOW |  |  |  | REF | By request | C | [5 empty] | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
FD02 | FD02-FI-002 | FD02-F-002 | FLD | 107-EV | INDICATOR - FLOW | FD02 NITROGEN INLET | 106.0 | NITROGEN INLET |  |  |  | REF | By request | [14 empty] | 45
FD02 | FD02-FT-002 | FD02-F-002 | FLD | 107-EV | TRANSMITTER - FLOW | FD02 NITROGEN INLET | 106.0 | NITROGEN INLET |  |  |  | REF | By request |  |  | I.S | AI |  |  |  | C1 | ENDRESS + HAUSER | Proline T Mass 65F25 |  | TI702-SP-5061 |  |  | 45
FD02 | FD02-HS-001A | FD02-H-001 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02 TOP | 106.0 | AGITATOR START |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-001B | FD02-H-001 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02-GB1 | 106.0 | AGITATOR START |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-002A | FD02-H-002 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02 TOP | 106.0 | AGITATOR STOP |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-002B | FD02-H-002 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02-GB1 | 106.0 | AGITATOR STOP |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HIC-003 | FD02-H-003 | LCP | 107-EV | CONTROLLER - HAND | LCP ADJ TO FD02 TOP | 106.0 | AGITATOR SPEED CONTROL |  | - | - | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-004 | FD02-H-004 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02 TOP | 106.0 | SMOOTH/RESLURRY DISCHARGE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HV-005 | FD02-H-005 | FLD | 107-EV | HAND VALVE | 40-P-PT1A-0-9024826 | 106.0 | PROCESS INLET | 7460 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD02 | FD02-HZSC-005 | FD02-H-005 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS INLET | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-HZSO-005 | FD02-H-005 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01
FD02 | FD02-HV-006 | FD02-H-006 | FLD | 107-EV | HAND VALVE | 25-SO-PT1A-0-9024930 | 106.0 | SOLVENT INLET | 8121 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN |  | KV0007 |  |  |  | 01
FD02 | FD02-HZSC-006 | FD02-H-006 | FLD | 107-EV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENT INLET | [7 empty] | I.S | DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD02 | FD02-HZSO-006 | FD02-H-006 | FLD | 107-EV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENT INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01
FD02 | FD02-HS-007A | FD02-H-007 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02 TOP | 106.0 | AGITATOR RAISE/LOWER |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-007B | FD02-H-007 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02-GB1 | 106.0 | AGITATOR RAISE/LOWER |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HC-009 | FD02-H-009 | LCP | 107-EV | CONTROLLER - HAND | LCP ADJ TO FD02 TOP | 106.0 | AGITATOR SPEED UP/DOWN |  | - | - | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-011 | FD02-H-011 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02 TOP | 106.0 | FILTER PULSE JET ON/OFF | 8624 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | C1 | [6 empty] | 01
FD02 | FD02-HS-012 | FD02-H-012 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02 TOP | 106.0 | PANEL LOCAL/REMOTE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-013A | FD02-H-013 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02 TOP | 106.0 | EMERGENCY STOP |  | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-013B | FD02-H-013 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02-GB1 | 106.0 | EMERGENCY STOP |  | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-014 | FD02-H-014 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02-GB1 | 106.0 | BASE RAISE/LOWER |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-015 | FD02-H-015 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02-GB1 | 106.0 | GLOVEBOX LOCK/UNLOCK |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-016 | FD02-H-016 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02-GB1 | 106.0 | NITROGEN |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-017 | FD02-H-017 | LCP | 107-EV | SWITCH - HAND OP. | LCP ADJ TO FD02-GB1 | 106.0 | LIGHT |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-HS-018 | FD02-H-018 | FLD | 107-EV | SWITCH - HAND OP. | ADJ TO FD02-GB1 | 106.0 | LIGHT |  |  |  | REF | REQ | F | [13 empty] | 01
FD02 | FD02-LIC-001 | FD02-L-001 | PCS | 107-EV | INDICATING CONTROLLER - LEVEL |  |  | RC1 LEVEL |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-LT-001 | FD02-L-001 | FLD | 107-EV | TRANSMITTER - LEVEL | FD02-RC1/N4/100 | 106.0 | RC1 LEVEL |  |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | C1 | ENDRESS + HAUSER | FMR245 note2/3 | KL0028/P2 | TI702-SP-5026 | +/- 10% 0 - 30 l |  | 01
FD02 | FD02-LAH-002 | FD02-L-002 | PCS | 107-EV | ALARM - LEVEL - HIGH |  |  | RC1 HIGH LEVEL | L6467 | Off/on | Off/on | SHE | 24 | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-LE-002 | FD02-L-002 | FLD | 107-EV | ELEMENT - LEVEL | 40-P-PT1A-C-9024933 | 106.0 | RC1 HIGH LEVEL | L6467 | Off/on | Off/on | SHE | 24 | F |  | I.S |  |  |  | 0 |  | ENDRESS + HAUSER | [5 empty] | 01
FD02 | FD02-LSH-002 | FD02-L-002 | CPR | 107-EV | SWITCH - LEVEL - HIGH | 40-P-PT1A-C-9024933 | 106.0 | RC1 HIGH LEVEL | L6467 | Off/on | Off/on | SHE | 24 | C |  | N.I.S | DI |  |  | 35 | C1 | ENDRESS + HAUSER | FTL51C-4AELYY7G4AA | KL0014/P1 |  |  |  | 01
FD02 | FD02-PI-002B | FD02-P-002 | LCP | 107-EV | INDICATOR - PRESSURE | LCP ADJ TO FD02 TOP | 106.0 | PRESSURE | L8626 | -1 to 3 barg | +/- 40 mbarg | SHE | 12 | C |  | I.S |  |  |  | 0 | [7 empty] | 01
FD02 | FD02-PIC-002 | FD02-P-002 | PCS | 107-EV | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-PSH-002 | FD02-P-002 | [6 empty] | L8626 | +30 mbarg | +/-10 mbarg | SHE | 12
FD02 | FD02-PSL-002 | FD02-P-002 | [6 empty] | L8626 | -30 mbarg | +/- 10mbarg | SHE | 12
FD02 | FD02-PT-002 | FD02-P-002 | FLD | 107-EV | TRANSMITTER - PRESSURE | CONTROL PANEL | 106.0 | PRESSURE | L8626 | -1 to 3 barg | +/- 40 mbarg | SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | ROSEMOUNT | 3051S ULTRA |  | TI702-SP-5139 |  |  | 01
FD02 | FD02-PDI-003 | FD02-P-003 | PCS | 107-EV | INDICATOR - PRESSURE - DIFF |  |  | FILTER DIFF PRESSURE |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-PDT-003 | FD02-P-003 | PKG | 107-EV | TRANSMITTER - PRESSURE - DIFF | 50-P-PT1A-E-9024918 | 106.0 | FILTER DIFF PRESSURE |  |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | C1 | ROSEMOUNT | 3051 |  | TI702-SP-5151 |  |  | 01
FD02 | FD02-PIC-004 | FD02-P-004 | PCS | 107-EV | INDICATING CONTROLLER - PRESSURE |  |  | VC1 INLET PRESSURE |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-PIT-004 | FD02-P-004 | FLD | 107-EV | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-E-9024918 | 106.0 | VC1 INLET PRESSURE |  |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | C1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
FD02 | FD02-PI-005 | FD02-P-005 | FLD | 107-EV | PRESSURE GAUGE - DIAPHRAGM | 40-HT-CS3A-C-9024912 | 106.0 | JP1 SUCTION PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
FD02 | FD02-PI-006 | FD02-P-006 | FLD | 107-EV | PRESSURE GAUGE - DIAPHRAGM | 40-HT-CS3A-D-9024939 | 106.0 | JP1 DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
FD02 | FD02-PI-007 | FD02-P-007 | FLD | 107-EV | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-C-9024933 | 106.0 | RC1 PRESSURE |  | -1 to 1.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
FD02 | FD02-PI-008 | FD02-P-008 | FLD | 107-EV | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-0-9024936 | 106.0 | TP1 DISCHARGE PRESSURE |  | 0 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note3) | KP0006/1 |  |  |  | 01
FD02 | FD02-PSV-009 | FD02-P-009 | FLD | 107-EV | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9024940 | 106.0 | JACKET HTF RELIEF |  | 10 barg | +/- 10% |  | 24 | C | [5 empty] | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
FD02 | FD02-PSV-010 | FD02-P-010 | FLD | 107-EV | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9024941 | 106.0 | VC1 HTF RELIEF |  | 10 barg | +/- 10% |  | 24 | C | [5 empty] | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
FD02 | FD02-PRV-014 | FD02-P-014 | FLD | 107-EV | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028839 | 106.0 | N2 SUPPLY |  | set @ 2.0 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
FD02 | FD02-PI-015 | FD02-P-015 | DEL | 107-EV | PRESSURE GAUGE | DELETED |  | DELETED |  |  |  |  | REQ | C | [5 empty] | 0 | [5 empty] | DELETED |  | 01
FD02 | FD02-PSL-016 | FD02-P-016 | PKG | 107-EV | SWITCH - PRESSURE - LOW | DELETED | 106.0 | DELETED |  | set @ -30 mbar | +/- 1% |  | 12 | C | [5 empty] | 0 | [5 empty] | DELETED |  | 01
FD02 | FD02-PSH-017 | FD02-P-017 | PKG | 107-EV | SWITCH - PRESSURE - HIGH | DELETED | 106.0 | DELETED |  | set @ 30 mbar | +/- 1% |  | 12 | C | [5 empty] | 0 | [5 empty] | DELETED |  | 01
FD02 | FD02-PI-018 | FD02-P-018 | LCP | 107-EV | PRESSURE GAUGE | LCP ADJ TO FD02-GB1 | 106.0 | GLOVEBOX PRESSURE |  | 0.05 TO 0.5 kpA | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-PI-019 | FD02-P-019 | LCP | 107-EV | PRESSURE GAUGE | LCP ADJ TO FD02-GB1 | 106.0 | EXTRACT FILTER CONDITION |  | 0 to 125 pA | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-PI-020 | FD02-P-020 | PKG | 107-EV | PRESSURE GAUGE | 15-N-SS1U-0-9022494 | 106.0 | AGITATOR SEAL PRESSURE |  | 0 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-PI-021 | FD02-P-021 | LCP | 107-EV | PRESSURE GAUGE | LCP ADJ TO FD02-GB1 | 106.0 | NITROGEN PRESSURE |  | 0 to 1.6 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-PI-022 | FD02-P-022 | PKG | 107-EV | PRESSURE GAUGE | SEAL LUBRICATOR | 106.0 | AGI SEAL LUB PRESSURE |  | 0 to 6 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-PI-023 | FD02-P-023 | FLD | 107-EV | PRESSURE GAUGE | FD02-HE01 |  | FD02-HE01 |  | 0 to 6 barg | +/- 5% |  | REQ
FD02 | FD02-PI-024 | FD02-P-024 | FLD | 107-EV | PRESSURE GAUGE | FD02-HE01 |  | FD02-HE01 |  | 0 to 6 barg | +/- 5% |  | REQ
FD02 | FD02-SI-001 | FD02-S-001 | PCS | 107-EV | INDICATOR - SPEED |  |  | AGITATOR |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-SIC-001 | FD02-S-001 | PKG | 107-EV | AC INVERTER DRIVE | SWITCHROOM | 106.0 | AGITATOR |  |  |  | SHE | By request | F |  | N.I.S | AI |  |  | 13 | C1 |  |  |  |  | MIN SPEED 4 rpm |  | 01
FD02 | FD02-TE-002 | FD02-T-002 | FLD | 107-EV | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9024920 |  | VC1 VENT TEMPERATURE |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-TI-002 | FD02-T-002 | PCS | 107-EV | INDICATOR - TEMPERATURE |  |  | VC1 VENT TEMPERATURE | [11 empty] | 0 | [7 empty] | 01
FD02 | FD02-TT-002 | FD02-T-002 | FLD | 107-EV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 106.0 | VC1 VENT TEMPERATURE |  |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
FD02 | FD02-TE-003 | FD02-T-003 | FLD | 107-EV | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9024923 |  | VC1 HTF RTN TEMP |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-TI-003 | FD02-T-003 | PCS | 107-EV | INDICATOR - TEMPERATURE |  |  | VC1 HTF RTN TEMP | [11 empty] | 0 | [7 empty] | 01
FD02 | FD02-TT-003 | FD02-T-003 | FLD | 107-EV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 106.0 | VC1 HTF RTN TEMP |  |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
FD02 | FD02-TI-004 | FD02-T-004 | FLD | 107-EV | INDICATOR - TEMPERATURE | 40-HT-CS3A-D-9024907 | 106.0 | HTF TEMPERATURE |  |  |  | REF | By request | C | [5 empty] | 0 |  | WIKA | S5550/4 | KT0003 |  |  |  | 01
FD02 | FD02-TE-005 | FD02-T-005 | PKG | 107-EV | ELEMENT - TEMPERATURE - RTD | FD02/T1/40 |  | TEMPERATURE |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-TI-005A | FD02-T-005 | PCS | 107-EV | INDICATOR - TEMPERATURE |  |  | TEMPERATURE |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-TI-005B | FD02-T-005 | LCP | 107-EV | INDICATOR - TEMPERATURE | LCP ADJ TO FD02 TOP | 106.0 | TEMPERATURE |  |  |  | SHE | By request | C |  | I.S |  |  |  | 0 | [7 empty] | 01
FD02 | FD02-TT-005 | FD02-T-005 | PKG | 107-EV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 106.0 | TEMPERATURE |  |  |  | SHE | By request | C |  | I.S | AI |  |  | 11 | C1 | ROSEMOUNT | 244E |  | TI702-SP-5078 |  |  | 01
FD02 | FD02-TE-006 | FD02-T-006 | FLD | 107-EV | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-D-9024939 | 106.0 | JACKET INLET TEMP. | L6608 | -30 to 170 degC | +/-2degC | SHE | 12 | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-TIC-006 | FD02-T-006 | PCS | 107-EV | INDICATING CONTROLLER - TEMPERATURE |  | 106.0 | JACKET INLET TEMP. | L6608 | -30 to 170 degC | +/-2degC | SHE | 12 | [6 empty] | 0 | [7 empty] | 01
FD02 | FD02-TT-006 | FD02-T-006 | FLD | 107-EV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 106.0 | JACKET INLET TEMP. | L6608 | -30 to 170 degC | +/-2degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
FD02 | FD02-TI-007 | FD02-T-007 | PKG | 107-EV | INDICATOR - TEMPERATURE | FD02-TP1 SEAL POT | 106.0 | TP1 SEAL POT FAILURE |  |  |  | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-TE-008 | FD02-T-008 | FLD | 107-EV | ELEMENT - TEMPERATURE | FD02 NITROGEN INLET | 106.0 | NITROGEN INLET |  |  |  | SHE | By request | [14 empty] | 45
FD02 | FD02-TI-008 | FD02-T-008 | FLD | 107-EV | INDICATOR - TEMPERATURE | FD02 NITROGEN INLET | 106.0 | NITROGEN INLET |  |  |  | SHE | By request | [14 empty] | 45
FD02 | FD02-TT-008 | FD02-T-008 | FLD | 107-EV | TRANSMITTER - TEMPERATURE | FD02 NITROGEN INLET | 106.0 | NITROGEN INLET |  |  |  | SHE | By request |  |  | I.S | AI |  |  |  | C1 | ROSEMOUNT | 248H |  | TI702-SP-5058 |  |  | 45
FD02 | FD02-TE-009 | FD02-T-009 | FLD | 107-EV | ELEMENT- TEMPERATURE | FD02 BOTTOM OUTLET | 106.0 | BOTTOM OUTLET |  |  |  | REF | By request | [14 empty] | 45
FD02 | FD02-TI-009 | FD02-T-009 | FLD | 107-EV | INDICATOR - TEMPERATURE | FD02 BOTTOM OUTLET | 106.0 | BOTTOM OUTLET |  |  |  | REF | By request | [14 empty] | 45
FD02 | FD02-TT-009 | FD02-T-009 | FLD | 107-EV | TRANSMITTER - TEMPERATURE | FD02 BOTTOM OUTLET | 106.0 | BOTTOM OUTLET |  |  |  | REF | By request |  |  | I.S | AI |  |  |  | C1 | ROSEMOUNT | 248 |  | TI702-SP-5058 |  |  | 45
FD02 | FD02-YS-002 | FD02-Y-002 | PKG | 107-EV | SWITCH - POSITION | FD02-GB1 | 106.0 | GLOVEBOX OPEN |  | - | - | SIL | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-YS-003 | FD02-Y-003 | PKG | 107-EV | SWITCH - BASE OPEN | FD02 | 106.0 | BASE OPEN |  | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-YI-004 | FD02-Y-004 | PCS | 107-EV | INDICATOR - PERMISSIVE |  |  | PERMISSIVE INTERLOCK | [11 empty] | 0 | [7 empty] | 01
FD02 | FD02-YS-004 | FD02-Y-004 | PKG | 107-EV | PERMISSIVE SIGNAL | SWITCHROOM | 106.0 | PERMISSIVE INTERLOCK | 8629 | - | - |  | REQ | F |  | N.I.S | DI |  |  | 35 | C1 | [6 empty] | 01
FD02 | FD02-YI-006A | FD02-Y-006 | LCP | 107-EV | INDICATOR - LAMP | LCP ADJ TO FD02 TOP | 106.0 | AGITATOR RUNNING |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-YI-006B | FD02-Y-006 | LCP | 107-EV | INDICATOR - LAMP | LCP ADJ TO FD02-GB1 | 106.0 | AGITATOR RUNNING |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-YI-007 | FD02-Y-007 | LCP | 107-EV | INDICATOR - LAMP | LCP ADJ TO FD02 TOP | 106.0 | PANEL ACTIVE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-LI-003 | FD02-Y-011 | PKG | 107-EV | INDICATOR - LEVEL GAUGE | FD03 AGITATOR | 106.0 | TP1 SEAL POT FAILURE |  |  | - | REF | By request | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-LSH-004 | FD02-Y-011 | PKG | 107-EV | SWITCH - LEVEL - HIGH | FD02-TP1 SEAL POT | 106.0 | TP1 SEAL POT FAILURE | L15847 | Off/on | Off/on | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
FD02 | FD02-LSL-005 | FD02-Y-011 | PKG | 107-EV | SWITCH - LEVEL - LOW | FD02-TP1 SEAL POT | 106.0 | TP1 SEAL POT FAILURE | L15846 | Off/on | Off/on | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
FD02 | FD02-PI-011 | FD02-Y-011 | PKG | 107-EV | PRESSURE GAUGE | FD03 AGITATOR | 106.0 | TP1 SEAL POT FAILURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-PSL-012 | FD02-Y-011 | PKG | 107-EV | SWITCH - PRESSURE - LOW | FD02-TP1 SEAL POT | 106.0 | TP1 SEAL POT FAILURE | L15854 | On/Off | On/Off | SHE | 24 | C |  | I.S |  |  |  | 0 | [7 empty] | 01
FD02 | FD02-YA-011 | FD02-Y-011 | PCS | 107-EV | ALARM - COMMON |  |  | TP1 SEAL POT FAILURE |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
FD02 | FD02-YS-011 | FD02-Y-011 | PKG | 107-EV | SWITCH - COMMON ALARM | FD02-TP1 SEAL POT | 106.0 | TP1 SEAL POT FAILURE | 8630 | - | - | SHE | REQ | F |  | I.S | DI |  |  | 32 | C1 | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
FD02 | FD02-YI-012 | FD02-Y-012 | LCP | 107-EV | INDICATOR - LAMP | LCP ADJ TO FD02-GB1 | 106.0 | PANEL ACTIVE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD02 | FD02-YI-013 | FD02-Y-013 | LCP | 107-EV | INDICATOR - LAMP | LCP ADJ TO FD02-GB1 | 106.0 | PURGE COMPLETE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-BD-001 | FD03-B-001 | FLD | 107-CU | RUPTURE DISC | 80-P-PT1A-E-9022915 | 103.0 | BURSTING DISC | 6728 | 6.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | SSR / BAS + | KS0003/P6 | TI702-SP-5077 |  |  | 01
FD03 | FD03-YI-001 | FD03-B-001 | PCS | 107-CU | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01
FD03 | FD03-BD-002 | FD03-B-002 | FLD | 107-CU | RUPTURE DISC | 50-RV-PT1A-C-9022927 | 103.0 | RC1 BURSTING DISC | 6731 | 6.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | S-90 / BAS + | KS0003 | TI702-SP-5077 |  |  | 01
FD03 | FD03-YI-002 | FD03-B-002 | PCS | 107-CU | ALARM - RUPTURE DISC FAIL |  |  | RC1 BURSTING DISC | [11 empty] | 0 | [7 empty] | 01
FD03 | FD03-CV-002 | FD03-C-002 | FLD | 107-CU | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9022901 | 103.0 | 0.8 BAR N2 SUPPLY | 7133 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD03 | FD03-CY-002 | FD03-C-002 | FLD | 107-CU | SOLENOID VALVE | RACK MOUNTED |  | 0.8 BAR N2 SUPPLY | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD03 | FD03-ZSC-002 | FD03-C-002 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-ZSO-002 | FD03-C-002 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-003 | FD03-C-003 | FLD | 107-CU | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9022902 | 103.0 | 6 BAR N2 SUPPLY | 7155 | - | - | REF | REQ | F |  | I.S | AO |  |  | 0 | GP2 | XOMOX TUFLIN / SAMSON | R202 / 3730-2 POSITIONER | KV0007 | TI702-SP-5008 |  |  | 01
FD03 | FD03-CY-003 | FD03-C-003 | FLD | 107-CU | SOLENOID VALVE | RACK MOUNTED |  | 6 BAR N2 SUPPLY | [7 empty] | I.S | DO |  |  | 41 | GP2 | [6 empty] | 01
FD03 | FD03-ZSC-003 | FD03-C-003 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | [6 empty] | 01
FD03 | FD03-ZSO-003 | FD03-C-003 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | [6 empty] | 01
FD03 | FD03-CV-004 | FD03-C-004 | PKG | 107-CU | SOLENOID VALVE | LINE MOUNTED | 103.0 | FILTER PULSE | 8631 | - | - | REF | REQ | F |  | I.S | DO |  |  | 41 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-005 | FD03-C-005 | FLD | 107-CU | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9022917 | 103.0 | RECIRC | 7166 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD03 | FD03-CY-005 | FD03-C-005 | FLD | 107-CU | SOLENOID VALVE | RACK MOUNTED |  | RECIRC | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD03 | FD03-ZSC-005 | FD03-C-005 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RECIRC | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-ZSO-005 | FD03-C-005 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RECIRC | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-006 | FD03-C-006 | FLD | 107-CU | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-E-9022918 | 103.0 | TO VC1 | 7299 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD03 | FD03-CY-006 | FD03-C-006 | FLD | 107-CU | SOLENOID VALVE | RACK MOUNTED |  | TO VC1 | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD03 | FD03-ZSC-006 | FD03-C-006 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO VC1 | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-ZSO-006 | FD03-C-006 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO VC1 | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-008 | FD03-C-008 | FLD | 107-CU | V-BALL VALVE - CONTROL - F.C. | 40-VP-PT1A-0-9022922 | 103.0 | DRYER VACUUM | 6836 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
FD03 | FD03-CV-009 | FD03-C-009 | FLD | 107-CU | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9022922 | 036.2 | DRYER VACUUM | 7273 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD03 | FD03-CY-009 | FD03-C-009 | FLD | 107-CU | SOLENOID VALVE | RACK MOUNTED |  | DRYER VACUUM | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD03 | FD03-ZSC-009 | FD03-C-009 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DRYER VACUUM | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-ZSO-009 | FD03-C-009 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DRYER VACUUM | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-010 | FD03-C-010 | FLD | 107-CU | V-BALL VALVE - CONTROL - F.C. | 40-P-PT1A-0-9022920 | 103.0 | SCRUBBER 02 | 6816 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
FD03 | FD03-CV-011 | FD03-C-011 | FLD | 107-CU | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022920 | 008.2 | SCRUBBER 02 | 7252 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD03 | FD03-CY-011 | FD03-C-011 | FLD | 107-CU | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD03 | FD03-ZSC-011 | FD03-C-011 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-ZSO-011 | FD03-C-011 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-012 | FD03-C-012 | FLD | 107-CU | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-D-9022907 | 103.0 | COLD HTF RTN | 6772 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
FD03 | FD03-CV-014 | FD03-C-014 | FLD | 107-CU | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-E-9022916 | 103.0 | RC1 INLET | 7308 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD03 | FD03-CY-014 | FD03-C-014 | FLD | 107-CU | SOLENOID VALVE | RACK MOUNTED |  | RC1 INLET | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD03 | FD03-ZSC-014 | FD03-C-014 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RC1 INLET | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-ZSO-014 | FD03-C-014 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RC1 INLET | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-017 | FD03-C-017 | FLD | 107-CU | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-C-9022933 | 103.0 | NITROGEN TO RC1 | 6837 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
FD03 | FD03-CV-018 | FD03-C-018 | FLD | 107-CU | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9022937 | 103.0 | TP1 DISCHARGE | 7161 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD03 | FD03-CY-018 | FD03-C-018 | FLD | 107-CU | SOLENOID VALVE | RACK MOUNTED |  | TP1 DISCHARGE | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD03 | FD03-ZSC-018 | FD03-C-018 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TP1 DISCHARGE | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-ZSO-018 | FD03-C-018 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TP1 DISCHARGE | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-019 | FD03-C-019 | FLD | 107-CU | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029167 | 103.0 | HOT HTF SUPPLY | 7126 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
FD03 | FD03-CY-019 | FD03-C-019 | FLD | 107-CU | SOLENOID VALVE | RACK MOUNTED |  | HOT HTF SUPPLY | [7 empty] | I.S | DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD03 | FD03-ZSC-019 | FD03-C-019 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-ZSO-019 | FD03-C-019 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-020 | FD03-C-020 | FLD | 107-CU | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-C-9029430 | 103.0 | COLD HTF SUPPLY | 7491 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
FD03 | FD03-ZSC-020 | FD03-C-020 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-ZSO-020 | FD03-C-020 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-CV-021 | FD03-C-021 | FLD | 107-CU | SOLENOID VALVE | ADJ TO PT-002 | 103.0 | INTERLOCK | 8636 |  |  | SHE | [9 empty] | RSG | [5 empty] | 01
FD03 | FD03-DIC-001 | FD03-D-001 | PCS | 107-CU | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01
FD03 | FD03-DS-001 | FD03-D-001 | MCC | 107-CU | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
FD03 | FD03-DY-001 | FD03-D-001 | MCC | 107-CU | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | [7 empty] | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
FD03 | FD03-DYC-001 | FD03-D-001 | MCC | 107-CU | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 103.0 | JACKET PUMP | 8632 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
FD03 | FD03-DIC-002 | FD03-D-002 | PCS | 107-CU | INDICATING CONTR. - MOTOR DRIVE |  |  | TP1 TRANSFER PUMP |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
FD03 | FD03-DS-002 | FD03-D-002 | MCC | 107-CU | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
FD03 | FD03-DY-002 | FD03-D-002 | MCC | 107-CU | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP |  |  |  | SHE |  |  |  | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
FD03 | FD03-DYC-002 | FD03-D-002 | MCC | 107-CU | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 103.0 | TP1 TRANSFER PUMP | 8633 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
FD03 | FD03-FI-001 | FD03-F-001 | FLD | 107-CU | INDICATOR - FLOW | 25-N-SS1U-0-9028706 | 043.4 | N2 SUPPLY FLOW |  |  |  | REF | By request | C | [5 empty] | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
FD03 | FD03-HS-001A | FD03-H-001 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03 TOP | 103.0 | AGITATOR START |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-001B | FD03-H-001 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03-GB1 | 103.0 | AGITATOR START |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-002A | FD03-H-002 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03 TOP | 103.0 | AGITATOR STOP |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-002B | FD03-H-002 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03-GB1 | 103.0 | AGITATOR STOP |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HIC-003 | FD03-H-003 | LCP | 107-CU | INDICATING/CONTROLLER - HAND | LCP ADJ TO FD03 TOP | 103.0 | AGITATOR SPEED CONTROL |  | - | - | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-004 | FD03-H-004 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03 TOP | 103.0 | SMOOTH-RESLURRY/DISCHARGE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HV-005 | FD03-H-005 | FLD | 107-CU | HAND VALVE | 40-P-PT1A-0-9022866 | 103.0 | PROCESS INLET | 7452 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD03 | FD03-HZSC-005 | FD03-H-005 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS INLET | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-HZSO-005 | FD03-H-005 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01
FD03 | FD03-HV-006 | FD03-H-006 | FLD | 107-CU | HAND VALVE | 25-P-PT1A-0-9022903 | 103.0 | SOLVENT INLET | 7404 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD03 | FD03-HZSC-006 | FD03-H-006 | FLD | 107-CU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENT INLET | [7 empty] | I.S | DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-HZSO-006 | FD03-H-006 | FLD | 107-CU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENT INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01
FD03 | FD03-HS-007A | FD03-H-007 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03 TOP | 103.0 | AGITATOR RAISE/LOWER |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-007B | FD03-H-007 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03-GB1 | 103.0 | AGITATOR RAISE/LOWER |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HC-009 | FD03-H-009 | LCP | 107-CU | CONTROLLER - HAND | LCP ADJ TO FD03 TOP | 103.0 | AGITATOR SPEED UP/DOWN |  | - | - | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-011 | FD03-H-011 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03 TOP | 103.0 | FILTER PULSE JET ON/OFF | 8634 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
FD03 | FD03-HS-012 | FD03-H-012 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03 TOP | 103.0 | PANEL LOCAL/REMOTE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-013A | FD03-H-013 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03 TOP | 103.0 | EMERGENCY STOP |  | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-013B | FD03-H-013 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03-GB1 | 103.0 | EMERGENCY STOP |  | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-014 | FD03-H-014 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03-GB1 | 103.0 | BASE RAISE/LOWER |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-015 | FD03-H-015 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03-GB1 | 103.0 | GLOVEBOX LOCK/UNLOCK |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-016 | FD03-H-016 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03-GB1 | 103.0 | NITROGEN |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-017 | FD03-H-017 | LCP | 107-CU | SWITCH - HAND OP. | LCP ADJ TO FD03-GB1 | 103.0 | LIGHT |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-HS-018 | FD03-H-018 | FLD | 107-CU | SWITCH - HAND OP. | ADJ TO FD03-GB1 | 103.0 | LIGHT |  |  |  | REF | REQ | F | [13 empty] | 01
FD03 | FD03-LE-001 | FD03-L-001 | [9 empty] | REF | By request
FD03 | FD03-LIC-001 | FD03-L-001 | PCS | 107-CU | INDICATING CONTROLLER - LEVEL |  |  | RC1 LEVEL |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-LT-001 | FD03-L-001 | FLD | 107-CU | TRANSMITTER - LEVEL | FD03-RC1/N4/100 | 103.0 | RC1 LEVEL |  |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | ENDRESS + HAUSER | FMR245 note2/3 | KL0028/P2 | TI702-SP-5026 |  |  | 01
FD03 | FD03-LAH-002 | FD03-L-002 | PCS | 107-CU | ALARM - LEVEL - HIGH |  |  | RC1 HIGH LEVEL | L6468 | On/Off | On/Off | SHE | 24 | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-LE-002 | FD03-L-002 | FLD | 107-CU | ELEMENT - LEVEL | FD03-RC1 VENT LINE | 103.0 | RC1 HIGH LEVEL | L6468 | On/Off | On/Off | SHE | 24 | F |  | I.S |  |  |  | 0 |  | ENDRESS + HAUSER | [5 empty] | 01
FD03 | FD03-LSH-002 | FD03-L-002 | CPR | 107-CU | SWITCH - LEVEL - HIGH | FD03-RC1 VENT LINE | 103.0 | RC1 HIGH LEVEL | L6468 | On/Off | On/Off | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | GP2 | ENDRESS + HAUSER | FDL31-GYY9AC70 | KL0014 |  |  |  | 01
FD03 | FD03-PI-002B | FD03-P-002 | LCP | 107-CU | INDICATOR - PRESSURE | LCP ADJ TO FD03 TOP | 103.0 | PRESSURE | L8636 | -1 to 3 barg | +/-40 mbarg | SHE | 12 | C |  | I.S |  |  |  | 0 | [7 empty] | 01
FD03 | FD03-PIC-002 | FD03-P-002 | PCS | 107-CU | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-PSH-002 | FD03-P-002 | [6 empty] | L8636 | +30 mbarg | +/-10 mbarg | SHE | 12
FD03 | FD03-PSL-002 | FD03-P-002 | [6 empty] | L8636 | -30 mbarg | +/-10 mbarg | SHE | 12
FD03 | FD03-PT-002 | FD03-P-002 | FLD | 107-CU | TRANSMITTER - PRESSURE | CONTROL PANEL | 103.0 | PRESSURE | L8636 | -1 to 3 barg | +/-40 mbarg | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 3051S ULTRA | KP001/P2 | TI702-SP-5141 |  |  | 01
FD03 | FD03-PDI-003 | FD03-P-003 | PCS | 107-CU | INDICATING CONTROLLER - PRESSURE |  |  | FILTER DIFF PRESSURE |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-PDT-003 | FD03-P-003 | PKG | 107-CU | TRANSMITTER - PRESSURE - DIFF | FD03 | 103.0 | FILTER DIFF PRESSURE |  |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 3051T |  | TI702-SP-5046 |  |  | 01
FD03 | FD03-PIC-004 | FD03-P-004 | PCS | 107-CU | INDICATING CONTROLLER - PRESSURE |  |  | VC1 INLET PRESSURE | [11 empty] | 0 | [7 empty] | 01
FD03 | FD03-PIT-004 | FD03-P-004 | FLD | 107-CU | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-E-9022918 | 103.0 | VC1 INLET PRESSURE | 6677 | -1 to 3 barg | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
FD03 | FD03-PT-004 | FD03-P-004 | [9 empty] | REF | By request
FD03 | FD03-PI-005 | FD03-P-005 | FLD | 107-CU | PRESSURE GAUGE - DIAPHRAGM | 40-HT-CS3A-C-9029430 | 103.0 | JP1 SUCTION PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
FD03 | FD03-PI-006 | FD03-P-006 | FLD | 107-CU | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9022939 | 103.0 | JP1 DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
FD03 | FD03-PI-007 | FD03-P-007 | FLD | 107-CU | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-0-9022933 | 103.0 | N2 TO RC1 PRESSURE |  | -1 to 1.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
FD03 | FD03-PI-008 | FD03-P-008 | FLD | 107-CU | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-0-9022937 | 103.0 | TP1 DISCHARGE PRESSURE |  | 0 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note3) | KP0006/1 |  |  |  | 01
FD03 | FD03-PSV-009 | FD03-P-009 | FLD | 107-CU | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9022940 | 103.0 | JACKET HTF RELIEF |  | 10 barg | +/- 10% |  | 24 | C | [5 empty] | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
FD03 | FD03-PSV-010 | FD03-P-010 | FLD | 107-CU | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022941 | 103.0 | VC1 HTF RELIEF |  | 10 barg | +/- 10% |  | 24 | C | [5 empty] | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
FD03 | FD03-PSL-011 | FD03-P-011 | PKG | 107-CU | SWITCH - PRESSURE - LOW | DELETED | 103.0 | DELETED |  | set @ -30 mbar | +/- 1% |  | 12 | C | [5 empty] | 0 | [5 empty] | DELETED |  | 01
FD03 | FD03-PSH-012 | FD03-P-012 | PKG | 107-CU | SWITCH - PRESSURE - HIGH | DELETED | 103.0 | DELETED |  | set @ 30 mbar | +/- 1% |  | 12 | C | [5 empty] | 0 | [5 empty] | DELETED |  | 01
FD03 | FD03-PI-013 | FD03-P-013 | DEL | 107-CU | PRESSURE GAUGE | DELETED |  | DELETED |  |  |  |  | REQ | C | [5 empty] | 0 | [5 empty] | DELETED |  | 01
FD03 | FD03-PRV-016 | FD03-P-016 | FLD | 107-CU | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028707 | 103.0 | N2 SUPPLY |  | set @ 2.0 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
FD03 | FD03-PI-018 | FD03-P-018 | LCP | 107-CU | PRESSURE GAUGE | LCP ADJ TO FD03-GB1 | 103.0 | GLOVEBOX PRESSURE |  | 0.05 to 0.5 kpA | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-PI-019 | FD03-P-019 | LCP | 107-CU | PRESSURE GAUGE | LCP ADJ TO FD03-GB1 | 103.0 | EXTRACT FILTER CONDITION |  | 0 to 1 kpA | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-PI-020 | FD03-P-020 | PKG | 107-CU | PRESSURE GAUGE | 15-N-SS1U-0-9022943 | 103.0 | AGITATOR SEAL PRESSURE |  | 0 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-PI-021 | FD03-P-021 | LCP | 107-CU | PRESSURE GAUGE | LCP ADJ TO FD03-GB1 | 103.0 | NITROGEN PRESSURE |  | 0 to 1.6 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-PI-022 | FD03-P-022 | PKG | 107-CU | PRESSURE GAUGE | SEAL LUBRICATOR | 103.0 | AGI SEAL LUBRICATOR PRESSURE |  | 0 to 6 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-SI-001 | FD03-S-001 | PCS | 107-CU | INDICATOR - SPEED |  |  | AGITATOR |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-SIC-001 | FD03-S-001 | PKG | 107-CU | AC INVERTER DRIVE | SWITCHROOM | 103.0 | AGITATOR |  |  |  | SHE | By request | F |  | N.I.S | AI |  |  | 13 | GP2 |  |  |  |  | MIN SPEED 4 rpm |  | 01
FD03 | FD03-TE-002 | FD03-T-002 | FLD | 107-CU | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9022920 |  | VC1 VENT TEMPERATURE |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-TI-002 | FD03-T-002 | PCS | 107-CU | INDICATOR - TEMPERATURE |  |  | VC1 VENT TEMPERATURE |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-TT-002 | FD03-T-002 | FLD | 107-CU | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 103.0 | VC1 VENT TEMPERATURE |  |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
FD03 | FD03-TE-003 | FD03-T-003 | FLD | 107-CU | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9022923 |  | VC1 HTF RTN TEMP. |  |  |  | REF | By request | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-TI-003 | FD03-T-003 | PCS | 107-CU | INDICATOR - TEMPERATURE |  |  | VC1 HTF RTN TEMP. | [11 empty] | 0 | [7 empty] | 01
FD03 | FD03-TT-003 | FD03-T-003 | FLD | 107-CU | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 103.0 | VC1 HTF RTN TEMP. |  |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
FD03 | FD03-TI-004 | FD03-T-004 | FLD | 107-CU | INDICATOR - TEMPERATURE | 80-HT-CS3A-D-9022940 | 103.0 | JACKET HTF RTN TEMPERATURE |  |  |  | REF | By request | C | [5 empty] | 0 |  | WIKA | S5550/4 | KT0003 |  |  |  | 01
FD03 | FD03-TE-005 | FD03-T-005 | PKG | 107-CU | ELEMENT - TEMPERATURE - RTD | FD03/T1/40 |  | TEMPERATURE |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-TI-005A | FD03-T-005 | PCS | 107-CU | INDICATOR - TEMPERATURE |  |  | TEMPERATURE |  |  |  | SHE | By request | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-TI-005B | FD03-T-005 | LCP | 107-CU | INDICATOR - TEMPERATURE | LCP ADJ TO FD03 TOP | 103.0 | TEMPERATURE |  |  |  | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA |  |  | TI702-SP-5078 |  |  | 01
FD03 | FD03-TT-005 | FD03-T-005 | PKG | 107-CU | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 103.0 | TEMPERATURE |  |  |  | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 244E |  | TI702-SP-5078 |  |  | 01
FD03 | FD03-TE-006 | FD03-T-006 | FLD | 107-CU | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022939 |  | JACKET INLET TEMP. | L6611 | -30 to 170 degC | +/-2 degC | GxP | 12 | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-TIC-006 | FD03-T-006 | PCS | 107-CU | INDICATING CONTROLLER - TEMPERATURE |  |  | JACKET INLET TEMP. | L6611 | -30 to 170 degC | +/-2degC | GxP | 12 | [6 empty] | 0 | [7 empty] | 01
FD03 | FD03-TT-006 | FD03-T-006 | FLD | 107-CU | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 103.0 | JACKET INLET TEMP. | L6611 | -30 to 170 degC | +/-2 degC | GxP | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
FD03 | FD03-UY-002 | FD03-U-002 | [6 empty] | L8636 | -30 to 30 barg | +/-10mbarg |  | -
FD03 | FD03-YS-002 | FD03-Y-002 | PKG | 107-CU | SWITCH - POSITION | FD03-GB1 | 103.0 | GLOVE BOX OPEN |  | - | - | SIL | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-YS-003 | FD03-Y-003 | PKG | 107-CU | SWITCH - MANWAY OPEN | FD03 - BOTTOM PLATE OPEN | 103.0 | BASE OPEN |  | - | - | SHE | REQ | F | [5 empty] | 0 |  | VENDOR SUPPLY | [5 empty] | 01
FD03 | FD03-YI-004 | FD03-Y-004 | PCS | 107-CU | INDICATOR - PERMISSIVE |  |  | PERMISSIVE INTERLOCK | [11 empty] | 0 | [7 empty] | 01
FD03 | FD03-YS-004 | FD03-Y-004 | PKG | 107-CU | PERMISSIVE SIGNAL | SWITCHROOM | 103.0 | PERMISSIVE INTERLOCK | 8639 | - | - |  | REQ | F |  | N.I.S | DI |  |  | 35 | GP2 | [6 empty] | 01
FD03 | FD03-YI-006A | FD03-Y-006 | LCP | 107-CU | INDICATOR - LAMP | LCP ADJ TO FD03 TOP | 103.0 | AGITATOR RUNNING |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-YI-006B | FD03-Y-006 | LCP | 107-CU | INDICATOR - LAMP | LCP ADJ TO FD03-GB1 | 103.0 | AGITATOR RUNNING |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-YI-007 | FD03-Y-007 | LCP | 107-CU | INDICATOR - LAMP | LCP ADJ TO FD03 TOP | 103.0 | PANEL ACTIVE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-LI-003 | FD03-Y-011 | PKG | 107-CU | INDICATOR - LEVEL GAUGE | FD03-TP1 SEAL POT | 103.0 | TP1 SEAL PT FAILURE |  |  | - | REF | By request | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-LSH-004 | FD03-Y-011 | PKG | 107-CU | SWITCH - LEVEL - HIGH | FD03-TP1 SEAL POT | 103.0 | TP1 SEAL PT FAILURE | L15852 | Off/on | Off/on | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
FD03 | FD03-LSL-005 | FD03-Y-011 | PKG | 107-CU | SWITCH - LEVEL - LOW | FD03-TP1 SEAL POT | 103.0 | TP1 SEAL PT FAILURE | L15053 | Off/on | Off/on | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
FD03 | FD03-PI-014 | FD03-Y-011 | PKG | 107-CU | PRESSURE GAUGE | FD03-TP1 SEAL POT | 103.0 | TP1 SEAL PT FAILURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-PSL-015 | FD03-Y-011 | PKG | 107-CU | SWITCH - PRESSURE - LOW | FD03-TP1 SEAL POT | 103.0 | TP1 SEAL PT FAILURE | L15855 | On/Off | On/Off | SHE | 24 | C |  | I.S |  |  |  | 0 | [7 empty] | 01
FD03 | FD03-TI-007 | FD03-Y-011 | PKG | 107-CU | INDICATOR - TEMPERATURE | FD03-TP1 SEAL POT | 103.0 | TP1 SEAL PT FAILURE |  |  |  | REF | By request | C | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-YA-011 | FD03-Y-011 | PCS | 107-CU | ALARM - COMMON |  |  | TP1 SEAL PT FAILURE |  |  |  | SHE | [7 empty] | 0 | [7 empty] | 01
FD03 | FD03-YS-011 | FD03-Y-011 | PKG | 107-CU | SWITCH - COMMON ALARM | FD03-TP1 SEAL POT | 103.0 | TP1 SEAL PT FAILURE | 8640 | - | - | SHE | REQ | F |  | I.S | DI |  |  | 32 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD03 | FD03-YI-012 | FD03-Y-012 | LCP | 107-CU | INDICATOR - LAMP | LCP ADJ TO FD03-GB1 | 103.0 | PANEL ACTIVE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD03 | FD03-YI-013 | FD03-Y-013 | LCP | 107-CU | INDICATOR - LAMP | LCP ADJ TO FD03-GB1 | 103.0 | PURGE COMPLETE |  | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
FD04 | FD04-BD-001 | FD04-B-001 | FLD | 107-CV | RUPTURE DISC | 40-P-PT1A-C-9025543 | 167.0 | RC1 BURSTING DISC | 13172 | 6.0 barg | - | N/A | - | - | - | I.S | DI | 1 |  | 32 | GP2 | BS&B | SPR-7 / BAS + | KS0003/P4 | TI702-SP-5077 |  |  | 01
FD04 | FD04-YI-001 | FD04-B-001 | PCS | 107-CV | ALARM - RUPTURE DISC FAIL |  |  | RC1 BURSTING DISC |  |  |  | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-BD-002 | FD04-B-002 | FLD | 107-CV | RUPTURE DISC | 50-RV-CS1A-0-9026735 | 167.0 | PROCESS RELIEF | 13173 | 1.0 barg | - | N/A | - | - | - | I.S | DI | 1 |  | 32 | GP2 | BS&B | SPR-7 / BAS + | KS0003/P4 | TI702-SP-5077 |  |  | 01
FD04 | FD04-YI-002 | FD04-B-002 | LCP | 107-CV | ALARM - RUPTURE DISC FAIL |  | 167.0 | FD04BURSTING DISC |  |  |  | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-BD-011 | FD04-B-011 | PKG | 107-CV | RUPTURE DISC | FD04 | 167.0 | FD04 BURSTING DISC |  | 5.5 barg | - | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-YI-011 | FD04-B-011 | PKG | 107-CV | ALARM - RUPTURE DISC FAIL | LCP ADJ TO FD04 | 167.0 | BURSTING DISC |  |  |  | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-CV-002 | FD04-C-002 | PKG | 107-CV | BALL VALVE - ON/OFF - F.C. | ???? | 167.0 | 0.8 BAR N2 SUPPLY |  | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD04 | FD04-CY-002 | FD04-C-002 | PKG | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | 0.8 BAR N2 SUPPLY | 13174 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
FD04 | FD04-ZSC-002 | FD04-C-002 | PKG | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | 0.8 BAR N2 SUPPLY | 13174 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | WESTLOCK CONTROLS | 3045 |  | TI702-SP-5000 |  |  | 01
FD04 | FD04-ZSO-002 | FD04-C-002 | PKG | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | 0.8 BAR N2 SUPPLY | 13174 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | WESTLOCK CONTROLS | 3045 |  | TI702-SP-5000 |  |  | 01
FD04 | FD04-CV-003 | FD04-C-003 | PKG | 107-CV | BALL VALVE - ON/OFF - F.C. | ???? | 167.0 | 2 BAR N2 SUPPLY |  | - | - | N/A | - | - | - | I.S | AO |  |  |  | GP2 | XOMOX TUFLIN / SAMSON | R202 / 3730-2 POSITIONER | KV0007 | TI702-SP-5008 |  |  | 01
FD04 | FD04-CY-003 | FD04-C-003 | PKG | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | 2 BAR N2 SUPPLY | 13175 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | [6 empty] | 01
FD04 | FD04-ZSC-003 | FD04-C-003 | PKG | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | 2 BAR N2 SUPPLY | 13175 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
FD04 | FD04-ZSO-003 | FD04-C-003 | PKG | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | 2 BAR N2 SUPPLY | 13175 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
FD04 | FD04-CV-004 | FD04-C-004 | PKG | 107-CV | SOLENOID VALVE | FD04 | 167.0 | FILTER PULSE |  | - | - | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-CV-005 | FD04-C-005 | PKG | 107-CV | BALL VALVE - ON/OFF - F.C. | 25-P-HS??-E-9025034 | 167.0 | RECIRC |  | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD04 | FD04-CY-005 | FD04-C-005 | PKG | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | RECIRC | 13176 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
FD04 | FD04-ZSC-005 | FD04-C-005 | PKG | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | RECIRC | 13176 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | WESTLOCK CONTROLS | 3045 |  | TI702-SP-5000 |  |  | 01
FD04 | FD04-ZSO-005 | FD04-C-005 | PKG | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | RECIRC | 13176 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | WESTLOCK CONTROLS | 3045 |  | TI702-SP-5000 |  |  | 01
FD04 | FD04-CV-006 | FD04-C-006 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-H-9025539 | 167.0 | TO VC1 | 13177 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-006 | FD04-C-006 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | TO VC1 | 13177 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-006 | FD04-C-006 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | TO VC1 | 13177 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-006 | FD04-C-006 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | TO VC1 | 13177 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-008 | FD04-C-008 | FLD | 107-CV | V-BALL VALVE - CONTROL - F.C. | 40-VP-PT1A-0-9025511 | 167.0 | DRYER VACUUM | 13178 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | GP2 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004/P1 | TI702-SP-5090 |  |  | 01
FD04 | FD04-CV-009 | FD04-C-009 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9025511 | 167.0 | DRYER VACUUM | 13179 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-009 | FD04-C-009 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | DRYER VACUUM | 13179 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-009 | FD04-C-009 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | DRYER VACUUM | 13179 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-009 | FD04-C-009 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | DRYER VACUUM | 13179 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-010 | FD04-C-010 | FLD | 107-CV | V-BALL VALVE - CONTROL - F.C. | 40-P-PT1A-0-9025510 | 167.0 | DRYER SCRUBBER | 13180 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | GP2 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004/P1 | TI702-SP-5090 |  |  | 01
FD04 | FD04-CV-011 | FD04-C-011 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9025510 | 167.0 | SCRUBBER 02 | 13181 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-011 | FD04-C-011 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | SCRUBBER 02 | 13181 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-011 | FD04-C-011 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | SCRUBBER 02 | 13181 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-011 | FD04-C-011 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | SCRUBBER 02 | 13181 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-014 | FD04-C-014 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-H-9025548 | 167.0 | RC1 INLET | 13182 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-014 | FD04-C-014 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | RC1 INLET | 13182 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-014 | FD04-C-014 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | RC1 INLET | 13182 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-014 | FD04-C-014 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | RC1 INLET | 13182 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-017 | FD04-C-017 | FLD | 107-CV | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-C-9025544 | 167.0 | NITROGEN TO RC1 | 13183 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004/P1 | TI702-SP-5008 |  |  | 01
FD04 | FD04-CV-018 | FD04-C-018 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-C-9025546 | 167.0 | TP1 DISCHARGE | 13184 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-018 | FD04-C-018 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | TP1 DISCHARGE | 13184 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-018 | FD04-C-018 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | TP1 DISCHARGE | 13184 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-018 | FD04-C-018 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | TP1 DISCHARGE | 13184 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-021 | FD04-C-021 | FLD | 107-CV | V-BALL VALVE - CONTROL - F.C. | 50-SV-GR1A-0-9026208 | 167.0 | GLOVEBOX TO LEV | 13185 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | GP2 | HABONIM / MOORE | 31 SERIES V-FLOW / 760EA15EAAGNNB8 POSITIONER | KV0004/P1 | TI702-SP-5090 |  |  | 01
FD04 | FD04-CV-022 | FD04-C-022 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 50-SV-GR1A-0-9026208 | 167.0 | ACID SCRUBBER | 13186 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-022 | FD04-C-022 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | ACID SCRUBBER | 13186 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-022 | FD04-C-022 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | ACID SCRUBBER | 13186 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-022 | FD04-C-022 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | ACID SCRUBBER | 13186 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-023 | FD04-C-023 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-C-9025541 | 167.0 | DUST FILTER | 13187 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-023 | FD04-C-023 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | DUST FILTER | 13187 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-023 | FD04-C-023 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | DUST FILTER | 13187 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-023 | FD04-C-023 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | DUST FILTER | 13187 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-024 | FD04-C-024 | FLD | 107-CV | BALL VALVE - ON/OFF - F.O. | 25-P-PT1A-C-9025542 | 167.0 | CONDENSATE TO RC1 | 13188 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-024 | FD04-C-024 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | CONDENSATE TO RC1 | 13188 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-024 | FD04-C-024 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | CONDENSATE TO RC1 | 13188 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-024 | FD04-C-024 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | CONDENSATE TO RC1 | 13188 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-025 | FD04-C-025 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9025546 | 167.0 | RC1 RECYCLE | 13189 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-025 | FD04-C-025 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | RC1 RECYCLE | 13189 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-025 | FD04-C-025 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | RC1 RECYCLE | 13189 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-025 | FD04-C-025 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | RC1 RECYCLE | 13189 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-026 | FD04-C-026 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022828 | 167.0 | PROCESS INLET | 13191 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-026 | FD04-C-026 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | PROCESS INLET | 13190 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-026 | FD04-C-026 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | PROCESS INLET | 13190 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-026 | FD04-C-026 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | PROCESS INLET | 13190 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-027 | FD04-C-027 | FLD | 107-CV | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-902???? | 167.0 | SOLVENT INLET | 13192 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
FD04 | FD04-CY-027 | FD04-C-027 | FLD | 107-CV | SOLENOID VALVE | RACK MOUNTED | 167.0 | SOLVENT INLET | 13191 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
FD04 | FD04-ZSC-027 | FD04-C-027 | FLD | 107-CV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 167.0 | SOLVENT INLET | 13191 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-ZSO-027 | FD04-C-027 | FLD | 107-CV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 167.0 | SOLVENT INLET | 13191 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
FD04 | FD04-CV-028 | FD04-C-028 | PKG | 107-CV | BALL VALVE - ON/OFF - F.C. | ???? | 167.0 |  |  | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
FD04 | FD04-CV-029 | FD04-C-029 | PKG | 107-CV | SOLENOID VALVE | FD04 | 167.0 | MECHANICAL SEAL PURGE |  | - | - | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-CV-031 | FD04-C-031 | PKG | 107-CV | V-BALL VALVE - CONTROL - F.C. |  | 167.0 | HEAT/COOL PACKAGE |  | N/A: SHE; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-DIC-002 | FD04-D-002 | PCS | 107-CV | INDICATING CONTR. - MOTOR DRIVE |  |  | TP1 TRANSFER PUMP |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-DS-002 | FD04-D-002 | MCC | 107-CV | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13192 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | GP2 | [6 empty] | 01
FD04 | FD04-DY-002 | FD04-D-002 | MCC | 107-CV | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13192 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | GP2 | [6 empty] | 01
FD04 | FD04-DYC-002 | FD04-D-002 | MCC | 107-CV | DRIVE - START/STOP | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13192 | - | - | REF | REQ | F | Ref | N.I.S | DO | 1 |  | 42 | GP2 | [6 empty] | 01
FD04 | FD04-DY-003 | FD04-D-003 | PKG | 107-HG | PACKAGE RUNNING |  | 167.0 | HEAT/COOL PACKAGE | 13193 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | [7 empty] | 01
FD04 | FD04-DYC-003 | FD04-D-003 | PKG | 107-HG | PACKAGE - START/STOP |  | 167.0 | HEAT/COOL PACKAGE | 13193 |  |  | N/A | - | - | - | N.I.S | DO | 1 |  | 42 | GP2 | [6 empty] | 01
FD04 | FD04-FI-001 | FD04-F-001 | PKG | 107-CV | INDICATOR - FLOW |  | 167.0 | N2 SUPPLY FLOW |  | N/A: REF; -: REQ; -: C; -: Ref | [10 empty] | 01
FD04 | FD04-FI-002 | FD04-F-002 | PKG | 107-CV | INDICATOR - FLOW |  | 167.0 | MECHANICAL SEAL PURGE |  | N/A: REF; -: REQ; -: C; -: Ref | [10 empty] | 01
FD04 | FD04-FAH-003 | FD04-F-003 | LCP | 107-CV | ALARM - HIGH FLOW | LCP ADJ TO FD04 | 167.0 | MECHANICAL SEAL PURGE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-FSH-003 | FD04-F-003 | PKG | 107-CV | SWITCH - FLOW - HIGH |  | 167.0 | MECHANICAL SEAL PURGE |  | N/A: REF; -: REQ; -: C; -: Ops | [10 empty] | 01
FD04 | FD04-FS-011 | FD04-F-011 | PKG | 107-CV | FLOW SWITCH |  | 167.0 | HEAT/COOL PACKAGE |  | N/A: REF; -: REQ; -: C; -: Ops | [10 empty] | 01
FD04 | FD04-HS-001A | FD04-H-001 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-TOP | 167.0 | AGITATOR START |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-001B | FD04-H-001 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | AGITATOR START |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-002A | FD04-H-002 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-TOP | 167.0 | AGITATOR STOP |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-002B | FD04-H-002 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | AGITATOR STOP |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-007A | FD04-H-007 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-TOP | 167.0 | AGITATOR RAISE/LOWER |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-007B | FD04-H-007 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | AGITATOR RAISE/LOWER |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-011 | FD04-H-011 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04 | 167.0 | FILTER PULSE JET ON/OFF |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-012A | FD04-H-012 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-TOP | 167.0 | AGITATOR SPEED UP/DOWN |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-012B | FD04-H-012 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04 | 167.0 | AGITATOR SPEED UP/DOWN |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-013A | FD04-H-013 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-TOP | 167.0 | EMERGENCY STOP |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
FD04 | FD04-HS-013B | FD04-H-013 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | EMERGENCY STOP |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
FD04 | FD04-HS-014 | FD04-H-014 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04 | 167.0 | BASE RAISE/LOWER |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-015 | FD04-H-015 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | GLOVEBOX LOCK/UNLOCK |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-016 | FD04-H-016 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | NITROGEN |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-017A | FD04-H-017A | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04 | 167.0 | LIGHT |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-017B | FD04-H-017B | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | LIGHT |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-019 | FD04-H-019 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04 | 167.0 | MECHANICAL SEAL PURGE |  | N/A: REF; -: REQ; -: F; -: Ref | [10 empty] | 01
FD04 | FD04-HS-020 | FD04-H-020 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | AGITATOR DIRECTION |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-021 | FD04-H-021 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | SYSTEM RESET |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-HS-022 | FD04-H-022 | LCP | 107-CV | SWITCH - HAND OP. | LCP ADJ TO FD04-GB1 | 167.0 | AGITATOR AUTO RAISE/LOWE ON/OFF |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
FD04 | FD04-LI-001B | FD04-L-001 | FLD | 107-CV | INDICATOR - LEVEL | GP2 | 167.0 | RC1 LEVEL |  | 0 to 300 l | +/- 1% | REF | 12 | C | Ops | I.S |  |  |  |  | GP2 | BEKA | BA324D | KX0017/P1 | TI702-SP-5122 |  |  | 01
FD04 | FD04-LIC-001 | FD04-L-001 | PCS | 107-CV | INDICATING CONTROLLER - LEVEL |  |  | RC1 LEVEL |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-LT-001 | FD04-L-001 | FLD | 107-CV | TRANSMITTER - LEVEL | FD04-RC1/N4/100 | 167.0 | RC1 LEVEL | 13194 | 0 to 300 l | +/- 4% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | GP2 | ENDRESS + HAUSER | FMR245-24APKAA2A | KL0028/P2 | TI702-SP-5122 |  |  | 01
FD04 | FD04-LAH-002 | FD04-L-002 | PCS | 107-CV | ALARM - LEVEL - HIGH |  |  | RC1 HIGH LEVEL |  | N/A: SHE; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-LSH-002 | FD04-L-002 | FLD | 107-CV | SWITCH - LEVEL - HIGH | FD04-RCV-N7/8O | 167.0 | RC1 HIGH LEVEL | 13195 | - | - | SHE | 12 | C | Ops | I.S | DI | 1 |  | 32 | GP2 | ENDRESS + HAUSER | FLT51 C 4ALKBK8G4AA | KL0014/P2 | TI702-SP-5036 |  |  | 01
FD04 | FD04-PI-002B | FD04-P-002 | LCP | 107-CV | INDICATOR - PRESSURE | LCP ADJ TO FD04 | 167.0 | PRESSURE |  | -1 to 6 barg | +/- 1% |  | 12 | C | SHE | [12 empty] | 01
FD04 | FD04-PIC-002A | FD04-P-002 | PCS | 107-CV | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-PSHL-002 | FD04-P-002 | PKG | 107-CV | SWITCH - PRESSURE - HIGH/LOW | FD04/P1/80 | 167.0 | HIGH / LOW PRESSURE |  | set @ +/-30 mbar | +/- 1% | SHE | 12 | C | SHE | [12 empty] | 01
FD04 | FD04-PT-002 | FD04-P-002 | PKG | 107-CV | TRANSMITTER - PRESSURE - DIAPHRAGM | FD04/P1/80 | 167.0 | PRESSURE | 13196 | -1 to 6 barg | 0.3% | GxP | 12 | C | SHE | I.S | AI | 1 |  | 11 | GP2 | ROSEMOUNT | 3051 |  | TI702-SP-5164 |  |  | 01
FD04 | FD04-PDI-003 | FD04-P-003 | PCS | 107-CV | INDICATOR - PRESSURE - DIFF |  |  | FILTER DIFF PRESSURE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-PDT-003 | FD04-P-003 | PKG | 107-CV | TRANSMITTER - PRESSURE - DIFF | ACROSS FILTER | 167.0 | FILTER DIFF PRESSURE | 13197 | 0 to 1 bar | +/- 2% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | GP2 | ROSEMOUNT | 3051 |  | TI702-SP-5164 |  |  | 01
FD04 | FD04-PIC-004 | FD04-P-004 | PCS | 107-CV | INDICATING CONTROLLER - PRESSURE |  | 167.0 | VC1 INLET PRESSURE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-PT-004 | FD04-P-004 | FLD | 107-CV | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-H-9025539 | 167.0 | VC1 INLET PRESSURE | 13198 | -1 to 3 barg | +/- 1% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | GP2 | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 01
FD04 | FD04-PI-007 | FD04-P-007 | FLD | 107-CV | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-C-9025544 | 167.0 | RC1 PRESSURE |  | -1 to 3 barg | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100/990.27 | KP0006/P6 SHT2 |  |  |  | 01
FD04 | FD04-PI-008 | FD04-P-008 | FLD | 107-CV | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-0-9025546 | 167.0 | TP1 DISCHARGE PRESSURE |  | 0 to 4 barg | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | 233.50.100/990.27 | KP0006/P6 SHT2 |  |  |  | 01
FD04 | FD04-PSV-010 | FD04-P-010 | PKG | 107-CV | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9025512 | 167.0 | VC1 HTF RELIEF |  | 10 barg | +/- 10% | N/A | - | - | - | [6 empty] | BROADY | 2531D-C-B000 | KS0001/P |  |  |  | 01
FD04 | FD04-PRV-016 | FD04-P-016 | PKG | 107-CV | CONTROL VALVE SELF ACTUATING |  | 167.0 | N2 SUPPLY |  | set @ 2 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
FD04 | FD04-PRV-017 | FD04-P-017 | PKG | 107-CV | CONTROL VALVE SELF ACTUATING |  | 167.0 | N2 SUPPLY |  | set @ 0.8 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
FD04 | FD04-PI-018 | FD04-P-018 | LCP | 107-CV | PRESSURE GAUGE | LCP ADJ TO FD04-GB1 | 167.0 | GLOVEBOX PRESSURE |  | 0.05 TO 0.5 kpA | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
FD04 | FD04-PI-019 | FD04-P-019 | LCP | 107-CV | PRESSURE GAUGE | LCP ADJ TO FD04-GB1 | 167.0 | EXTRACT FILTER CONDITION |  | 0 to 125 pA | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
FD04 | FD04-PI-020 | FD04-P-020 | PKG | 107-CV | PRESSURE GAUGE |  | 167.0 | AGITATOR SEAL PRESSURE |  | 0 to 6 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
FD04 | FD04-PDI-021 | FD04-P-021 | LCP | 107-CV | INDICATOR - PRESSURE - DIFF | LCP ADJ TO FD04-GB1 | 167.0 | NITROGEN FLOW |  | 0 to 1.6 barg | +/- 5% | GxP | 12 | C | SHE | [12 empty] | 01
FD04 | FD04-PAL-022 | FD04-P-022 | LCP | 107-CV | ALARM - PRESSURE - LOW | LCP ADJ TO FD04 | 167.0 |  |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-PSL-022 | FD04-P-022 | PKG | 107-CV | SWITCH - PRESSURE - LOW | SEAL | 167.0 | AGI SEAL PRESSURE |  | set @??? | +/- 5% | REF | REQ | C | Ops | [12 empty] | 01
FD04 | FD04-PSH-023 | FD04-P-023 | PKG | 107-CV | SWITCH - PRESSURE - HIGH | LCP ADJ TO FD04-GB1 | 167.0 | GLOVEBOX PRESSURE HIGH |  | set @-50pa |  | SHE | 12 | C | SHE | [12 empty] | 01
FD04 | FD04-PRV-024 | FD04-P-024 | PKG | 107-CV | CONTROL VALVE SELF ACTUATING |  | 167.0 | GLOVEBOX PURGE |  | set @ 0.9 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
FD04 | FD04-PRV-025 | FD04-P-025 | PKG | 107-CV | CONTROL VALVE SELF ACTUATING |  | 167.0 | MECHANICAL SEAL PURGE |  | set @ 4.5 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
FD04 | FD04-PDSL-026 | FD04-P-026 | PKG | 107-CV | SWITCH -PRESSURE - DIFF LOW |  | 167.0 |  |  | set @??? |  | SHE | 12 | C | SHE | [12 empty] | 01
FD04 | FD04-PAH-027 | FD04-P-027 | PCS | 107-CV | ALARM - PRESSURE - HIGH |  |  |  |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-PSH-027 | FD04-P-027 | FLD | 107-CV | SWITCH - PRESSURE - HIGH | 50-RV-CS1A-0-9026735 | 167.0 | PROCESS ALARM | 13199 | set@ 0.75 barg |  | REF | REQ | C | Ops | I.S | DI | 1 |  | 32 | GP2 | DELTA CONTROLS LTD | W28102G522C20 | KP0012/P | TI702-SP-5085 |  |  | 01
FD04 | FD04-PSV-030 | FD04-P-030 | PKG | 107-HG | PRESSURE RELIEF VALVE |  | 167.0 | HEAT/COOL PACKAGE |  | set @ 4 barg |  | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-PSH-031 | FD04-P-031 | PKG | 107-HG | SWITCH - PRESSURE - HIGH |  | 167.0 | HEAT/COOL PACKAGE |  | N/A: REF; -: REQ; -: C; -: Ops | [10 empty] | 01
FD04 | FD04-PI-032 | FD04-P-032 | PKG | 107-HG | PRESSURE GAUGE |  | 167.0 | HEAT/COOL PACKAGE |  | N/A: REF; -: REQ; -: C; -: Ref | [10 empty] | 01
FD04 | FD04-PIC-033 | FD04-P-033 | PCS | 107-CV | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE |  | N/A: SHE; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-PT-033 | FD04-P-033 | PKG | 107-CV | TRANSMITTER - PRESSURE | FD04 GLOVEBOX | 167.0 | PRESSURE | 13200 | -50 to 50 Pa |  | SHE | 12 | C | SHE | I.S | AI | 1 |  | 11 | GP2 | ROSEMOUNT | 3051 |  | TI702-SP-5164 |  |  | 01
FD04 | FD04-RO-001 | FD04-R-001 | PKG | 107-CV | RESTRICTION ORIFICE |  | 167.0 | GLOVEBOX PURGE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-RO-002 | FD04-R-002 | FLD | 107-CV | RESTRICTION ORIFICE | 25-P-PT1A-0-9025546 | 167.0 | TP1 DISCHARGE |  | 5mm |  | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-SI-001A | FD04-S-001 | PCS | 107-CV | INDICATOR - SPEED |  |  | AGITATOR |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-SI-001B | FD04-S-001 | LCP | 107-CV | INDICATOR - SPEED | LCP ADJ TO FD04 | 167.0 | AGITATOR |  | N/A: REF; -: REQ; -: C; -: Ref | [10 empty] | 01
FD04 | FD04-SIC-001 | FD04-S-001 | PKG | 107-CV | AC INVERTER DRIVE | SWITCHROOM | 167.0 | AGITATOR | 13201 | 0-24 rpm | +/- 2.5% | SHE | REQ | F | Ref | I.S | AI | 1 |  | 13 | GP2 |  |  |  | KFD0-CC-EX1 | CANNOT CERTIFY TWO BARRIERS |  | 01
FD04 | FD04-TE-002 | FD04-T-002 | FLD | 107-CV | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9025540 | 167.0 | VC1 VENT TEMPERATURE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-TI-002 | FD04-T-002 | PCS | 107-CV | INDICATOR - TEMPERATURE |  |  | VC1 VENT TEMPERATURE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-TT-002 | FD04-T-002 | FLD | 107-CV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 167.0 | VC1 VENT TEMPERATURE | 13202 | -20 to 80 degC | +/- 1% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | GP2 | ROSEMOUNT | 644H | KT0004/P2SHT2 | TI702-SP-5012 |  |  | 01
FD04 | FD04-TE-003 | FD04-T-003 | FLD | 107-CV | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9025512 | 167.0 | VC1 HTF RTN TEMP |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-TI-003 | FD04-T-003 | PCS | 107-CV | INDICATOR - TEMPERATURE |  |  | VC1 HTF RTN TEMP |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-TT-003 | FD04-T-003 | FLD | 107-CV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 167.0 | VC1 HTF RTN TEMP | 13203 | -30 to 70 degC | +/- 1% | REF | REQ | C | Ref | I.S | AI | 1 |  | 11 | GP2 | ROSEMOUNT | 644H | KT0004/P2SHT1 | TI702-SP-5012 |  |  | 01
FD04 | FD04-TI-004 | FD04-T-004 | PKG | 107-CV | INDICATOR - TEMPERATURE | 25-HWR-SS1C-H-902???? | 167.0 | HOT WATER RTN TEMPERATURE |  | N/A: REF; -: REQ; -: C; -: Ref | [10 empty] | 01
FD04 | FD04-TE-005 | FD04-T-005 | PKG | 107-CV | ELEMENT - TEMPERATURE - RTD | FD04/T1/40 | 167.0 | TEMPERATURE |  | N/A: SHE; -: 12; -: C; -: GMP | [10 empty] | 01
FD04 | FD04-TI-005A | FD04-T-005 | PCS | 107-CV | INDICATOR - TEMPERATURE |  |  | TEMPERATURE |  | N/A: SHE; -: 12; -: C; -: GMP | [10 empty] | 01
FD04 | FD04-TI-005B | FD04-T-005 | LCP | 107-CV | INDICATOR - TEMPERATURE | LCP ADJ TO FD04 | 167.0 | TEMPERATURE |  | -30 to 170 degC | +/- 0.5% | SHE | 12 | C | GMP | [12 empty] | 01
FD04 | FD04-TSH-005 | FD04-T-005 | PKG | 107-CV | SWITCH - TEMPERATURE - HI | LCP ADJ TO FD04 | 167.0 | TEMPERATURE HIGH |  | N/A: SHE; -: 12; -: C; -: GMP | [10 empty] | 01
FD04 | FD04-TT-005 | FD04-T-005 | PKG | 107-CV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 167.0 | TEMPERATURE | 13204 | -30 to 150 degC | +/- 0.5% | SHE | 12 | C | GMP | I.S | AI | 1 |  | 11 | GP2 | MOORE INDUSTRIES | THZ2/PRG |  | KFD2-CRG-EX1.D | CANNOT CERTIFY TWO BARRIERS |  | 01
FD04 | FD04-TI-006 | FD04-T-006 | FLD | 107-CV | INDICATOR - TEMPERATURE | HEAD MOUNTED | 167.0 | JACKET INLET TEMP. |  | 0 to 100 degC | +/- 5% | REF | 12 | C | Ops | [6 empty] | WIKA | S5550/4 | KT0003/P1 |  |  |  | 01
FD04 | FD04-TC-011 | FD04-T-011 | PCS | 107-HG | REMOTE SETPOINT - TEMPERATURE |  |  | HEAT/COOL PACKAGE | 13206 | 0 to 100 C |  | GxP/SHE | - | - | - | N.I.S | AO | 1 |  | 22 | GP2 | [6 empty] | 01
FD04 | FD04-TIC-011 | FD04-T-011 | PKG | 107-HG | INDICATING CONTROLLER - TEMPERATURE |  | 167.0 | HEAT/COOL PACKAGE | 13206 | 0 to 100 C |  | GxP/SHE | REQ | C | Ops | N.I.S | AI | 1 |  | 13 | GP2 | [6 empty] | 01
FD04 | FD04-TSH-012 | FD04-T-012 | PKG | 107-HG | SWITCH - TEMPERATURE - HI |  | 167.0 | HEAT/COOL PACKAGE |  | set @??? |  | REF | REQ | C | Ops | [12 empty] | 01
FD04 | FD04-TI-013 | FD04-T-013 | PCS | 107-HG | INDICATOR - TEMPERATURE |  |  | HEAT/COOL PACKAGE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-TT-013 | FD04-T-013 | PKG | 107-HG | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 167.0 | HEAT/COOL PACKAGE | 13207 | 0 to 100 C |  | REF | REQ | C | Ops | N.I.S | AI | 1 |  | 13 | GP2 | [6 empty] | 01
FD04 | FD04-TSL-014 | FD04-T-014 | PKG | 107-HG | SWITCH - TEMPERATURE - LOW |  | 167.0 | HEAT/COOL PACKAGE |  | set @??? |  | REF | REQ | C | Ops | [12 empty] | 01
FD04 | FD04-TE-015 | FD04-T-015 | FLD | 107-CV | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-H-9025539 | 167.0 | VC1 INLET TEMPERATURE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-TI-015 | FD04-T-015 | PCS | 107-CV | INDICATOR - TEMPERATURE |  |  | VC1 INLET TEMPERATURE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-TT-015 | FD04-T-015 | FLD | 107-CV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 167.0 | VC1 INLET TEMPERATURE | 13205 | -20 to 100 degC | +/- 1% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | GP2 | ROSEMOUNT | 644H | KT0004/P2SHT2 | TI702-SP-5012 |  |  | 01
FD04 | FD04-YS-002A | FD04-Y-002 | PKG | 107-CV | SWITCH - POSITION | FD04-GB1 | 167.0 | GLOVEBOX OPEN |  | - | - | SIL | 12 | F | SHE | [12 empty] | 01
FD04 | FD04-YS-002B | FD04-Y-002 | PKG | 107-CV | SWITCH - POSITION | FD04-GB1 | 167.0 | GLOVEBOX OPEN |  | - | - | SIL | 12 | F | SHE | [12 empty] | 01
FD04 | FD04-YI-003 | FD04-Y-003 | LCP | 107-CV | INDICATOR - LAMP | LCP ADJ TO FD04 | 167.0 | BASE FULLY RAISED |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-YS-003A | FD04-Y-003 | PKG | 107-CV | SWITCH - BASE OPEN | FD04 | 167.0 | BASE OPEN |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
FD04 | FD04-YS-003B | FD04-Y-003 | PKG | 107-CV | SWITCH - BASE OPEN | FD04 | 167.0 | BASE OPEN |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
FD04 | FD04-YS-003C | FD04-Y-003 | PKG | 107-CV | SWITCH - BASE OPEN | FD04 | 167.0 | BASE OPEN |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
FD04 | FD04-YI-004A | FD04-Y-004 | PCS | 107-CV | INDICATOR - PERMISSIVE |  |  | PERMISSIVE INTERLOCK |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-YI-004B | FD04-Y-004 | LCP | 107-CV | INDICATOR - PERMISSIVE | LCP ADJ TO FD04 | 167.0 | PERMISSIVE INTERLOCK |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-YS-004 | FD04-Y-004 | LCP | 107-CV | PERMISSIVE SIGNAL | SWITCHROOM | 167.0 | PERMISSIVE INTERLOCK | 13208 | - | - | REF | REQ | F | Ops | I.S | DI | 1 |  | 31 | GP2 | PEPPERL + FUCHS | KFD0-RO-EX2 |  | TI702-SP-5172 |  |  | 01
FD04 | FD04-YI-006 | FD04-Y-006 | LCP | 107-CV | INDICATOR - LAMP | LCP ADJ TO FD04-GB1 | 167.0 | AGITATOR RUNNING |  | - | - | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-YI-013 | FD04-Y-013 | LCP | 107-CV | INDICATOR - LAMP | LCP ADJ TO FD04-GB1 | 167.0 | PURGE COMPLETE |  | - | - | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-YI-014 | FD04-Y-014 | LCP | 107-CV | INDICATOR - LAMP | LCP ADJ TO FD04 | 167.0 | EMERGENCY STOP HEALTHY |  | - | - | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-YI-015 | FD04-Y-015 | LCP | 107-CV | INDICATOR - LAMP | LCP ADJ TO FD04 | 167.0 | GUARDS CIRCUIT HEALTHY |  | - | - | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-YS-016 | FD04-Y-016 | LCP | 107-CV | SWITCH | FD04 | 167.0 | BASE UN-CLAMPED |  | - | - | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-YS-017 | FD04-Y-017 | LCP | 107-CV | SWITCH | FD04 | 167.0 | BASE IN PLACE |  | - | - | N/A | - | - | - | [12 empty] | 01
FD04 | FD04-YA-021 | FD04-Y-021 | PCS | 107-HG | ALARM - FAULT |  |  | HEAT/COOL PACKAGE |  | N/A: N/A; -: -; -: -; -: - | [10 empty] | 01
FD04 | FD04-YS-021 | FD04-Y-021 | PKG | 107-HG | SWITCH - FAULT |  | 167.0 | HEAT/COOL PACKAGE | 13209 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | GP2 | [6 empty] | 01
FD04 | FD04-YS-022 | FD04-Y-022 | CPR | 107-HG | SWITCH - CRASH COOL |  | 167.0 | HEAT/COOL PACKAGE |  | N/A: SHE; -: 12; -: F; -: GMP | [10 empty] | 01
FD05 | FD05-BD-001 | FD05-B-001 | FLD | 107-HE | RUPTURE DISC | 50-P-PT1A-C-9025744 | 187 | FD05 RC01 BURSTING DISC | 13251 | 6.0 barg | - | REF | - | - | - | I.S | DI | 1 |  | 32 | FG1 | BS&B | SPR-7 / BAS + | KS0003/P4 | TI702-SP-5077 | Was MES03-B-001. |  | 54
FD05 | FD05-BDI-001 | FD05-B-001 | PCS | 107-HE | ALARM - RUPTURE DISC FAIL | PCS | 187 | FD05 RC01 BURSTING DISC | 13251 | - | - | REF | - | - | - | [10 empty] | Was MES03-B-001. |  | 54
FD05 | FD05-BD-011 | FD05-B-011 | FLD | 107-HE | RUPTURE DISC | FD05 PROCESS RELIEF | 187 | FD05 BURSTING DISC | 06763 | 5.5 barg | - | REF | - | - | - | [6 empty] | BS&B | SPR-7 | KS0003/P8 |  | new Inst |  | 54
FD05 | FD05-BD-011A | FD05-B-011 | PCS | 107-HE | ALARM - RUPTURE DISC FAIL | PCS | 187 | FD05 BURSTING DISC | 06763 | - | - | REF | - | - | - | I.S | DI |  |  |  | FG1 | ELFAB | FLO-TEL |  | TI702-SP-5106 | new Inst |  | 54
FD05 | FD05-BD-011B | FD05-B-011 | PKG | 107-HE | ALARM - RUPTURE DISC FAIL | LCP ADJ TO FD05 | 187 | FD05 BURSTING DISC | 06763 | - | - | REF | - | - | - | I.S | DI |  |  |  | FG1 | PEPPERL + FUCHS | KFD2-SR2-EX2.W |  | TI702-SP-5134 | new Inst |  | 54
FD05 | FD05-CV-002 | FD05-C-002 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 15-N-PT1A-H-9025767 | 187 | 0.8 BAR N2 SUPPLY | 13210 | - | - | SHE | - | - | - | [6 empty] | FLOWSERVE |  |  |  | new Inst |  | 54
FD05 | FD05-CY-002 | FD05-C-002 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | 0.8 BAR N2 SUPPLY | 13210 | - | - | SHE | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | new Inst |  | 54
FD05 | FD05-ZSC-002 | FD05-C-002 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | 0.8 BAR N2 SUPPLY | 13210 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | new Inst |  | 54
FD05 | FD05-ZSO-002 | FD05-C-002 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | 0.8 BAR N2 SUPPLY | 13210 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | new Inst |  | 54
FD05 | FD05-CV-003 | FD05-C-003 | FLD | 107-HE | CONTROL VALVE - F.C. | 25-N-PT1A-H-9025767 | 187 | 2 BAR N2 SUPPLY | 15904 | 0 T0 100% | - | SHE | - | - | - | I.S | AO |  |  |  | FG1 | FLOWSERVE | Logix 510si |  | TI702-SP-5079 | new Inst |  | 54
FD05 | FD05-CV-004 | FD05-C-004 | PKG | 107-HE | SOLENOID VALVE | FD05 | 187 | FILTER PULSE | PKG | - | - | SHE | - | - | - | [10 empty] | new Inst |  | 54
FD05 | FD05-CV-005 | FD05-C-005 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-H-9025756 | 187 | RECIRC | 13212 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007 |  | new Inst |  | 54
FD05 | FD05-CY-005 | FD05-C-005 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | RECIRC | 13212 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | new Inst |  | 54
FD05 | FD05-ZSC-005 | FD05-C-005 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | RECIRC | 13212 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | new Inst |  | 54
FD05 | FD05-ZSO-005 | FD05-C-005 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | RECIRC | 13212 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | new Inst |  | 54
FD05 | FD05-CV-006 | FD05-C-006 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-H-9025737 | 187 | TO VC1 | 13252 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-006 |  | 54
FD05 | FD05-CY-006 | FD05-C-006 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | TO VC1 | 13252 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-006 |  | 54
FD05 | FD05-ZSC-006 | FD05-C-006 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | TO VC1 | 13252 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-006 |  | 54
FD05 | FD05-ZSO-006 | FD05-C-006 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | TO VC1 | 13252 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-006 |  | 54
FD05 | FD05-CV-008 | FD05-C-008 | FLD | 107-HE | V-BALL VALVE - CONTROL - F.C. | 40-VP-PT1A-0-9025948 | 187 | DRYER VACUUM | 13256 | 0 T0 100% | - | REF | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004/P1 | TI702-SP-5008 | Was MES03-C-015 |  | 54
FD05 | FD05-CV-009 | FD05-C-009 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9025948 | 187 | CONT. VACUUM | 13253 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-012 |  | 54
FD05 | FD05-CY-009 | FD05-C-009 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | CONT. VACUUM | 13253 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-012 |  | 54
FD05 | FD05-ZSC-009 | FD05-C-009 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | CONT. VACUUM | 13253 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-012 |  | 54
FD05 | FD05-ZSO-009 | FD05-C-009 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | CONT. VACUUM | 13253 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-012 |  | 54
FD05 | FD05-CV-010 | FD05-C-010 | FLD | 107-HE | V-BALL VALVE - CONTROL - F.C. | 40-P-PT1A-0-9025746 | 187 | ACID SCRUBBER | 13257 | 0 T0 100% | - | REF | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | TI702-SP-5008 | TI702-SP-5008 | Was MES03-C-016 |  | 54
FD05 | FD05-CV-011 | FD05-C-011 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9025746 | 187 | ACID SCRUBBER | 13254 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-013 |  | 54
FD05 | FD05-CY-011 | FD05-C-011 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | ACID SCRUBBER | 13254 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-013 |  | 54
FD05 | FD05-ZSC-011 | FD05-C-011 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | ACID SCRUBBER | 13254 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-013 |  | 54
FD05 | FD05-ZSO-011 | FD05-C-011 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | ACID SCRUBBER | 13254 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-013 |  | 54
FD05 | FD05-CV-014 | FD05-C-014 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9025742 | 187 | FD05 RC1 INLET | 13255 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-014 |  | 54
FD05 | FD05-CY-014 | FD05-C-014 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | FD05 RC1 INLET | 13255 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-014 |  | 54
FD05 | FD05-ZSC-014 | FD05-C-014 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | FD05 RC1 INLET | 13255 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-014 |  | 54
FD05 | FD05-ZSO-014 | FD05-C-014 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | FD05 RC1 INLET | 13255 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-014 |  | 54
FD05 | FD05-CV-017 | FD05-C-017 | FLD | 107-HE | V-BALL VALVE - CONTROL - F.C. | 25-N-SS1U-0-9028896 | 187 | NITROGEN TO RC1 | 13258 | 0 T0 100% | - | REF | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004/P1 | TI702-SP-5008 | Was MES03-C-017 |  | 54
FD05 | FD05-CV-018 | FD05-C-018 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9025754 | 187 | TP1 DISCHARGE | 13259 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-018 |  | 54
FD05 | FD05-CY-018 | FD05-C-018 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | TP1 DISCHARGE | 13259 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-018 |  | 54
FD05 | FD05-ZSC-018 | FD05-C-018 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | TP1 DISCHARGE | 13259 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-018 |  | 54
FD05 | FD05-ZSO-018 | FD05-C-018 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | TP1 DISCHARGE | 13259 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-018 |  | 54
FD05 | FD05-CV-023 | FD05-C-023 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-C-9025740 | 187 | REFLUX | 13262 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-023 |  | 54
FD05 | FD05-CY-023 | FD05-C-023 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | REFLUX | 13262 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-023 |  | 54
FD05 | FD05-ZSC-023 | FD05-C-023 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | REFLUX | 13262 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-023 |  | 54
FD05 | FD05-ZSO-023 | FD05-C-023 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | REFLUX | 13262 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-023 |  | 54
FD05 | FD05-CV-024 | FD05-C-024 | FLD | 107-HE | BALL VALVE - ON/OFF - F.O. | 25-P-PT1A-0-9025741 | 187 | CONDENSATE TO RC1 | 13263 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-024 |  | 54
FD05 | FD05-CY-024 | FD05-C-024 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | CONDENSATE TO RC1 | 13263 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-024 |  | 54
FD05 | FD05-ZSC-024 | FD05-C-024 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | CONDENSATE TO RC1 | 13263 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-024 |  | 54
FD05 | FD05-ZSO-024 | FD05-C-024 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | CONDENSATE TO RC1 | 13263 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-024 |  | 54
FD05 | FD05-CV-025 | FD05-C-025 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9025743 | 187 | RC1 RECYCLE | 13264 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-025 |  | 54
FD05 | FD05-CY-025 | FD05-C-025 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | RC1 RECYCLE | 13264 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-025 |  | 54
FD05 | FD05-ZSC-025 | FD05-C-025 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | RC1 RECYCLE | 13264 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-025 |  | 54
FD05 | FD05-ZSO-025 | FD05-C-025 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | RC1 RECYCLE | 13264 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-025 |  | 54
FD05 | FD05-CV-026 | FD05-C-026 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023879 | 187 | PROCESS INLET 1 | 13265 | - | - | SHE | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-026 |  | 54
FD05 | FD05-CY-026 | FD05-C-026 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | PROCESS INLET 1 | 13265 | - | - | SHE | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-026 |  | 54
FD05 | FD05-ZSC-026 | FD05-C-026 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | PROCESS INLET 1 | 13265 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-026 |  | 54
FD05 | FD05-ZSO-026 | FD05-C-026 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | PROCESS INLET 1 | 13265 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-026 |  | 54
FD05 | FD05-CV-027 | FD05-C-027 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-SO-SSIC-0-9025759 | 187 | SOLVENT INLET | 13266 | - | - | SHE | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  | Was MES03-C-027 |  | 54
FD05 | FD05-CY-027 | FD05-C-027 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | SOLVENT INLET | 13266 | - | - | SHE | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | Was MES03-C-027 |  | 54
FD05 | FD05-ZSC-027 | FD05-C-027 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | SOLVENT INLET | 13266 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-027 |  | 54
FD05 | FD05-ZSO-027 | FD05-C-027 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | SOLVENT INLET | 13266 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Was MES03-C-027 |  | 54
FD05 | FD05-CV-028 | FD05-C-028 | PKG | 107-HE | BALL VALVE - ON/OFF - F.C. | FD05 | 187 | GLOVEBOX PURGE | PKG | - | - | SHE | - | - | - | [10 empty] | No limits for this valve? |  | 54
FD05 | FD05-CV-029 | FD05-C-029 | PKG | 107-HE | SOLENOID VALVE | FD05 | 187 | MECHANICAL SEAL PURGE | PKG | - | - | SHE | - | - | - | [10 empty] | No limits for this valve? |  | 54
FD05 | FD05-CV-031 | FD05-C-031 | PKG | 107-HH | V-BALL VALVE - CONTROL - F.C. | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | PKG | - | - | SHE | - | - | - | [10 empty] | Was MES03-C-031 |  | 54
FD05 | FD05-CV-032 | FD05-C-032 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-H-902??? | 187 | CONV DRYING OUTLET | 15900 | - | - | REF | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007 |  | new Inst |  | 54
FD05 | FD05-CY-032 | FD05-C-032 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | CONV DRYING OUTLET | 15900 | - | - | REF | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 | new Inst |  | 54
FD05 | FD05-ZSC-032 | FD05-C-032 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | CONV DRYING OUTLET | 15900 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | new Inst |  | 54
FD05 | FD05-ZSO-032 | FD05-C-032 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | CONV DRYING OUTLET | 15900 | - | - | REF | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | new Inst |  | 54
FD05 | FD05-CY-033 | FD05-C-033 | PKG | 107-HE | SOLENOID VALVE | FD05 PURGE PANEL | 187 | HYDRAULIC PUMP | PKG | -: -; -: -; N/A: REF
FD05 | FD05-CY-034 | FD05-C-034 | PKG | 107-HE | SOLENOID VALVE | FD05 PURGE PANEL | 187 | AGITATOR RAISE | PKG | -: -; -: -; N/A: SHE
FD05 | FD05-CY-035 | FD05-C-035 | PKG | 107-HE | SOLENOID VALVE | FD05 PURGE PANEL | 187 | AGITATOR LOWER | PKG | -: -; -: -; N/A: SHE
FD05 | FD05-CY-036 | FD05-C-036 | PKG | 107-HE | SOLENOID VALVE | FD05 PURGE PANEL | 187 | BASE CLAMP | PKG | -: -; -: -; N/A: REF
FD05 | FD05-CY-037 | FD05-C-037 | PKG | 107-HE | SOLENOID VALVE | FD05 PURGE PANEL | 187 | BASE UNCLAMP | PKG | -: -; -: -; N/A: REF
FD05 | FD05-CY-038 | FD05-C-038 | PKG | 107-HE | SOLENOID VALVE | FD05 PURGE PANEL | 187 | BASE RAISE | PKG | -: -; -: -; N/A: SHE
FD05 | FD05-CY-039 | FD05-C-039 | PKG | 107-HE | SOLENOID VALVE | FD05 PURGE PANEL | 187 | BASE LOWER | PKG | -: -; -: -; N/A: SHE
FD05 | FD05-CY-040 | FD05-C-040 | PKG | 107-HE | SOLENOID VALVE | FD05 PURGE PANEL | 187 | SPARE | PKG | -: -; -: -; N/A: REF
FD05 | FD05-CY-041 | FD05-C-041 | PKG | 107-HE | SOLENOID VALVE | FD05 PURGE PANEL | 187 | GLOVE GUARD UNLOCK | PKG | -: -; -: -; N/A: REF
FD05 | FD05-CV-042 | FD05-C-042 | FLD | 107-HE | 3 PORT BALL VALVE - HWF/CWF - F.CWF. | 50-HWF-SS1U-H-9028946 | 187 | FD05 JACKET FLUID SUPPLY | Not assigned | -: -; -: -; N/A: SIL
FD05 | FD05-CY-042 | FD05-C-042 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | FD05 JACKET FLUID SUPPLY | Not assigned | - | - | SIL |  |  |  | I.S | DO |  |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004
FD05 | FD05-ZSC-042 | FD05-C-042 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | FD05 JACKET FLUID SUPPLY | Not assigned | - | - | REF |  |  |  | I.S | DI |  |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
FD05 | FD05-ZSO-042 | FD05-C-042 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | FD05 JACKET FLUID SUPPLY | Not assigned | - | - | REF |  |  |  | I.S | DI |  |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
FD05 | FD05-CV-043 | FD05-C-043 | FLD | 107-HE | 3 PORT BALL VALVE - HWR/CWR - F.CWR. | 50-HWF-SS1U-H-9025761 | 187 | FD05 JACKET FLUID RETURN | Not assigned | -: -; -: -; N/A: SIL
FD05 | FD05-CY-043 | FD05-C-043 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | FD05 JACKET FLUID RETURN | Not assigned | - | - | SIL |  |  |  | I.S | DO |  |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004
FD05 | FD05-ZSC-043 | FD05-C-043 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | FD05 JACKET FLUID RETURN | Not assigned | - | - | REF |  |  |  | I.S | DI |  |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
FD05 | FD05-ZSO-043 | FD05-C-043 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | FD05 JACKET FLUID RETURN | Not assigned | - | - | REF |  |  |  | I.S | DI |  |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
FD05 | FD05-CV-044 | FD05-C-044 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-N-SS1U-H-9025766 | 187 | 6 BAR N2 FROM FD05-EH2 | Not assigned | -: -; -: -; N/A: REF
FD05 | FD05-CY-044 | FD05-C-044 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 187 | 6 BAR N2 FROM FD05-EH2 | Not assigned | - | - | REF |  |  |  | I.S | DO |  |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004
FD05 | FD05-ZSC-044 | FD05-C-044 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 187 | 6 BAR N2 FROM FD05-EH2 | Not assigned | - | - | REF |  |  |  | I.S | DI |  |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
FD05 | FD05-ZSO-044 | FD05-C-044 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 187 | 6 BAR N2 FROM FD05-EH2 | Not assigned | - | - | REF |  |  |  | I.S | DI |  |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
FD05 | FD05-DIC-001 | FD05-D-001 | PCS | 107-HH | INDICATING CONTR. - MOTOR DRIVE | PCS | 074.0 | HOT WATER PUMP | Deleted | -: -; -: -; N/A: REF |  |  | 0 | [5 empty] | Was MES03-D-001 |  | 54
FD05 | FD05-DS-001 | FD05-D-001 | CPR | 107-HH | DRIVE - AVAILABLE | MES03-HW1 PANEL | 074.0 | HOT WATER PUMP | Deleted | - | - | REF |  |  |  | N.I.S | DI | 1 |  | 35 | FG1 |  |  |  |  | Was MES03-D-001 |  | 54
FD05 | FD05-DY-001 | FD05-D-001 | CPR | 107-HH | DRIVE - RUNNING | MES03-HW1 PANEL | 074.0 | HOT WATER PUMP | Deleted | - | - | REF |  |  |  | N.I.S | DI | 1 |  | 35 | FG1 |  |  |  |  | Was MES03-D-001 |  | 54
FD05 | FD05-DYC-001 | FD05-D-001 | CPR | 107-HH | DRIVE - START/STOP | MES03-HW1 PANEL | 074.0 | HOT WATER PUMP | Deleted | - | - | REF | REQ | F |  | N.I.S | DO | 1 |  | 42 | FG1 |  |  |  |  | Was MES03-D-001 |  | 54
FD05 | FD05-DIC-002 | FD05-D-002 | PCS | 107-HE | INDICATING CONTR. - MOTOR DRIVE | PCS |  | TP1 TRANSFER PUMP | 13268 | - | - | N/A | - | - | - | [10 empty] | Was MES03-D-002 |  | 54
FD05 | FD05-DS-002 | FD05-D-002 | MCC | 107-HE | DRIVE - START/STOP | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13268 | - | - | N/A | - | - | - | N.I.S | DO | 1 |  | 42 | FG1 |  |  |  |  | Was MES03-D-002 |  | 54
FD05 | FD05-DY-002 | FD05-D-002 | MCC | 107-HE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13268 | - | - | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 |  |  |  |  | Was MES03-D-002 |  | 54
FD05 | FD05-DYC-002 | FD05-D-002 | MCC | 107-HE | DRIVE - AVAILABLE |  |  | TP1 TRANSFER PUMP | 13268 | - | - | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 |  |  |  |  | Was MES03-D-002 |  | 54
FD05 | FD05-DY-003 | FD05-D-003 | PKG | 107-HH | PACKAGE RUNNING |  | 171.4 | HEAT/COOL PACKAGE | 13269 | - | - | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 |  |  |  |  | Was MES03-D-003 |  | 54
FD05 | FD05-DYC-003 | FD05-D-003 | PCS | 107-HH | PACKAGE - START/STOP | PCS | 171.4 | HEAT/COOL PACKAGE | 13269 | - | - | N/A | - | - | - | N.I.S | DO | 1 |  | 42 | FG1 |  |  |  |  | Was MES03-D-003 |  | 54
FD05 | FD05-DS-004 | FD05-D-004 | PKG | 107-HE | HEATER - AVAILABLE | LCP ADJ TO EH01 | 187 | EH2 N2 HEATER | 15900 | - | - | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 54
FD05 | FD05-DY-004 | FD05-D-004 | PKG | 107-HE | HEATER - RUNNING | LCP ADJ TO EH01 | 187 | EH2 N2 HEATER | 15900 | - | - | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 54
FD05 | FD05-DYC-004 | FD05-D-004 | PKG | 107-HE | HEATER - START/STOP | LCP ADJ TO EH01 | 187 | EH2 N2 HEATER | 15900 | - | - | N/A | - | - | - | N.I.S | DO | 1 |  | 42 | FG1 | [6 empty] | 54
FD05 | FD05-FI-001 | FD05-F-001 | FLD | 107-HE | INDICATOR - FLOW | 15-N-SSIU-O-9025768 | 187 | 0.8bar N2 SUPPLY FLOW | 15902 | -: ?; -: ?; N/A: REF
FD05 | FD05-FT-001 | FD05-F-001 | FLD | 107-HE | TRANSMITTER - FLOW | 15-N-SSIU-O-9025768 | 187 | 0.8bar N2 SUPPLY FLOW | 15902 | ? | ? | REF | REQ | C | Ref | I.S | AI |  |  |  | FG1 | KROHNE | DK37/M8E |  | TI702-SP-5060 | new Inst |  | 54
FD05 | FD05-FIC-002 | FD05-F-002 | FLD | 107-HE | INDICATOR - FLOW | FD05 NITROGEN INLET | 187 | NITROGEN INLET | 15903 | -: 0 to 1200 Nl/min; -: +/- 30 Nl/min; N/A: SHE; -: By request | [8 empty] | new Inst |  | 54
FD05 | FD05-FIT-002 | FD05-F-002 | FLD | 107-HE | TRANSMITTER - FLOW | 40-N-SS1U-H-9025766 | 187 | NITROGEN INLET | 15903 | 0 to 1200 Nl/min | +/- 30 Nl/min | SHE | By request |  |  | I.S | AI |  |  |  | FG1 | ENDRESS + HAUSER | Proline T Mass 65F25-AK4AH23GABCT |  | TI702-SP-5142 | new Inst |  | 54
FD05 | FD05-FSL-002 | FD05-F-002 | FLD | 107-HE | SWITCH - FLOW - LOW | FD05 NITROGEN INLET | 187 | NITROGEN INLET | 15903 | -: Set at 60 Nl/min; -: -0 / + 40 Nl/min; N/A: SHE
FD05 | FD05-FAH-003 | FD05-F-003 | LCP | 107-HE | ALARM - HIGH FLOW | LCP ADJ TO FD05 | 187 | MECHANICAL SEAL PURGE | PKG | 0.024 L/min | +/- 6ml/min | N/A | - | - | - | [10 empty] | new Inst |  | 54
FD05 | FD05-FI-003 | FD05-F-003 | PKG | 107-HE | INDICATOR - FLOW | N2 TO FD05 MECH SEAL | 187 | MECHANICAL SEAL PURGE | PKG | 0.05 to 60 L/min | +/- 2 % | REF | REQ | C | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-FSH-003 | FD05-F-003 | PKG | 107-HE | SWITCH - FLOW - HIGH | N2 TO FD05 MECH SEAL | 187 | MECHANICAL SEAL PURGE | PKG | 0.024 L/min | +/- 6ml/min | REF | REQ | C | Ops | [10 empty] | new Inst |  | 54
FD05 | FD05-FI-004 | FD05-F-004 | PKG | 107-HE | INDICATOR - FLOW |  | 187 | MECHANICAL SEAL PURGE | Deleted | N/A: REF; -: REQ; -: C; -: Ref | [8 empty] | new Inst |  | 54
FD05 | FD05-FS-011 | FD05-F-011 | PKG | 107-HH | FLOW SWITCH | HOT WATER FLOW | 171.4 | HEAT/COOL PACKAGE | PKG | ? | ? | REF | By request | C | Ops | [10 empty] | Was MES03-F-011 |  | 54
FD05 | FD05-FI-021 | FD05-F-021 | PKG | 107-HE | INDICATOR - FLOW | N2 TO FD05-GB1 | 187 | GLOVE BOX N2 | PKG | -: 21 to 190 l/min; -: +/- 2 %; N/A: SHE | [8 empty] | new Inst |  | 54
FD05 | FD05-FSL-021 | FD05-F-021 | PKG | 107-HE | LOW FLOW SWITCH | LCP ADJ TO FD05 | 187 | GLOVE BOX N2 | PKG | -: Set at 80Nl/min; -: -0 / 8 Nl/min; N/A: SHE | [8 empty] | new Inst |  | 54
FD05 | FD05-FSL-021 | FD05-F-021 | LCP | 107-HE | LOW FLOW SWITCH | N2 TO FD05-GB1 | 187 | GLOVE BOX N2 | PKG | -: Set at 80Nl/min; -: -0 / 8 Nl/min; N/A: SHE
FD05 | FD05-HS-001 | FD05-H-001 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-TOP | 187 | AGITATOR START | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-002 | FD05-H-002 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-TOP | 187 | AGITATOR STOP | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-007A | FD05-H-007 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-TOP | 187 | AGITATOR RAISE | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-007B | FD05-H-007 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-GB1 | 187 | AGITATOR LOWER | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-012A | FD05-H-012 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-TOP | 187 | AGITATOR SPEED INCREASE | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-012B | FD05-H-012 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05 | 187 | AGITATOR SPEED DECREASE | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-013A | FD05-H-013 | LCP | 107-HE | SAFETY SWITCH - HAND OP. (1 of 3) | LCP ADJ TO FD05-TOP | 187 | EMERGENCY STOP | PKG | - | - | SIL | 12 | F | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-013B | FD05-H-013 | LCP | 107-HE | SAFETY SWITCH - HAND OP. (2 of 3) | LCP ADJ TO FD05-GB1 | 187 | EMERGENCY STOP | PKG | - | - | SIL | 12 | F | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-013C | FD05-H-013 | LCP | 107-HE | SAFETY SWITCH - HAND OP. (3 of 3) | LCP ADJ TO FD05 | 187 | EMERGENCY STOP | PKG | - | - | SIL | 12 | F | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-014A | FD05-H-014 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05 | 187 | BASE RAISE | PKG | - | - | SHE | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-014B | FD05-H-014 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05 | 187 | BASE LOWER | PKG | - | - | SHE | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-015A | FD05-H-015 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-GB1 | 187 | GLOVEBOX LOCK | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-015B | FD05-H-015 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-GB1 | 187 | GLOVEBOX UNLOCK | PKG | - | - | REF | REQ | F | Ref
FD05 | FD05-HS-017 | FD05-H-017 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05 | 187 | VESSEL LIGHT | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-018A | FD05-H-018 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-GB1 | 187 | GLOVEBOX LIGHT - ON | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-018B | FD05-H-018 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-GB1 | 187 | GLOVEBOX LIGHT - OFF | PKG | - | - | REF | REQ | F | Ref
FD05 | FD05-HS-020A | FD05-H-020 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-TOP | 187 | AGITATOR DIRECTION - SMOOTH | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-020B | FD05-H-020 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-GB1 | 187 | AGITATOR DIRECTION - PLOUGH | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-021 | FD05-H-021 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-GB1 | 187 | SYSTEM RESET | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-HS-023 | FD05-H-023 | LCP | 107-HE | SWITCH - HAND OP. | LCP ADJ TO FD05-GB1 | 187 | MANUAL / HMI SELECT | PKG | - | - | REF | REQ | F | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-II-001 | FD05-I-001 | PCS | 107-HE | INDICATOR - CURRENT | PCS | 187 |  | PKG | bar: - to N/A
FD05 | FD05-II-002 | FD05-I-002 | PCS | 107-HE | INDICATOR - CURRENT | PCS | 187 |  | PKG | bar: - to N/A
FD05 | FD05-LIC-001 | FD05-L-001 | PCS | 107-HE | INDICATING CONTROLLER - LEVEL | PCS | 187 | RC1 LEVEL | 13271 | 0 to 600 l | +/- 1% | REF | 12 | C | Ops | [10 empty] | Was MES03-L-001 |  | 54
FD05 | FD05-LT-001 | FD05-L-001 | FLD | 107-HE | TRANSMITTER - LEVEL | FD05-RC1/N4/100 | 187 | RC1 LEVEL | 13271 | 0 to 600 l | +/- 1% | REF | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | VEGA | VEGAPULS 63 | KL0028/P3 | TI702-SP-5009 | Was MES03-L-001 |  | 54
FD05 | FD05-LAH-002 | FD05-L-002 | PCS | 107-HE | ALARM - LEVEL - HIGH | PCS | 187 | RC1 HIGH LEVEL | 13272 | Off/on | Off/on | SHE | - | - | - | [10 empty] | Was MES03-L-002 |  | 54
FD05 | FD05-LSH-002 | FD05-L-002 | FLD | 107-HE | SWITCH - LEVEL - HIGH | FD05-RC1/N7/80 | 187 | RC1 HIGH LEVEL | 13272 | Off/on | Off/on | SHE | 24 | C | Ops | I.S | DI | 1 |  | 32 | FG1 | ENDRESS + HAUSER | FLT51 C 4ALKBK8G4AA | KL0014/P2 | TI702-SP-5036 | Was MES03-L-002 |  | 54
FD05 | FD05-LI-003 | FD05-L-003 | PKG | 107-HE | INDICATOR - LEVEL | LCP ADJ TO FD05 | 187 | FD05 LEVEL | PKG | -: 0 to 570 l; -: ?; N/A: REF | [8 empty] | new Inst |  | 54
FD05 | FD05-LT-003 | FD05-L-003 | PKG | 107-HE | TRANSMITTER - LEVEL | FD05 | 187 | FD05 LEVEL | PKG | -: 0 to 570 l; -: ?; N/A: REF | [8 empty] | new Inst |  | 54
FD05 | FD05-PI-002A | FD05-P-002 | PKG | 107-HE | INDICATOR - PRESSURE | LCP ADJ TO FD05 | 187 | PRESSURE | 13213 | -: -1 to 3 barg; -: +/- 10 mbarg; N/A: REF
FD05 | FD05-PI-002B | FD05-P-002 | LCP | 107-HE | INDICATOR - PRESSURE | LCP ADJ TO FD05 | 187 | PRESSURE | 13213 | -1 to 3 barg | +/- 10 mbarg | REF | 12 | C | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-PIC-002 | FD05-P-002 | PCS | 107-HE | INDICATING CONTROLLER - PRESSURE | PCS | 187 | PRESSURE | 13213 | -1 to 3 barg | +/- 40 mbarg | REF | - | - | - | [10 empty] | new Inst |  | 54
FD05 | FD05-PT-002 | FD05-P-002 | PKG | 107-HE | TRANSMITTER - PRESSURE - DIAPHRAGM | FD05/T4/80 | 187 | FD05 PRESSURE | 13213 | -1 to 3 barg | +/- 40 mbarg | REF | 12 | C | SHE | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT / PEPPERL + FUCHS | 3051T / KFD2-CD2-EX2 |  | TI702-SP-5135 | new Inst |  | 54
FD05 | FD05-PIC-004 | FD05-P-004 | PCS | 107-HE | INDICATING CONTROLLER - PRESSURE | PCS | 187 | VC1 INLET PRESSURE | 13273 | N/A | N/A | REF | By request | - | - | [10 empty] | Was MES03-P-006 |  | 54
FD05 | FD05-PIT-004 | FD05-P-004 | FLD | 107-HE | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-H-9025737 | 187 | VC1 INLET PRESSURE | 13273 | -1 to 3 barg | +/- 0.25% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 3051 | KP0001/P | TI702-SP-5013 | Was MES03-P-006 |  | 54
FD05 | FD05-PI-007 | FD05-P-007 | FLD | 107-HE | PRESSURE GAUGE - DIAPHRAGM | 80-P-PT1A-C-9025741 | 187 | FD05 RC1 PRESSURE | N/A | -1 to 3 barg | +/- 1% | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100/990.27 | KP0006/P6 |  | Was MES03-P-007 |  | 54
FD05 | FD05-PI-008 | FD05-P-008 | FLD | 107-HE | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-0-9025754 | 187 | TP1 DISCHARGE PRESSURE | N/A | 0 to 4 barg | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | 233.50.100/990.27 | KP0006/P6 |  | Was MES03-P-008 |  | 54
FD05 | FD05-PSV-010 | FD05-P-010 | FLD | 107-HE | PRESSURE RELIEF VALVE | 25-HT-CS3A-O-9025748 | 187 | VC1 HTF RELIEF | N/A | Set at 10 barg | +/- 10% | N/A | - | - | - | [6 empty] | BROADY | 2531D-C-B000 | KS0001/P |  | Was MES03-P-010 |  | 54
FD05 | FD05-PRV-011 | FD05-P-011 | PKG | 107-HH | CONTROL VALVE SELF ACTUATING | 40-HWF-CS1B-H-9025732 | 074.0 | HOT WATER BYPASS RELIEF | PKG | set @ 2.4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | ROSEMOUNT | 98H(FS98H-75) | KV0006/1 |  | Was MES03-P-011 |  | 54
FD05 | FD05-PI-012 | FD05-P-012 | PKG | 107-HH | PRESSURE GAUGE | MES03-HW1 | 074.0 | P1 DISCHARGE PRESSURE | PKG | 0 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [5 empty] | Was MES03-P-012 |  | 54
FD05 | FD05-PRV-016 | FD05-P-016 | FLD | 107-HE | CONTROL VALVE SELF ACTUATING | 40-N-SSIU-H-9027566 | 187 | N2 SUPPLY | N/A | set @ 2 barg | +/- 5% | N/A | REQ | C | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-PI-018 | FD05-P-018 | LCP | 107-HE | PRESSURE GAUGE | LCP ADJ TO FD05-GB1 | 187 | GLOVEBOX PRESSURE | N/A | 0 to 250 Pa | +/- 5% | REF | REQ | C | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-PDI-019 | FD05-P-019 | LCP | 107-HE | PRESSURE GAUGE | LCP ADJ TO FD05-GB1 | 187 | EXTRACT FILTER CONDITION | N/A | 0 to 1 kPa | +/- 5% | REF | REQ | C | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-PSL-021 | FD05-P-021 | LCP | 107-HE | SWITCH - PRESSURE - LOW | LCP ADJ TO FD05-GB1 | 187 | GLOVEBOX PRESSURE LOW | PKG | Set at -1000pa | +/- 50Pa | SHE | 12 | C | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-PAL-022 | FD05-P-022 | LCP | 107-HE | ALARM - PRESSURE - LOW | LCP ADJ TO FD05 | 187 | AGI SEAL PRESSURE | PKG | Set at 4 barg | - 0 / + 0.5 barg | REF | - | - | - | [10 empty] | new Inst |  | 54
FD05 | FD05-PSL-022 | FD05-P-022 | PKG | 107-HE | SWITCH - PRESSURE - LOW | SEAL | 187 | AGI SEAL PRESSURE | PKG | Set at 4 barg | - 0 / + 0.5 barg | REF | REQ | C | Ops | [10 empty] | new Inst |  | 54
FD05 | FD05-PSH-023 | FD05-P-023 | LCP | 107-HE | SWITCH - PRESSURE - HIGH | LCP ADJ TO FD05-GB1 | 187 | GLOVEBOX PRESSURE HIGH | PKG | Set at -25 Pa | +/- 20 Pa | SIL | 12 | C | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-PRV-024 | FD05-P-024 | PKG | 107-HE | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028863 | 187 | GLOVEBOX PURGE | PKG | Set at 1.0 barg | +/- 5% | N/A | REQ | C | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-PRV-025 | FD05-P-025 | PKG | 107-HE | CONTROL VALVE SELF ACTUATING | PSL MECHANICAL SEAL LINE | 187 | MECHANICAL SEAL PURGE | PKG | Set at 4.5 barg | +/- 5% | N/A | REQ | C | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-PSV-030 | FD05-P-030 | PKG | 107-HH | PRESSURE RELIEF VALVE | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | PKG | Set at 4.0 barg | +/- 5% | N/A | - | - | - | [10 empty] | Was MES03-P-030 |  | 54
FD05 | FD05-PSH-031 | FD05-P-031 | PKG | 107-HH | SWITCH - PRESSURE - HIGH | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | PKG | Set at ? | ? | REF | By request | C | Ops | [10 empty] | Was MES03-P-031 |  | 54
FD05 | FD05-PI-032 | FD05-P-032 | PKG | 107-HH | PRESSURE GAUGE | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | PKG | ? | ? | REF | REQ | C | Ref | [10 empty] | Was MES03-P-032 |  | 54
FD05 | FD05-PI-033 | FD05-P-033 | PCS | 107-HE | INDICATING CONTROLLER - PRESSURE | PCS | 187 | PRESSURE | PKG | -500 to 500 Pa | +/- 20 Pa | SHE | - | - | - | [10 empty] | new Inst |  | 54
FD05 | FD05-PT-033 | FD05-P-033 | PKG | 107-HE | TRANSMITTER - PRESSURE | FD05 GLOVEBOX | 187 | PRESSURE | PKG | -500 to 500 Pa | +/- 20 Pa | SHE | 12 | C | SHE | I.S | MODBUS |  |  |  | FG1 |  |  |  |  | new Inst |  | 54
FD05 | FD05-PSL-034 | FD05-P-034 | PKG | 107-HE | SWITCH - PRESSURE - LOW | FD05 | 187 | PRESSURE | PKG | -: Set at 5.0 barg; -: - 0 / + 0.2 barg; N/A: REF
FD05 | FD05-PDI-035 | FD05-P-035 | FLD | 107-HE | INDICATOR - PRESSURE | FD05-VF1 | 187 | PRESSURE | N/A | -: 0 to 250 Pa; -: ?; N/A: REF
FD05 | FD05-RO-002 | FD05-R-002 | FLD | 107-HE | RESTRICTION ORIFICE | 25-P-PT1A-0-9025754 | 187 | TP1 DISCHARGE | N/A | 5mm | N/A | N/A | - | - | - | [10 empty] | Was MES03-R-002 |  | 54
FD05 | FD05-SI-001A | FD05-S-001 | PCS | 107-HE | INDICATOR - SPEED | PCS | 187 | AGITATOR | PKG | 0-24 rpm | +/- 2.5% | REF | - | - | - | [10 empty] | new Inst |  | 54
FD05 | FD05-SI-001B | FD05-S-001 | LCP | 107-HE | INDICATOR - SPEED | LCP ADJ TO FD05 | 187 | AGITATOR | PKG | 0-24 rpm | +/- 2.5% | REF | REQ | C | Ref | [10 empty] | new Inst |  | 54
FD05 | FD05-SIC-001 | FD05-S-001 | PKG | 107-HE | AC INVERTER DRIVE | LCP | 187 | AGITATOR | PKG | 0-24 rpm | +/- 2.5% | SHE | REQ | F | Ref | I.S | MODBUS |  |  |  | FG1 |  |  |  |  | new Inst |  | 54
FD05 | FD05-SI-002 | FD05-S-002 | PKG | 107-HE | INDICATOR - SPEED | LOCP 1 ADJ TO FD05 | 187 | AGITATOR | PKG | -: 0-24 rpm; -: +/- 2.5%; N/A: REF
FD05 | FD05-SIC-002 | FD05-S-002 | PKG | 107-HE | AC INVERTER DRIVE | LCP | 187 | AGITATOR | PKG | -: 0-24 rpm; -: +/- 2.5%; N/A: REF
FD05 | FD05-TE-002 | FD05-T-002 | FLD | 107-HE | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9025746 | 187 | VC1 VENT TEMPERATURE | 13276 | ? | ? | REF | - | - | - | [10 empty] | Was MES03-T005 |  | 54
FD05 | FD05-TI-002 | FD05-T-002 | PCS | 107-HE | INDICATOR - TEMPERATURE | PCS | 187 | VC1 VENT TEMPERATURE | 13276 | ? | ? | REF | - | - | - | [10 empty] | Was MES03-T005 |  | 54
FD05 | FD05-TT-002 | FD05-T-002 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 187 | VC1 VENT TEMPERATURE | 13276 | ? | ? | REF | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 248H | KT0004/P2 | TI702-SP-5058 | Was MES03-T005 |  | 54
FD05 | FD05-TE-003 | FD05-T-003 | FLD | 107-HE | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9023707 | 187 | VC1 HTF RTN TEMP | 13275 | ? | ? | REF | - | - | - | [10 empty] | Was MES03-T003 |  | 54
FD05 | FD05-TI-003 | FD05-T-003 | PCS | 107-HE | INDICATOR - TEMPERATURE | PCS | 187 | VC1 HTF RTN TEMP | 13275 | ? | ? | REF | - | - | - | [10 empty] | Was MES03-T003 |  | 54
FD05 | FD05-TT-003 | FD05-T-003 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 187 | VC1 HTF RTN TEMP | 13275 | ? | ? | REF | By request | C | Ref | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P2 | TI702-SP-5012 | Was MES03-T003 |  | 54
FD05 | FD05-TI-004 | FD05-T-004 | FLD | 107-HE | INDICATOR - TEMPERATURE | 50-HWR-SS1U-H-9025761 | 187 | HWR TEMPERATURE | N/A | 0 to 100 degC | +/- 5% | REF | 12 | C | Ops | [6 empty] | WIKA | S5550/4 | KT0003/P1 |  | new Inst |  | 54
FD05 | FD05-TE-005 | FD05-T-005 | PKG | 107-HE | ELEMENT - TEMPERATURE - RTD | FD05/S3/15 | 187 | TEMPERATURE | 13217 | -10 to 150 degC | +/- 2°C | SHE | 12 | C | GMP | [10 empty] | New Inst |  | 54
FD05 | FD05-TI-005A | FD05-T-005 | PCS | 107-HE | INDICATOR - TEMPERATURE | PCS | 187 | TEMPERATURE | 13217 | -10 to 150 degC | +/- 2°C | SHE | 12 | C | GMP | [10 empty] | New Inst |  | 54
FD05 | FD05-TI-005B | FD05-T-005 | LCP | 107-HE | INDICATOR - TEMPERATURE | LCP ADJ TO FD05 | 187 | TEMPERATURE | 13217 | -10 to 150 degC | N/A | SHE | 12 | C | GMP | [10 empty] | New Inst |  | 54
FD05 | FD05-TSH-005 | FD05-T-005 | PKG | 107-HE | SWITCH - TEMPERATURE - HI | LCP ADJ TO FD05 | 187 | TEMPERATURE HIGH | 13217 | Set at 90°C | +/- 2°C | SHE | 12 | C | GMP | [10 empty] | New Inst |  | 54
FD05 | FD05-TT-005 | FD05-T-005 | PKG | 107-HE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 187 | TEMPERATURE | 13217 | -10 to 150 degC | +/- 2°C | SHE | 12 | C | GMP | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT / PEPPERL + FUCHS | 644H / KFD2-CD2-EX2 |  | TI702-SP-5136 | New Inst |  | 54
FD05 | FD05-TI-006 | FD05-T-006 | FLD | 107-HE | INDICATOR - TEMPERATURE | 50-HWF-SSIU-H-9028946 | 167.0 | JACKET INLET TEMP. |  | 0 to 100 degC | +/- 5% | SHE | 12 | C | Ops | [6 empty] | WIKA | S5550/4 | KT0003/P1 |  | New Inst |  | 54
FD05 | FD05-TE-008 | FD05-T-008 | FLD | 107-HE | ELEMENT - TEMPERATURE | 50-N-SS1C-9025766 | 187 | NITROGEN INLET | 15905 | -50 to 250°C | +/- 2°C | SHE | 12 |  | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-TI-008 | FD05-T-008 | PCS | 107-HE | INDICATOR - TEMPERATURE | PCS | 187 | NITROGEN INLET | 15905 | -50 to 250°C | +/- 2°C | SHE | 12 |  | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-TSH-008 | FD05-T-008 | FLD | 107-HE | SWITCH - TEMPERATURE - HI | LCP ADJ TO EH01 | 187 | NITROGEN INLET | 15905 | Set at 90°C | +/- 2°C | SHE | 12 |  | SHE
FD05 | FD05-TT-008 | FD05-T-008 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | 40-N-SS1U-H-9025766 | 187 | NITROGEN INLET | 15905 | -50 to 250°C | +/- 2°C | SHE | 12 |  | SHE | I.S | AI |  |  |  | FG1 | ROSEMOUNT | 248H |  | TI702-SP-5143 | new Inst |  | 54
FD05 | FD05-TE-009 | FD05-T-009 | FLD | 107-HE | ELEMENT - TEMPERATURE | 50-P-PT1A-H-9025742 | 187 | BOTTOM OUTLET | 15906 | -: -50 to 250°C; -: +/- 2°C; N/A: REF; -: By request | [8 empty] | new Inst |  | 54
FD05 | FD05-TI-009 | FD05-T-009 | PCS | 107-HE | INDICATOR - TEMPERATURE | PCS | 187 | BOTTOM OUTLET | 15906 | -: -50 to 250°C; -: +/- 2°C; N/A: REF; -: By request | [8 empty] | new Inst |  | 54
FD05 | FD05-TT-009 | FD05-T-009 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | 50-P-PT1A-H-9025742 | 187 | BOTTOM OUTLET | 15906 | -50 to 250°C | +/- 2°C | REF | By request |  |  | I.S | AI |  |  |  | FG1 | ROSEMOUNT | 248 |  | TI702-SP-5058 | new Inst |  | 54
FD05 | FD05-TC-011 | FD05-T-011 | PCS | 107-HH | REMOTE SETPOINT - TEMPERATURE | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | 13278 | 0 to 100°C | +/- 2°C | GxP/SHE | - | - | - | N.I.S | AO | 1 |  | 22 | FG1 |  |  |  |  | Was MES03-T011 |  | 54
FD05 | FD05-TIC-011 | FD05-T-011 | PKG | 107-HH | INDICATING CONTROLLER - TEMPERATURE | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | 13278 | 0 to 100°C | +/- 2°C | GxP/SHE | REQ | C | Ops | N.I.S | AI | 1 |  | 13 | FG1 |  |  |  |  | Was MES03-T011 |  | 54
FD05 | FD05-TSH-012 | FD05-T-012 | PKG | 107-HH | SWITCH - TEMPERATURE - HI | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | PKG | N/A | N/A | REF | By request | C | Ops | [10 empty] | Was MES03-T012 |  | 54
FD05 | FD05-TI-013 | FD05-T-013 | PCS | 107-HH | INDICATOR - TEMPERATURE | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | PKG | N/A | N/A | REF | - | - | - | [10 empty] | Was MES03-T013 |  | 54
FD05 | FD05-TT-013 | FD05-T-013 | PKG | 107-HH | TRANSMITTER - TEMPERATURE | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | PKG | N/A | N/A | REF | By request | C | Ops | N.I.S | AI | 1 |  | 13 | FG1 |  |  |  |  | Was MES03-T013 |  | 54
FD05 | FD05-TSL-014 | FD05-T-014 | PKG | 107-HH | SWITCH - TEMPERATURE - LOW | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | PKG | N/A | N/A | REF | By request | C | Ops | [10 empty] | Was MES03-T014 |  | 54
FD05 | FD05-TE-015 | FD05-T-015 | FLD | 107-HE | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-H-9025737 | 187 | VC1 INLET TEMPERATURE | 13277 | N/A | N/A | REF | - | - | - | [10 empty] | Was MES03-T015 |  | 54
FD05 | FD05-TI-015 | FD05-T-015 | PCS | 107-HE | INDICATOR - TEMPERATURE | PCS | 187 | VC1 INLET TEMPERATURE | 13277 | N/A | N/A | REF | - | - | - | [10 empty] | Was MES03-T015 |  | 54
FD05 | FD05-TT-015 | FD05-T-015 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 187 | VC1 INLET TEMPERATURE | 13277 | N/A | N/A | REF | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 248H | KT0004/P2 | TI702-SP-5058 | Was MES03-T015 |  | 54
FD05 | FD05-TC-016 | FD05-T-016 | PCS | 107-HE | REMOTE SETPOINT - TEMPERATURE | PCS | 187 | EH2 N2 HEATER | 15901 | -20 to 135°C | +/- 2°C | SHE | - | - | - | N.I.S | AO | 1 |  | 22 | FG1 | [6 empty] | 54
FD05 | FD05-TI-016 | FD05-T-016 | PCS | 107-HE | PROCESS TEMP | PCS | 187 | EH2 N2 HEATER | 15901 | -: -20 to 135°C; -: +/- 2°C; N/A: SHE
FD05 | FD05-TIC-016 | FD05-T-016 | PKG | 107-HE | INDICATING CONTROLLER - TEMPERATURE | LCP ADJ TO EH01 | 187 | EH2 N2 HEATER | 15901 | -20 to 135°C | +/- 2°C | SHE | REQ | C | Ops | N.I.S | AI | 1 |  | 13 | FG1 | [6 empty] | 54
FD05 | FD05-TSH-016 | FD05-T-016 | PKG | 107-HE | PROCESS TEMP | EH2 N2 HEATER | 187 | EH2 N2 HEATER | 15901 | -: Set at 95°C; -: +/- 2°C; N/A: SHE
FD05 | FD05-TT-016 | FD05-T-016 | PKG | 107-HE | PROCESS TEMP | EH2 N2 HEATER | 187 | EH2 N2 HEATER | 15901 | -: -20 to 135°C; -: +/- 2°C; N/A: SHE
FD05 | FD05-TE-017 | FD05-T-017 | PKG | 107-HE | END PLATE TEMP | EH2 N2 HEATER | 187 | EH2 N2 HEATER | PKG | -: N/A; -: N/A; N/A: SHE
FD05 | FD05-TSH-017 | FD05-T-017 | PKG | 107-HE | SWITCH - TEMPERATURE - HIGH | EH2 N2 HEATER | 187 | EH2 N2 HEATER | PKG | -: Set at 125°C; -: +/- 2°C; N/A: SHE
FD05 | FD05-TE-018 | FD05-T-018 | PKG | 107-HE | HEATER ELEMENT TEMP | EH2 N2 HEATER | 187 | EH2 N2 HEATER | PKG | -: N/A; -: N/A; N/A: SHE
FD05 | FD05-TSH-018 | FD05-T-018 | PKG | 107-HE | SWITCH - TEMPERATURE - HIGH | EH2 N2 HEATER | 187 | EH2 N2 HEATER | PKG | -: Set at 560°C; -: +/- 2°C; N/A: SHE
FD05 | FD05-TI-019 | FD05-T-019 | FLD | 107-HE | INDICATOR - TEMPERATURE | 50-HWR-SS1U-H-9025761 | 187 | HWR TEMPERATURE | N/A | 0 to 100 degC | +/- 5% | REF | 12 | C | Ops | [6 empty] | WIKA | S5550/4 | KT0003/P1
FD05 | FD05-TI-020 | FD05-T-020 | FLD | 107-HE | INDICATOR - TEMPERATURE | 50-HWR-SS1U-H-9025761 | 187 | HWR TEMPERATURE | N/A | 0 to 100 degC | +/- 5% | REF | 12 | C | Ops | [6 empty] | WIKA | S5550/4 | KT0003/P1
FD05 | FD05-TI-021 | FD05-T-021 | PCS | 107-HE | INDICATOR - TEMPERATURE | PCS | 187 | HWF TEMPERATURE | 16005 | -: -30 to 150°C; -: +/- 2°C; N/A: SIL; -: 12
FD05 | FD05-TSH-021 | FD05-T-021 | FLD | 107-HE | SWITCH - TEMPERATURE - HI | LCP ADJ TO FD05 | 187 | HWF TEMPERATURE | 16005 | -: Set at 90°C; -: +/- 2°C; N/A: SIL; -: 12
FD05 | FD05-TT-021 | FD05-T-021 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | 50-HWF-SS1U-H-9028946 | 187 | HWF TEMPERATURE | 16005 | -30 to 150°C | +/- 2°C | SIL | 12 |  |  | I.S | AI |  |  |  | SIS | ROSEMOUNT | 248H |  | TI702-SP-5058
FD05 | FD05-UI-001 | FD05-U-001 | PKG | 107-HE | HEIGHT INDICATOR | LOCP 1 HMI | 187 | AGITATOR HEIGHT | PKG | -: 0 to 300mm; -: +/- 2%; N/A: REF; -: 12
FD05 | FD05-UT-001 | FD05-U-001 | FLD | 107-HE | ELEMENT - LINEAR POSITION SENSOR | FD05 | 187 | AGITATOR HEIGHT | PKG | -: 0 to 300mm; -: +/- 2%; N/A: REF; -: 12
FD05 | FD05-XI-001 | FD05-X-001 | PKG | 107-HE | SOUNDER | LOCP 1 | 187 | FD05 GLOVE BOX ALARM | PKG | -: -; -: -; N/A: REF
FD05 | FD05-XS-001 | FD05-X-001 | PKG | 107-HE | PLC OUTPUT | FD05 PURGE PANEL | 187 | FD05 GLOVE BOX ALARM | PKG | -: -; -: -; N/A: REF
FD05 | FD05-XI-011 | FD05-X-011 | PLC | 107-HE | INDICATOR | LOCP 1 HMI | 187 | FILTER BACK PULSE ENABLE | PKG | -: -; -: -; N/A: REF
FD05 | FD05-XS-011 | FD05-X-011 | PCS | 107-HE | PCS OUTPUT | PCS | 187 | FILTER BACK PULSE ENABLE | PKG | - | - | REF | REQ | F | Ref | I.S | DI |  |  |  | FG1 | PEPPERL + FUCHS | KFD2-SR2-EX2.W |  | TI702-SP-5134 | new Inst |  | 54
FD05 | FD05-XY-011 | FD05-X-011 | PLC | 107-HE | PLC INPUT | FD05 PURGE PANEL | 187 | FILTER BACK PULSE ENABLE | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-XI-012 | FD05-X-012 | FLD | 107-HE | INDICATOR - LAMP | LOCP 1 & 2 | 187 | AGI DIRECTION INDICATOR - PLOUGH | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-XS-012 | FD05-X-012 | PLC | 107-HE | PLC OUTPUT | FD05 PURGE PANEL | 187 | AGI DIRECTION INDICATOR - PLOUGH | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-XI-013 | FD05-X-013 | FLD | 107-HE | INDICATOR - LAMP | LOCP 1 & 2 | 187 | AGI DIRECTION INDICATOR - SMOOTH | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-XS-013 | FD05-X-013 | PLC | 107-HE | PLC OUTPUT | FD05 PURGE PANEL | 187 | AGI DIRECTION INDICATOR - SMOOTH | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-XI-014 | FD05-X-014 | FLD | 107-HE | INDICATOR - LAMP | LOCP 1 & 2 | 187 | GLOVEBOX LIGHT | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-XS-014 | FD05-X-014 | PLC | 107-HE | PLC OUTPUT | FD05 PURGE PANEL | 187 | GLOVEBOX LIGHT | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-XI-015 | FD05-X-015 | FLD | 107-HE | INDICATOR - LAMP | LOCP 1 & 2 | 187 | VESSEL LIGHT | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-XS-015 | FD05-X-015 | PLC | 107-HE | PLC OUTPUT | FD05 PURGE PANEL | 187 | VESSEL LIGHT | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-YI-002 | FD05-Y-002 | PLC | 107-HE | INDICATOR | LOCP 1 HMI | 187 | GLOVE GUARD LOCKED | PKG: PKG; -: -; -: -; REF: SIL
FD05 | FD05-YS-002A | FD05-Y-002 | PKG | 107-HE | SAFETY SWITCH - POSITION (1 of 2) | FD05-GB1 | 187 | GLOVE GUARD LOCKED | PKG | - | - | SIL | 12 | F | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-YS-002B | FD05-Y-002 | PKG | 107-HE | SAFETY SWITCH - POSITION (2 of 2) | FD05-GB1 | 187 | GLOVE GUARD LOCKED | PKG | - | - | SIL | 12 | F | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-YI-003A | FD05-Y-003 | PLC | 107-HE | INDICATOR | LOCP 1 HMI | 187 | LEG 1 FULLY RAISED | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-YI-003B | FD05-Y-003 | PLC | 107-HE | INDICATOR | LOCP 1 HMI | 187 | LEG 2 FULLY RAISED | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-YI-003C | FD05-Y-003 | PLC | 107-HE | INDICATOR | LOCP 1 HMI | 187 | LEG 3 FULLY RAISED | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-YS-003A | FD05-Y-003 | PKG | 107-HE | SWITCH - POSITION | FD05 | 187 | LEG 1 FULLY RAISED | PKG | - | - | REF | 12 | F | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-YS-003B | FD05-Y-003 | PKG | 107-HE | SWITCH - POSITION | FD05 | 187 | LEG 2 FULLY RAISED | PKG | - | - | REF | 12 | F | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-YS-003C | FD05-Y-003 | PKG | 107-HE | SWITCH - POSITION | FD05 | 187 | LEG 3 FULLY RAISED | PKG | - | - | REF | 12 | F | SHE | [10 empty] | new Inst |  | 54
FD05 | FD05-YI-016 | FD05-Y-016 | PCS | 107-HE | INDICATOR | FD05 | 187 | BASE UN-CLAMPED | PKG: PKG; -: -; -: -; REF: REF
FD05 | FD05-YS-016 | FD05-Y-016 | PKG | 107-HE | SWITCH - POSITION | FD05 | 187 | BASE UN-CLAMPED | PKG | - | - | REF | - | - | - | [10 empty] | new Inst |  | 54
FD05 | FD05-YI-017 | FD05-Y-017 | PLC | 107-HE | INDICATOR | FD05 | 187 | BASE CLAMPED | PKG: PKG; -: -; -: -; REF: SIL
FD05 | FD05-YS-017A | FD05-Y-017 | PKG | 107-HE | SAFETY SWITCH - POSITION (1 of 2) | FD05 | 187 | BASE CLAMPED | PKG | - | - | SIL | - | - | - | [10 empty] | new Inst |  | 54
FD05 | FD05-YS-017B | FD05-Y-017 | PKG | 107-HE | SAFETY SWITCH - POSITION (2 of 2) | FD05 | 187 | BASE CLAMPED | PKG | - | - | SIL | - | - | - | [10 empty] | new Inst |  | 54
FD05 | FD05-YI-018 | FD05-Y-018 | PLC | 107-HE | INDICATOR | FD05 | 187 | FILTER COVER IN PLACE | PKG: PKG; -: -; -: -; REF: SIL
FD05 | FD05-YS-018A | FD05-Y-018 | PKG | 107-HE | SAFETY SWITCH - POSITION (1 of 2) | FD05 | 187 | FILTER COVER IN PLACE | PKG: PKG; -: -; -: -; REF: SIL | [10 empty] | 54
FD05 | FD05-YS-018B | FD05-Y-018 | PKG | 107-HE | SAFETY SWITCH - POSITION (2 of 2) | FD05 | 187 | FILTER COVER IN PLACE | PKG: PKG; -: -; -: -; REF: SIL
FD05 | FD05-YI-019 | FD05-Y-019 | PLC | 107-HE | INDICATOR | FD05 | 187 | DISCHARGE/SAMPLE PLUG IN PLACE | PKG: PKG; -: -; -: -; REF: SIL
FD05 | FD05-YS-019A | FD05-Y-019 | PKG | 107-HE | SAFETY SWITCH - POSITION (1 of 2) | FD05 | 187 | DISCHARGE/SAMPLE PLUG IN PLACE | PKG: PKG; -: -; -: -; REF: SIL | [10 empty] | 54
FD05 | FD05-YS-019B | FD05-Y-019 | PKG | 107-HE | SAFETY SWITCH - POSITION (2 of 2) | FD05 | 187 | DISCHARGE/SAMPLE PLUG IN PLACE | PKG: PKG; -: -; -: -; REF: SIL
FD05 | FD05-YA-021 | FD05-Y-021 | PCS | 107-HH | ALARM - FAULT | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | 13280 | - | - | N/A | - | - | - | [10 empty] | Was MES03-Y021 |  | 54
FD05 | FD05-YS-021 | FD05-Y-021 | PKG | 107-HH | SWITCH - FAULT | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | 13280 | - | - | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 |  |  |  |  | Was MES03-Y021 |  | 54
FD05 | FD05-YS-022 | FD05-Y-022 | PKG | 107-HH | SWITCH - CRASH COOL | HEAT/COOL PACKAGE | 171.4 | HEAT/COOL PACKAGE | 13280 | - | - | SHE | 12 | F | GMP | [10 empty] | Was MES03-Y022 |  | 54
FD05 | FD05-YA-023 | FD05-Y-023 | PCS | 107-HE | ALARM - FAULT | PCS | 187 | EH2 N2 HEATER | PKG | - | - | N/A | - | - | - | [5 empty] | FG1 | [6 empty] | 54
FD05 | FD05-YS-023 | FD05-Y-023 | PKG | 107-HE | SWITCH - FAULT | LCP ADJ TO EH01 | 187 | EH2 N2 HEATER | PKG | - | - | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 54
FD05 | FD05-YS-024 | FD05-Y-024 | PKG | 107-HE | SWITCH - FLOW INHIBIT | LCP ADJ TO EH01 | 187 | EH2 N2 HEATER | PKG | - | - | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 54
FD05 | FD05-YI-036 | FD05-Y-036 | PCS | 107-HE | INTERFACE SIGNAL | PCS | 187 | PLC EMERGENCY STOP | PKG: 15999; -: -; -: -; REF: REF
FD05 | FD05-YS-036 | FD05-Y-036 | PLC | 107-HE | SAFETY SWITCH - STATUS | FD05 | 187 | PLC EMERGENCY STOP | PKG: 15999; -: -; -: -; REF: REF |  |  |  | FG1 | MTL | 5526 | TI702-SP-5131 | TI702-SP-5131
FD05 | FD05-YI-037 | FD05-Y-037 | PCS | 107-HE | INTERFACE SIGNAL | PCS | 187 | BASE CLAMPED | PKG: 16000; -: -; -: -; REF: REF
FD05 | FD05-YS-037 | FD05-Y-037 | PLC | 107-HE | SAFETY SWITCH - STATUS | FD05 | 187 | BASE CLAMPED | 16000 | - | - | REF |  |  |  | I.S | DI |  |  | 41 | SIS | MTL | 5526 |  | TI702-SP-5146
FD05 | FD05-YI-038 | FD05-Y-038 | PCS | 107-HE | INTERFACE SIGNAL | PCS | 187 | FILTER COVER IN PLACE | PKG: 16001; -: -; -: -; REF: REF
FD05 | FD05-YS-038 | FD05-Y-038 | PLC | 107-HE | SAFETY SWITCH - STATUS | FD05 | 187 | FILTER COVER IN PLACE | 16001 | - | - | REF |  |  |  | I.S | DI |  |  | 41 | SIS | MTL | 5526 |  | TI702-SP-5146
FD05 | FD05-YI-039 | FD05-Y-039 | PCS | 107-HE | INTERFACE SIGNAL | PCS | 187 | DISCHARGE/SAMPLE PLUG IN PLACE | PKG: 16002; -: -; -: -; REF: REF
FD05 | FD05-YS-039 | FD05-Y-039 | PLC | 107-HE | SAFETY SWITCH - STATUS | FD05 | 187 | DISCHARGE/SAMPLE PLUG IN PLACE | 16002 | - | - | REF |  |  |  | I.S | DI |  |  | 41 | SIS | MTL | 5526 |  | TI702-SP-5146
FD05 | FD05-YI-040 | FD05-Y-040 | PCS | 107-HE | INTERFACE SIGNAL | PCS | 187 | GLOVE GUARD LOCKED | PKG: 16003; -: -; -: -; REF: REF
FD05 | FD05-YS-040 | FD05-Y-040 | PLC | 107-HE | SAFETY SWITCH - STATUS | FD05 | 187 | GLOVE GUARD LOCKED | 16003 | - | - | REF |  |  |  | I.S | DI |  |  |  | FG1 | MTL | 5526 |  | TI702-SP-5131
FD05 | FD05-YI-041 | FD05-Y-041 | PCS | 107-HE | INTERFACE SIGNAL | PCS | 187 | GLOVE GUARD LOCKED | PKG: 16004; -: -; -: -; REF: REF
FD05 | FD05-YS-041 | FD05-Y-041 | PLC | 107-HE | SEQUENCE - STATUS | FD05 | 187 | RECIPE | 16004 | - | - | REF |  |  |  | I.S | DI |  |  |  | FG1 | MTL | 5526 |  | TI702-SP-5131
FG1 | FG1-FQIC-001 | FG1-F-001 | FLD | 107-DB | MOBILE WATER BATCH METER | 25-P-SSIC-0-9023263 | 041.0 | PURIFIED WATER TO R14/16/18 | -: 15 to 117 l/min; -: +/- 0.5%; REF: REF; REQ: REQ; F: C |  |  | 0 | FG1 | ROSEMOUNT | 9455FB7C1A2R | KF0018 |  | COMMON FOR MODULE FG1 |  | 01
FG1 | FG1-FQIC-001A | FG1-F-001 | FLD | 107-DB | TURBINE WATER METER/TOTALISER | 25-P-SS1C-0-9023263 | 041.0 | PURIFIED WATER TO R14/16/18 |  | 0 to 100L per min | +/-5% | REF | By request | C |  | I.S |  |  |  | 0 |  | NIXON | BNO 500 |  |  | COMMON FOR MODULE FG1 |  | 01
MFD02 | FG1MFD02-CY-002 | FG1MFD02-C-002 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 166.0 | 0.8 BAR N2 SUPPLY | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-ZSC-002 | FG1MFD02-C-002 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 166.0 | 0.8 BAR N2 SUPPLY | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | FG1MFD02-ZSO-002 | FG1MFD02-C-002 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 166.0 | 0.8 BAR N2 SUPPLY | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | FG1MFD02-CY-003 | FG1MFD02-C-003 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 166.0 | 2 BAR N2 SUPPLY | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-ZSC-003 | FG1MFD02-C-003 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 166.0 | 2 BAR N2 SUPPLY | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | FG1MFD02-ZSO-003 | FG1MFD02-C-003 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 166.0 | 2 BAR N2 SUPPLY | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | FG1MFD02-CY-005 | FG1MFD02-C-005 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED | 166.0 | RECIRC | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-ZSC-005 | FG1MFD02-C-005 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 166.0 | RECIRC | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | FG1MFD02-ZSO-005 | FG1MFD02-C-005 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 166.0 | RECIRC | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | FG1MFD02-PIC-002 | FG1MFD02-P-002 | FLD | 107-HE | CONTROLLER - PRESSURE - DIAPHRAGM | MFD02/P1/80 | 166.0 | PRESSURE | Deleted | -1 to 6 barg | 0.3%@0barg | GxP | 12 | C | SHE | I.S | AI | 1 |  | 11 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-PT-002 | FG1MFD02-P-002 | FLD | 107-HE | TRANSMITTER - PRESSURE - DIAPHRAGM | MFD02/P1/80 | 166.0 | PRESSURE | Deleted | -1 to 6 barg | 0.3%@0barg | GxP | 12 | C | SHE | I.S | AI | 1 |  | 11 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-PDT-003 | FG1MFD02-P-003 | FLD | 107-HE | TRANSMITTER - PRESSURE - DIFF | 50-P-PT1A-E-902???? | 166.0 | FILTER DIFF PRESSURE | Deleted | 0 to 1 bar | +/- 2% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-PT-033 | FG1MFD02-P-033 | FLD | 107-HE | TRANSMITTER - PRESSURE | MFD02 GLOVEBOX | 166.0 | PRESSURE | Deleted | -500 TO 500Pa |  | GxP | 12 | C | SHE | I.S | AI | 1 |  | 11 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-SIC-001 | FG1MFD02-S-001 | FLD | 107-HE | AC INVERTER DRIVE | SWITCHROOM | 166.0 | AGITATOR | Deleted | 0-23 rpm | +/- 2.5% | REF | REQ | F | Ref | I.S | AI | 1 |  | 11 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-TT-005 | FG1MFD02-T-005 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 166.0 | TEMPERATURE | Deleted | -30 to 170 degC | +/- 0.5% | SHE | 12 | C | GMP | I.S | AI | 1 |  | 11 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-YS-004 | FG1MFD02-Y-004 | FLD | 107-HE | PERMISSIVE SIGNAL | SWITCHROOM | 166.0 | PERMISSIVE INTERLOCK | Deleted | - | - | REF | REQ | F | Ops | I.S | DI | 1 |  | 31 | FG1 | [6 empty] | 01
MFD02 | FG1MFD02-YS-005 | FG1MFD02-Y-005 | FLD | 107-HE | IN PLACE - PLUGGED IN | SWITCHROOM | 166.0 | PERMISSIVE INTERLOCK | Deleted | - | - | REF | REQ | F | Ref | I.S | DI | 1 |  | 31 | FG1 | [6 empty] | 01
FG1 | FG1-PI-011 | FG1-P-011 | FLD | 108-CD | PRESSURE GAUGE | 40-CA-SS1U-0-9028451 | 042.2 | MODULE FG1 AIR PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
FG1 | FG1-HS-003AG | FG1-X-003AG | FLD | C&E/693 | SWITCH - PUSHBUTTON | FG1 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. FG1 PROCESS GND FL | 8086 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
FG1 | FG1-XA-003AG | FG1-X-003AG | FLD | C&E/693 | ALARM - AUDIBLE | FG1 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. FG1 PROCESS GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
FG1 | FG1-XL-003AG | FG1-X-003AG | FLD | C&E/693 | ALARM - BEACON | FG1 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. FG1 PROCESS GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
FG1 | FG1-HS-003BG | FG1-X-003BG | FLD | C&E/693 | SWITCH - PUSHBUTTON | FG1 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. FG1 PROCESS 1ST FL | 8092 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
FG1 | FG1-XA-003BG | FG1-X-003BG | FLD | C&E/693 | ALARM - AUDIBLE | FG1 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. FG1 PROCESS 1ST FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
FG1 | FG1-XL-003BG | FG1-X-003BG | FLD | C&E/693 | ALARM - BEACON | FG1 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. FG1 PROCESS 1ST FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
FG1 | FG1-HS-003CG | FG1-X-003CG | FLD | C&E/693 | SWITCH - PUSHBUTTON | FG1 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. FG1 PROCESS 2ND FL | 8096 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
FG1 | FG1-XA-003CG | FG1-X-003CG | FLD | C&E/693 | ALARM - AUDIBLE | FG1 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. FG1 PROCESS 2ND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
FG1 | FG1-XL-003CG | FG1-X-003CG | FLD | C&E/693 | ALARM - BEACON | FG1 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. FG1 PROCESS 2ND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
FG1 | FG1 -FSL-002 | FG1-X-010 | CPR |  | TRIPAMP | FG1 COMMONEXTRACT |  | FG1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: C; Ref: SHE | [10 empty] | 01
FG1 | FG1-FE-002 | FG1-X-010 | FLD |  | AVERAGING PITOT TUBE | FG1 COMMONEXTRACT |  | FG1 EXTRACT LOW AIR FLOW | PKG: 13???? |  |  |  |  | TORBAR | 401 | KF0027/P3 |  |  |  | 01
FG1 | FG1-FT-002 | FG1-X-010 | FLD |  | TRANSMITTER-PRESSURE | FG1 COMMONEXTRACT |  | FG1 EXTRACT LOW AIR FLOW | 13???? | 0 to 1 mbarg |  |  | 12 | C | SHE | I.S | [5 empty] | ROSEMOUNT | 3051 | KFP0001/P |  |  |  | 01
FG1 | FG1-HS-010 | FG1-X-010 | LCP |  | HAND SWITCH | FG1 COMMONEXTRACT |  | FG1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
FG1 | FG1-XA-010 | FG1-X-010 | LCP |  | ALARM SOUNDER | FG1 COMMONEXTRACT |  | FG1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
FG1 | FG1-XL-010A | FG1-X-010 | LCP |  | INDICATOR LAMP | FG1 COMMONEXTRACT |  | FG1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
FG1 | FG1-XL-010B | FG1-X-010 | LCP |  | INDICATOR LAMP | FG1 COMMONEXTRACT |  | FG1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
FH001 | FH001-DPS-001 | FH001-DP-001 | FLD | HVAC | Differential pressure switch | CTC extract HEPA | 155.0 | CTC extract HEPA dP | -: 500 kPa |  |  |  |  | DELTA CONTROLS LTD | N3010ICNOGA30 |  |  |  |  | 01
FH002 | FH002-DPS-001 | FH002-DP-001 | FLD | HVAC | Differential pressure switch | Mill room extract HEPA | 155.0 | Mill room extract HEPA dP | -: 500 kPa |  |  |  |  | DELTA CONTROLS LTD | N3010ICNOGA30 |  |  |  |  | 01
FIRE | FIRE-XS-001 | FIRE-X-001 | FLD | C&E/693 | SWITCH - MISC. ALARM | FIRE SYSTEM | 019.0 | PLANT SPILLAGE | 8641 | - | - |  | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
FIRE | FIRE-XS-002 | FIRE-X-002 | FLD | C&E/693 | SWITCH - MISC. ALARM | FIRE SYSTEM | 019.0 | FIRE ALERT | 8642 | - | - |  | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
FIRE | FIRE-XS-003 | FIRE-X-003 | FLD | C&E/693 | SWITCH - MISC. ALARM | FIRE SYSTEM | 019.0 | FIRE EVACUATE | 8643 | - | - |  | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
FIRE | FIRE-XS-004 | FIRE-X-004 | FLD | C&E/693 | SWITCH - MISC. ALARM | FIRE SYSTEM | 019.0 | FIRE SYSTEM FAULT | 8644 | - | - |  | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
GAM02 | GAM02-FI-001 | GAM02-F-001 | FLD | 107-HS | FLOW INDICATOR | 6-P-SS1U-0-9024601 |  | GAS ADDITION FLOW | -: 0 to 8.3Nl/min |  |  |  |  | SWAGELOCK | VAF-G2-08L-1-0-Z
GAM02 | GAM02-PRV-001 | GAM02-P-001 | FLD | 107-HS | CONTROL VALVE SELF ACTUATING | 6-P-SS25T-0-9024600 |  | NITROGEN/AIR SUPPLY | -: 0 to 3.5 barg; -: +/- 5% |  |  |  |  | CONCOA PRECISION GAS CONTROLS | 312 SERIES REGULATOR 2322-FPT
GAM02 | GAM02-PI-002 | GAM02-P-002 | FLD | 107-HS | PRESSURE GAUGE | INTEGRAL TO PRV-001 |  | NITROGEN/AIR CYLINDER PRESSURE | -: 0 to 280 barg; -: +/- 5%
GAM02 | GAM02-PI-003 | GAM02-P-003 | FLD | 107-HS | PRESSURE GAUGE | INTEGRAL TO PRV-001 |  | NITROGEN/AIR SUPPLY PRESSURE | -: -1 to 7 barg; -: +/- 5%
GAM02 | GAM02-PSV-004 | GAM02-P-004 | FLD | 107-HS | PRESSURE RELIEF VALVE | 6-P-SS1U-0-9024601 |  | LINE PRESSURE RELIEF | -: Set at 3barg |  |  |  |  | SEETRU LIMITED | 64610A5748 TYPE SEETRU RELIEF C/W FDA SEALS
GP1 | GP1-FQIC-001 | GP1-F-001 | FLD | 107-BA | MOBILE WATER BATCH METER | 25-P-SS1C-0-9021163 | 041.0 | PURIFIED WATER TO R01/2/3/4/5/6 | -: 15 to 117 l/min; -: +/- 0.5%; REF: REF; REQ: REQ; F: C |  |  | 0 | GP1 | ROSEMOUNT | 9455FB7C1A2R | KF0018 |  | COMMON FOR MODULE GP1 |  | 01
GP1 | GP1-FQIC-001 | GP1-F-001 | [6 empty] | REF: REF
GP1 | GP1-FQIC-001A | GP1-F-001 | FLD | 107-BA | TURBINE WATER METER/TOTALISER | 25-P-SS1C-0-9021163 | 041.0 | PURIFIED WATER TO R01/2/3/4/5/6 |  | 0 to 100L per min | +/-5% | REF | By request | C |  | I.S |  |  |  | 0 |  | NIXON | BNO 500 |  |  | COMMON FOR MODULE GP1 |  | 01
MFD02 | GP1MFD02-CY-002 | GP1MFD02-C-002 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED | 166.0 | 0.8 BAR N2 SUPPLY | 13220 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
MFD02 | GP1MFD02-ZSC-002 | GP1MFD02-C-002 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 166.0 | 0.8 BAR N2 SUPPLY | 13220 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | WESTLOCK CONTROLS | 3045 |  | TI702-SP-5000 |  |  | 01
MFD02 | GP1MFD02-ZSO-002 | GP1MFD02-C-002 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 166.0 | 0.8 BAR N2 SUPPLY | 13220 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | WESTLOCK CONTROLS | 3045 |  | TI702-SP-5000 |  |  | 01
MFD02 | GP1MFD02-CV-003 | GP1MFD02-C-003 | FLD | 107-HF | CONTROL VALVE | MTD. ON VALVE | 166.0 |  | 13221 |  |  | N/A | - | - | - | I.S | AO | 1 |  | 41 | GP1 | SAMSON | 3730-2 POSITIONER |  | TI702-SP-5008 | Changed from CY to CV. Limits Removed |  | 01
MFD02 | GP1MFD02-ZSC-003 | GP1MFD02-C-003 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 166.0 | 2 BAR N2 SUPPLY | 13221 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  |  | Deleted |  | 01
MFD02 | GP1MFD02-ZSO-003 | GP1MFD02-C-003 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 166.0 | 2 BAR N2 SUPPLY | 13221 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  |  | Deleted |  | 01
MFD02 | GP1MFD02-CY-005 | GP1MFD02-C-005 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED | 166.0 | RECIRC | 13222 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
MFD02 | GP1MFD02-ZSC-005 | GP1MFD02-C-005 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 166.0 | RECIRC | 13222 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | WESTLOCK CONTROLS | 3045 |  | TI702-SP-5000 |  |  | 01
MFD02 | GP1MFD02-ZSO-005 | GP1MFD02-C-005 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 166.0 | RECIRC | 13222 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | WESTLOCK CONTROLS | 3045 |  | TI702-SP-5000 |  |  | 01
MFD02 | GP1MFD02-PIC-002 | GP1MFD02-P-002 | FLD | 107-HF | CONTROLLER - PRESSURE - DIAPHRAGM | MFD02/P1/80 | 166.0 | PRESSURE | 13223 | -1 to 6 barg | 0.3%@0barg | REF | REQ | C | SHE | I.S | AI | 1 |  | 11 | GP1 | [6 empty] | 49
MFD02 | GP1MFD02-PT-002 | GP1MFD02-P-002 | FLD | 107-HF | TRANSMITTER - PRESSURE - DIAPHRAGM | MFD02/P1/80 | 166.0 | PRESSURE | 13223 | -1 to 6 barg | 0.3%@0barg | REF | 12 | C | SHE | I.S | AI | 1 |  | 11 | GP1 | ROSEMOUNT | 3051 |  | TI702-SP-5164 |  |  | 01
MFD02 | GP1MFD02-PDT-003 | GP1MFD02-P-003 | FLD | 107-HF | TRANSMITTER - PRESSURE - DIFF | 50-P-PT1A-E-902???? | 166.0 | FILTER DIFF PRESSURE | 13224 | 0 to 1 bar | +/- 2% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | GP1 | ROSEMOUNT | 3051 |  | TI702-SP-5164 |  |  | 01
MFD02 | GP1MFD02-PT-033 | GP1MFD02-P-033 | FLD | 107-HF | TRANSMITTER - PRESSURE | MFD02 GLOVEBOX | 166.0 | PRESSURE | 13225 | -500 TO 500Pa |  | SHE | REQ | C | SHE | I.S | AI | 1 |  | 11 | GP1 | ROSEMOUNT | 3051 |  | TI702-SP-5164 |  |  | 49
MFD02 | GP1MFD02-SIC-001 | GP1MFD02-S-001 | FLD | 107-HF | AC INVERTER DRIVE | SWITCHROOM | 166.0 | AGITATOR | 13226 | 0-23 rpm | +/- 2.5% | REF | REQ | F | Ref | I.S | AI | 1 |  | 11 | GP1 |  |  |  | KFD0-CC-EX1 | CANNOT CERTIFY TWO BARRIERS |  | 01
MFD02 | GP1MFD02-TT-005 | GP1MFD02-T-005 | FLD | 107-HF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 166.0 | TEMPERATURE | 13227 | -30 to 170 degC | +/- 0.5% | SHE | 12 | C | GMP | I.S | AI | 1 |  | 11 | GP1 | MOORE INDUSTRIES | THZ2/PRG |  | KFD2-CRG-EX1.D | CANNOT CERTIFY TWO BARRIERS |  | 01
MFD02 | GP1MFD02-YS-004 | GP1MFD02-Y-004 | FLD | 107-HF | PERMISSIVE SIGNAL | SWITCHROOM | 166.0 | PERMISSIVE INTERLOCK | 13228 | - | - | REF | REQ | F | Ops | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | KFD0-RO-EX2 |  | TI702-SP-5172 |  |  | 01
MFD02 | GP1MFD02-YS-005 | GP1MFD02-Y-005 | FLD | 107-HF | IN PLACE - PLUGGED IN | SWITCHROOM | 166.0 | PERMISSIVE INTERLOCK | 13229 | - | - | REF | REQ | F | Ref | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | KFD0-RO-EX2 |  | TI702-SP-5172 |  |  | 01
GP1 | GP1-PI-011 | GP1-P-011 | FLD | 108-CC | PRESSURE GAUGE | 40-CA-SS1U-0-9028450 | 042.2 | MODULE GP1 AIR PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
GP1 | GP1-PI-012 | GP1-P-012 | FLD | 108-CD | PRESSURE GAUGE | 40-CA-SS1U-0-9028452 | 042.2 | MODULE GP1 AIR PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
GP1 | GP1-HS-003AB | GP1-X-003AB | FLD | C&E/693 | SWITCH - PUSHBUTTON | GP1 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. GP1 PROCESS GND FL | 8084 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
GP1 | GP1-XA-003AB | GP1-X-003AB | FLD | C&E/693 | ALARM - AUDIBLE | GP1 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. GP1 PROCESS GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
GP1 | GP1-XL-003AB | GP1-X-003AB | FLD | C&E/693 | ALARM - BEACON | GP1 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. GP1 PROCESS GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
GP1 | GP1-HS-003BB | GP1-X-003BB | FLD | C&E/693 | SWITCH - PUSHBUTTON | GP1 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. GP1 PROCESS 1ST FL | 8090 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
GP1 | GP1-XA-003BB | GP1-X-003BB | FLD | C&E/693 | ALARM - AUDIBLE | GP1 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. GP1 PROCESS 1ST FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
GP1 | GP1-XL-003BB | GP1-X-003BB | FLD | C&E/693 | ALARM - BEACON | GP1 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. GP1 PROCESS 1ST FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
GP1 | GP1-HS-003CB | GP1-X-003CB | FLD | C&E/693 | SWITCH - PUSHBUTTON | GP1 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. GP1 PROCESS 2ND FL | 8094 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
GP1 | GP1-XA-003CB | GP1-X-003CB | FLD | C&E/693 | ALARM - AUDIBLE | GP1 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. GP1 PROCESS 2ND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
GP1 | GP1-XL-003CB | GP1-X-003CB | FLD | C&E/693 | ALARM - BEACON | GP1 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. GP1 PROCESS 2ND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
GP1 | GP1 FSL-002 | GP1-X-010 | CPR |  | TRIPAMP | GP1 COMMONEXTRACT |  | GP1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: C; Ref: SHE | [10 empty] | 01
GP1 | GP1-FE-002 | GP1-X-010 | FLD |  | AVERAGING PITOT TUBE | GP1 COMMONEXTRACT |  | GP1 EXTRACT LOW AIR FLOW | PKG: 13???? |  |  |  |  | TORBAR | 401 | KF0027/P3 |  |  |  | 01
GP1 | GP1-FT-002 | GP1-X-010 | FLD |  | TRANSMITTER-PRESSURE | GP1 COMMONEXTRACT |  | GP1 EXTRACT LOW AIR FLOW | 13???? | 0 to 1 mbarg |  |  | 12 | C | SHE | I.S | [5 empty] | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 01
GP1 | GP1-HS-010 | GP1-X-010 | LCP |  | HAND SWITCH | GP1 COMMONEXTRACT |  | GP1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
GP1 | GP1-XA-010 | GP1-X-010 | LCP |  | ALARM SOUNDER | GP1 COMMONEXTRACT |  | GP1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
GP1 | GP1-XL-010A | GP1-X-010 | LCP |  | INDICATOR LAMP | GP1 COMMONEXTRACT |  | GP1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
GP1 | GP1-XL-010B | GP1-X-010 | LCP |  | INDICATOR LAMP | GP1 COMMONEXTRACT |  | GP1 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
GP2 | GP2-FQIC-001 | GP2-F-001 | FLD | 107-CA | MOBILE WATER BATCH METER | 25-P-SS1C-0-9022163 | 041.0 | PURIFIED WATER TO R07/8/9/10/11/12 | -: 15 to 117 l/min; -: +/- 0.5%; REF: REF; REQ: REQ; F: C |  |  | 0 | GP2 | ROSEMOUNT | 9455FB7C1A2R | KF0018 |  | COMMON FOR MODULE GP2 |  | 01
GP2 | GP2-FQIC-001A | GP2-F-001 | FLD | 107-CA | TURBINE WATER METER/TOTALISER | 25-P-SS1C-0-9022163 | 041.0 | PURIFIED WATER TO R07/8/9/10/11/12 |  | 0 to 100L per min | +/-5% | REF | By request | C |  | I.S |  |  |  | 0 |  | NIXON | BNO 500 |  |  | COMMON FOR MODULE GP2 |  | 01
GP2 | GP2-PI-011 | GP2-P-011 | FLD | 108-CD | PRESSURE GAUGE | 40-CA-SS1U-0-9028455 | 042.2 | MODULE GP2 AIR PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
GP2 | GP2-HS-003AD | GP2-X-003AD | FLD | C&E/693 | SWITCH - PUSHBUTTON | GP2 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. GP2 PROCESS GND FL | 8085 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
GP2 | GP2-XA-003AD | GP2-X-003AD | FLD | C&E/693 | ALARM - AUDIBLE | GP2 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. GP2 PROCESS GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
GP2 | GP2-XL-003AD | GP2-X-003AD | FLD | C&E/693 | ALARM - BEACON | GP2 PROC. AREA GND FLOOR | 083.2 | GEN. ALM. GP2 PROCESS GND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
GP2 | GP2-HS-003BD | GP2-X-003BD | FLD | C&E/693 | SWITCH - PUSHBUTTON | GP2 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. GP2 PROCESS 1ST FL | 8091 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
GP2 | GP2-XA-003BD | GP2-X-003BD | FLD | C&E/693 | ALARM - AUDIBLE | GP2 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. GP2 PROCESS 1ST FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
GP2 | GP2-XL-003BD | GP2-X-003BD | FLD | C&E/693 | ALARM - BEACON | GP2 PROC. AREA 1ST FLOOR | 083.2 | GEN. ALM. GP2 PROCESS 1ST FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
GP2 | GP2-HS-003CD | GP2-X-003CD | FLD | C&E/693 | SWITCH - PUSHBUTTON | GP2 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. GP2 PROCESS 2ND FL | 8095 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
GP2 | GP2-XA-003CD | GP2-X-003CD | FLD | C&E/693 | ALARM - AUDIBLE | GP2 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. GP2 PROCESS 2ND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
GP2 | GP2-XL-003CD | GP2-X-003CD | FLD | C&E/693 | ALARM - BEACON | GP2 PROC. AREA 2ND FLOOR | 083.2 | GEN. ALM. GP2 PROCESS 2ND FL |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
GP2 | GP2- FSL-002 | GP2-X-010 | CPR |  | TRIPAMP | GP2 COMMONEXTRACT |  | GP2 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: C; Ref: SHE | [10 empty] | 01
GP2 | GP2-FE-002 | GP2-X-010 | FLD |  | AVERAGING PITOT TUBE | GP2 COMMONEXTRACT |  | GP2 EXTRACT LOW AIR FLOW | PKG: 13???? |  |  |  |  | TORBAR | 401 | KF0027/P3 |  |  |  | 01
GP2 | GP2-FT-002 | GP2-X-010 | FLD |  | TRANSMITTER-PRESSURE | GP2 COMMONEXTRACT |  | GP2 EXTRACT LOW AIR FLOW | 13???? | 0 to 1 mbarg |  |  | 12 | C | SHE | I.S | [5 empty] | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 01
GP2 | GP2-HS-010 | GP2-X-010 | LCP |  | HAND SWITCH | GP2 COMMONEXTRACT |  | GP2 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
GP2 | GP2-XA-010 | GP2-X-010 | LCP |  | ALARM SOUNDER | GP2 COMMONEXTRACT |  | GP2 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
GP2 | GP2-XL-010A | GP2-X-010 | LCP |  | INDICATOR LAMP | GP2 COMMONEXTRACT |  | GP2 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
GP2 | GP2-XL-010B | GP2-X-010 | LCP |  | INDICATOR LAMP | GP2 COMMONEXTRACT |  | GP2 EXTRACT LOW AIR FLOW | PKG: 13????; REQ: 12; F: F; Ref: SHE; I.S: I.S | [10 empty] | 01
HC01 | HC01-CV-001 | HC01-C-001 | PKG | 107-SB | CONTROL VALVE | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP TEMPERATURE | -: N/A; -: N/A; REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-CV-002 | HC01-C-002 | PKG | 107-SB | CONTROL VALVE | HEAT/COOL PKG | 171.5 | COLD LOOP TAKE OFF PRESSURE | -: N/A; -: N/A; REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-CV-012 | HC01-C-012 | PKG | 107-SB | CONTROL VALVE | HEAT/COOL PKG | 171.5 | HOT LOOP TAKE OFF PRESSURE | -: N/A; -: N/A; REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-CV-021 | HC01-C-021 | PKG | 107-SB | 3 WAY VALVE | HEAT/COOL PKG | 171.5 | RETURN LOOP DIVERTER |  | N/A | N/A | N/A | N/A | N/A |  | I.S |  | DO | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-DS-001 | HC01-D-001 | PKG | 107-SB | DRIVE - AVAILABLE | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP PUMP |  | N/A | N/A | N/A | N/A | N/A |  | N.I.S |  | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-DY-001 | HC01-D-001 | PKG | 107-SB | DRIVE - RUNNING | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP PUMP |  | N/A | N/A | N/A | N/A | N/A |  | N.I.S |  | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-DYC-001 | HC01-D-001 | PKG | 107-SB | DRIVE - START/STOP | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP PUMP |  | N/A | N/A | N/A | N/A | N/A |  | N.I.S |  | DO | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-DS-011 | HC01-D-011 | PKG | 107-SB | DRIVE - AVAILABLE | HEAT/COOL PKG | 171.5 | HOT RE-CIRC LOOP PUMP |  | N/A | N/A | N/A | N/A | N/A |  | N.I.S |  | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-DY-011 | HC01-D-011 | PKG | 107-SB | DRIVE - RUNNING | HEAT/COOL PKG | 171.5 | HOT RE-CIRC LOOP PUMP |  | N/A | N/A | N/A | N/A | N/A |  | N.I.S |  | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-DYC-011 | HC01-D-011 | PKG | 107-SB | DRIVE - START/STOP | HEAT/COOL PKG | 171.5 | HOT RE-CIRC LOOP PUMP |  | N/A | N/A | N/A | N/A | N/A |  | N.I.S |  | DO | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-DS-012 | HC01-D-012 | PKG | 107-SB | HEATER AVAILABLE | HEAT/COOL PKG | 171.5 | HTF HEATER AVAILABLE |  | N/A | N/A | N/A | N/A | N/A |  | N.I.S |  | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-FSL-001 | HC01-F-001 | PKG | 107-SB | FLOW SWITCH | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP LOW FLOW ALARM | REF: Ref; REQ: By Req; F: F; I.S: N.I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-FSL-011 | HC01-F-011 | PKG | 107-SB | FLOW SWITCH | HEAT/COOL PKG | 171.5 | HOT RE-CIRC LOOP LOW FLOW ALARM | REF: Ref; REQ: By Req; F: F; I.S: N.I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-HS-021 | HC01-H-021 | PKG | 107-SB | HAND SWITCH | HEAT/COOL PKG | 171.5 | E/STOP | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-LSL-021 | HC01-L-021 | PKG | 107-SB | LEVEL SWITCH LOW | HEAT/COOL PKG | 171.5 | RESERVOIR LEVEL LOW | REF: Ref; REQ: By Req; F: F; I.S: N.I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-LSH-022 | HC01-L-022 | PKG | 107-SB | LEVEL SWITCH LOW | HEAT/COOL PKG | 171.5 | RESERVOIR LEVEL HIGH | REF: REF; REQ: 24; F: F; I.S: N.I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-LI-023 | HC01-L-023 | PKG | 107-SB | LEVEL SWITCH LOW | HEAT/COOL PKG | 171.5 | RESERVOIR LEVEL | REF: Ref; REQ: By Req; F: F | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-LSLL-024 | HC01-L-024 | PKG | 107-SB | LEVEL SWITCH LOW LOW | HEAT/COOL PKG | 171.5 | RESERVOIR LEVEL LOW LOW | REF: REF; REQ: 24; F: F; I.S: N.I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-PI-001 | HC01-P-001 | PKG | 107-SB | PRESSURE GAUGE | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP PRESSURE | REF: Ref; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PIC-002 | HC01-P-002 | PKG | 107-SB | PRESSURE TRANSMITTER | HEAT/COOL PKG | 171.5 | COLD LOOP TAKE OFF PRESSURE | REF: REF; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PT-002 | HC01-P-002 | PKG | 107-SB | PRESSURE TRANSMITTER | HEAT/COOL PKG | 171.5 | COLD LOOP TAKE OFF PRESSURE | REF: REF; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PI-011 | HC01-P-011 | PKG | 107-SB | PRESSURE GAUGE | HEAT/COOL PKG | 171.5 | HOT RE-CIRC LOOP PRESSURE | REF: Ref; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PIC-012 | HC01-P-012 | PKG | 107-SB | PRESSURE TRANSMITTER | HEAT/COOL PKG | 171.5 | HOT LOOP TAKE OFF PRESSURE | REF: REF; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PT-012 | HC01-P-012 | PKG | 107-SB | PRESSURE TRANSMITTER | HEAT/COOL PKG | 171.5 | HOT LOOP TAKE OFF PRESSURE | REF: REF; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PI-021 | HC01-P-021 | PKG | 107-SB | PRESSURE GAUGE | HEAT/COOL PKG | 171.5 | RESERVOIR PRESSURE | REF: Ref; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PSL-022 | HC01-P-022 | PKG | 107-SB | PRESSURE SWITCH | HEAT/COOL PKG | 171.5 | RESERVOIR PRESSURE LOW | REF: REF; REQ: By Req; F: F; I.S: N.I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-PRV-023 | HC01-P-023 | PKG | 107-SB | CONTROL VALVE SELF ACTUATING | HEAT/COOL PKG | 171.5 | RESERVOIR AIR SUPPLY | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PSV-024 | HC01-P-024 | PKG | 107-SB | PRESSURE RELIEF VALVE | HEAT/COOL PKG | 171.5 | RESERVOIR PRESSURE RELIEF | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PRV-025 | HC01-P-025 | PKG | 107-SB | CONTROL VALVE SELF ACTUATING | HEAT/COOL PKG | 171.5 | RESERVOIR EXPANSSION RELIEF | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-PSL-025 | HC01-P-025 | PKG | 107-SB | PRESSURE SWITCH | HEAT/COOL PKG | 171.5 | PURGE AIR LOW PRESSURE | REF: REF; REQ: 12; F: F; I.S: N.I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-PSV-026 | HC01-P-026 | PKG | 107-SB | PRESSURE RELIEF VALVE | HEAT/COOL PKG | 171.5 | HFT RELIEF | -: 10 barg; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | BROADY | 3531D-SB-000 | KS0001/P2 |  |  |  | 06
HC01 | HC01-TIC-001 | HC01-T-001 | PKG | 107-SB | TEMPERATURE CONTROLLER | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP TEMPERATURE | -: -30 to 170 C; REF: REF; REQ: By Req; F: C; I.S: N.I.S | AO | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-TT-001 | HC01-T-001 | PKG | 107-SB | TEMPERATURE TRANSMITTER | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP TEMPERATURE | -: -30 to 170 C; REF: REF; REQ: By Req; F: C; I.S: N.I.S | AI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-TI-002 | HC01-T-002 | PKG | 107-SB | TEMPERATURE GAUGE | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP TEMPERATURE | REF: Ref; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-TSH-003 | HC01-T-003 | PKG | 107-SB | TEMPERATURE SWITCH | HEAT/COOL PKG | 171.5 | COLD RE-CIRC LOOP TEMP ALARM | REF: REF; REQ: By Req; F: F; I.S: N.I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-TIC-011 | HC01-T-011 | PKG | 107-SB | TEMPERATURE CONTROLLER | HEAT/COOL PKG | 171.5 | HOT RE-CIRC LOOP TEMPERATURE | -: -30 to 170 C; REF: REF; REQ: By Req; F: C; I.S: N.I.S | AO | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-TT-011 | HC01-T-011 | PKG | 107-SB | TEMPERATURE TRANSMITTER | HEAT/COOL PKG | 171.5 | HOT RE-CIRC LOOP TEMPERATURE | -: -30 to 170 C; REF: REF; REQ: By Req; F: C; I.S: N.I.S | AI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-TI-012 | HC01-T-012 | PKG | 107-SB | TEMPERATURE GAUGE | HEAT/COOL PKG | 171.5 | HOT RE-CIRC LOOP TEMPERATURE | REF: Ref; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-TSH-013 | HC01-T-013 | PKG | 107-SB | TEMPERATURE SWITCH | HEAT/COOL PKG | 171.5 | HOT RE-CIRC LOOP TEMP ALARM | REF: REF; REQ: By Req; F: F; I.S: N.I.S | DI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-TIC-021 | HC01-T-021 | PKG | 107-SB | TEMPERATURE CONTROLLER | HEAT/COOL PKG | 171.5 | HTF RETURN TEMPERATURE | REF: REF; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
HC01 | HC01-TT-021 | HC01-T-021 | PKG | 107-SB | TEMPERATURE TRANSMITTER | HEAT/COOL PKG | 171.5 | HTF RETURN TEMPERATURE | REF: REF; REQ: By Req; F: C; I.S: N.I.S | AI | [5 empty] | N/A |  |  |  | 06
HC01 | HC01-YA-001 | HC01-Y-001 | PKG | 107-SB | PACKAGE ALARM | PCS | 083 | HEAT/COOL PACKAGE AVAILABLE | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  |  |  | 06
HCR | HCR-HS-001DA | HCR-H-001 | HCR | C&E/693 | SWITCH - PUSHBUTTON | HCR ALARM ANNUN. | 083.2 | H2 LEAK ALM. ACKNOWLEDGE | 8645 | - | - | REF | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
HCR | HCR-HS-003DA | HCR-H-003 | HCR | C&E/693 | SWITCH - PUSHBUTTON | HCR ALARM ANNUN. | 083.2 | GEN. ALM. ACKN. HYDROG | 8646 | - | - | REF | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
HCR | HCR-HS-005DA | HCR-H-005 | HCR | C&E/693 | SWITCH - KEY OP. | HCR ALARM ANNUN. | 083.2 | SELECT VENT VIA CV-020 | 8647 | - | - | REF | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
HCR | HCR-HS-006DA | HCR-H-006 | HCR | C&E/693 | SWITCH - PUSHBUTTON | HCR ALARM ANNUN. | 083.2 | HYDROG DEPRESS. TRIP RESET | 8648 | - | - | REF | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
HCR | HCR-HS-007DA | HCR-H-007 | HCR | C&E/693 | SWITCH - PUSHBUTTON | HCR ALARM ANNUN. | 083.2 | ANNUNCIATOR LAMP TEST | 8649 | - | - | REF | REQ | F |  | N.I.S |  | DI |  | 35 | SGS | [6 empty] | 01
HCR | HCR-XL-101 | HCR-X-101 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | H2 DETECTOR A - 1% LEL | 8650 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-102 | HCR-X-102 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | H2 DETECTOR A - 10% LEL | 8651 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-103 | HCR-X-103 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | H2 DETECTOR B - 1% LEL | 8652 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-104 | HCR-X-104 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | H2 DETECTOR B - 10% LEL | 8653 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-105 | HCR-X-105 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | H2 DETECTOR C - 1% LEL | 8654 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-106 | HCR-X-106 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | H2 DETECTOR C - 10% LEL | 8655 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-107 | HCR-X-107 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | VENT VIA CV-020 SELECTED | 8656 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-108 | HCR-X-108 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | PCS GENERAL ALARM | 8657 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-109 | HCR-X-109 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | BREATHING AIR LOW PRESSURE | 8658 | - | - |  | REQ | F |  | N.I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-110 | HCR-X-110 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. |  | SPARE(FUTURE) | I.S: N.I.S | DO |  | 42 | SGS |  |  |  |  | SPARE WINDOW |  | 01
HCR | HCR-XL-111 | HCR-X-111 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | LOOP REACTOR HYDROGEN SHUTOFF | -: -; -: -; REQ: REQ; F: F; I.S: N.I.S | DO |  | 42 | SGS | [6 empty] | 01
HCR | HCR-XL-112 | HCR-X-112 | HCR | C&E/693 | ANNUNCIATOR - LAMP | HCR ALARM ANNUN. | 083.2 | LOOP REACTOR CRASH COOL | -: -; -: -; REQ: REQ; F: F; I.S: N.I.S | DO |  | 42 | SGS | [6 empty] | 01
HTF01 | HTF01-CV-001 | HTF01-C-001 | FLD | 107-MA | GLOBE VALVE - CONTROL - F.C. | 100-HT-CS3A-C-9029400 | 040.2 | COLD HTF RTN | 6445 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | SAMSON | 241-7 / 3767-1 | KV0001 | TI702-SP-5053 |  |  | 01
HTF01 | HTF01-CV-002 | HTF01-C-002 | FLD | 108-GB | GLOBE VALVE - CONTROL - F.C. | 100-HT-CS3A-C-9029412 | 040.2 | GP2 COLD HTF BYPASS | 6446 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
HTF01 | HTF01-CV-003 | HTF01-C-003 | FLD | 107-MA | GLOBE VALVE - ON/OFF - STAYPUT | 80-HT-CS3A-C-9027325 | 040.2 | CV-001 BYPASS | 6774 | - | - | REF | REQ | F | [5 empty] | 0 |  | SAMSON | 241-7 | KV0001 |  |  |  | 01
HTF01 | HTF01-CY-003 | HTF01-C-003 | FLD | 107-MA | SOLENOID VALVE | RACK MOUNTED |  | CV-001 BYPASS | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
HTF01 | HTF01-ZSC-003 | HTF01-C-003 | FLD | 107-MA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CV-001 BYPASS | I.S: I.S; DI: DI |  |  | 31 | UTIL | SAMSON | 3768-12000010.03 |  | TI702-SP-5110 |  |  | 01
HTF01 | HTF01-ZSO-003 | HTF01-C-003 | FLD | 107-MA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CV-001 BYPASS | I.S: I.S; DI: DI |  |  | 31 | UTIL | SAMSON | 3768-12000010.03 |  | TI702-SP-5110 |  |  | 01
HTF01 | HTF01-DIC-001 | HTF01-D-001 | PCS | 107-MA | INDICATING CONTR. - MOTOR DRIVE |  |  | CP1 COLD HTF SUPPLY PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-DS-001 | HTF01-D-001 | MCC | 107-MA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | CP1 COLD HTF SUPPLY PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DY-001 | HTF01-D-001 | MCC | 107-MA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | CP1 COLD HTF SUPPLY PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DYC-001 | HTF01-D-001 | MCC | 107-MA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 040.1 | CP1 COLD HTF SUPPLY PUMP | 8659 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
HTF01 | HTF01-DIC-002 | HTF01-D-002 | PCS | 107-MA | INDICATING CONTR. - MOTOR DRIVE |  |  | CP2 COLD HTF SUPPLY PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-DS-002 | HTF01-D-002 | MCC | 107-MA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | CP2 COLD HTF SUPPLY PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DY-002 | HTF01-D-002 | MCC | 107-MA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | CP2 COLD HTF SUPPLY PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DYC-002 | HTF01-D-002 | MCC | 107-MA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 040.1 | CP2 COLD HTF SUPPLY PUMP | 8660 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
HTF01 | HTF01-DIC-003 | HTF01-D-003 | PCS | 107-MA | INDICATING CONTR. - MOTOR DRIVE |  |  | CP3 REFRIG PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-DS-003 | HTF01-D-003 | MCC | 107-MA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | CP3 REFRIG PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DY-003 | HTF01-D-003 | MCC | 107-MA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | CP3 REFRIG PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DYC-003 | HTF01-D-003 | MCC | 107-MA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 040.1 | CP3 REFRIG PUMP | 8661 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
HTF01 | HTF01-DIC-004 | HTF01-D-004 | PCS | 107-MA | INDICATING CONTR. - MOTOR DRIVE |  |  | CP4 REFRIG PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-DS-004 | HTF01-D-004 | MCC | 107-MA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | CP4 REFRIG PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DY-004 | HTF01-D-004 | MCC | 107-MA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | CP4 REFRIG PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DYC-004 | HTF01-D-004 | MCC | 107-MA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 040.1 | CP4 REFRIG PUMP | 8662 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
HTF01 | HTF01-DIC-005 | HTF01-D-005 | PCS | 107-MA | INDICATING CONTR. - MOTOR DRIVE |  |  | CP5 REFRIG PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-DS-005 | HTF01-D-005 | MCC | 107-MA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | CP5 REFRIG PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DY-005 | HTF01-D-005 | MCC | 107-MA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | CP5 REFRIG PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF01 | HTF01-DYC-005 | HTF01-D-005 | MCC | 107-MA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 040.1 | CP5 REFRIG PUMP | 8663 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
HTF01 | HTF01-DS-006 | HTF01-D-006 | PCS/MCC | 107-MA | Pump CP6 auto available signal | PCS/MCC |  | RU3 HTF supply pump CP6 | PKG: 13131 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-DY-006 | HTF01-D-006 | PCS/MCC | 107-MA | Pump CP6 running signal | PCS/MCC |  | RU3 HTF supply pump CP6 | PKG: 13131 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-DYC-006 | HTF01-D-006 | PCS/MCC | 107-MA | Pump CP6 enable signal | PCS/MCC | 040.1 | RU3 HTF supply pump CP6 | PKG: 13131 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-FIC-001 | HTF01-F-001 | PCS | 107-MA | INDICATING CONTROLLER - FLOW |  |  | COLD HTF SUPPLY FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-FT-001 | HTF01-F-001 | FLD | 107-MA | TRANSMITTER - FLOW | 150-HT-CS3A-C-9027305 | 040.2 | COLD HTF SUPPLY FLOW | 8242 | 50 to 150 m3/hr | +/- 2% | REF | 5 YR | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | 77FS1HJA211B04 | KF0008 | TI702-SP-5111 |  |  | 01
HTF01 | HTF01-FI-002A | HTF01-F-002 | PCS | 107-MA | INDICATOR - FLOW |  |  | HTF TO RU1 | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-FI-002B | HTF01-F-002 | FLD | 107-MA | INDICATOR - FLOW | ADJ COLD HTF PUMPS | 040.1 | HTF TO RU1 |  | 0 to 200 m3/hr | +/- 2% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324D |  |  |  |  | 01
HTF01 | HTF01-FT-002 | HTF01-F-002 | FLD | 107-MA | TRANSMITTER - FLOW | 150-HT-CS3A-C-9027312 | 040.1 | HTF TO RU1 | 11128 | 0 to 200 m3/hr | +/- 2% | REF | 5 YR | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | 77FS1FJA211Q04 | KF0008/P | TI702-SP-5111 |  |  | 01
HTF01 | HTF01-FI-003A | HTF01-F-003 | PCS | 107-MA | VA FLOW METER |  |  | HTF TO RU2 | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-FI-003B | HTF01-F-003 | FLD | 107-MA | VA FLOW METER | ADJ COLD HTF PUMPS | 040.1 | HTF TO RU2 | -: 0 to 200 m3/hr; -: +/- 2%; REQ: REQ; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324D |  |  |  |  | 01
HTF01 | HTF01-FT-003 | HTF01-F-003 | FLD | 107-MA | TRANSMITTER - FLOW | 150-HT-CS3A-C-9027313 | 040.1 | HTF TO RU2 | 11129 | 0 to 200 m3/hr | +/- 2% | REF | 5 YR | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | 77FS1FJA211Q04 | KF0008/P | TI702-SP-5111 |  |  | 01
HTF01 | HTF01-LI-001 | HTF01-L-001 | PCS | 107-MA | INDICATOR - LEVEL |  |  | ST1 COLD WELL LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-LIT-001 | HTF01-L-001 | FLD | 107-MA | TRANSMITTER - LEVEL | HTF01-ST1/L2/100 | 040.1 | ST1 COLD WELL LEVEL | 7006 | 0-9900 litres | +/- 2% | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | FMR53 | KL0028 | TI702-SP-5108 |  |  | 47
HTF01 | HTF01-LI-002 | HTF01-L-002 | PCS | 107-MA | INDICATOR - LEVEL |  |  | ST1 HOT WELL LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-LIT-002 | HTF01-L-002 | FLD | 107-MA | TRANSMITTER - LEVEL | HTF01-ST1/L1/100 | 040.1 | ST1 HOT WELL LEVEL | 6712 | 0-8600 litres | +/- 2% | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | FMR53 | KL0028 | TI702-SP-5108 |  |  | 47
HTF01 | HTF01-PI-001 | HTF01-P-001 | FLD | 107-MA | PRESSURE GAUGE - DIAPHRAGM | 25-HT-CS3A-C-9027324 | 040.1 | ST1 PRESSURE | -: 0 to 1 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006 |  |  |  | 01
HTF01 | HTF01-PI-002 | HTF01-P-002 | FLD | 107-MA | PRESSURE GAUGE - DIAPHRAGM | 150-HT-CS3A-C-9027303 | 040.1 | CP1 PUMP DISCHARGE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
HTF01 | HTF01-PI-003 | HTF01-P-003 | FLD | 107-MA | PRESSURE GAUGE - DIAPHRAGM | 150-HT-CS3A-C-9027304 | 040.1 | CP2 PUMP DISCHARGE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
HTF01 | HTF01-PDI-004 | HTF01-P-004 | FLD | 107-MA | DIFF PRESS GAUGE - DIAPHRAGM | HTF01-CP3 INLET/OUTLET | 040.1 | CP3 PUMP DIFFERENTIAL | -: 0 to 4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | BOURDON SEDEME | MDX7A30B19B20 | KP0006/P1 |  |  |  | 01
HTF01 | HTF01-PDI-005 | HTF01-P-005 | FLD | 107-MA | DIFF PRESS GAUGE - DIAPHRAGM | HTF01-CP4 INLET/OUTLET | 040.1 | CP4 PUMP DIFFERENTIAL | -: 0 to 4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | BOURDON SEDEME | MDX7A30B19B20 | KP0006/P1 |  |  |  | 01
HTF01 | HTF01-PDI-006 | HTF01-P-006 | FLD | 107-MA | DIFF PRESS GAUGE - DIAPHRAGM | HTF01-CP5 INLET/OUTLET | 040.1 | CP5 PUMP DIFFERENTIAL | -: 0 to 4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | BOURDON SEDEME | MDX7A30B19B20 | KP0006/P1 |  |  |  | 01
HTF01 | HTF01-PRV-008 | HTF01-P-008 | FLD | 107-MA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028849 | 040.1 | N2 SUPPLY | -: set @ 50mbarg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | BROADY | C3-L | KS0007 |  |  |  | 01
HTF01 | HTF01-PIC-009 | HTF01-P-009 | PCS | 107-MA | INDICATING CONTROLLER - PRESSURE |  |  | COLD HTF RTN PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-PIT-009 | HTF01-P-009 | FLD | 107-MA | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-HT-CS3A-C-9029400 | 040.2 | COLD HTF RTN PRESSURE | 6711 | 0 to 3 barg | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | UTIL | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5109 |  |  | 01
HTF01 | HTF01-PSV-010 | HTF01-P-010 | FLD | 107-MA | PRESSURE RELIEF VALVE | 80-HT-CS3A-C-9027323 | 040.1 | ST1 RELIEF | -: 3 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531J-C-B000 | KS0001 |  |  |  | 01
HTF01 | HTF01-PSV-011 | HTF01-P-011 | FLD | 107-MA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9027330 | 040.2 | COLD HTF RTN RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
HTF01 | HTF01-PSV-012 | HTF01-P-012 | FLD | 107-MC | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9027393 | 040.1 | RU1 COLD HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2532D-CB-000 | KS0001 |  |  |  | 01
HTF01 | HTF01-PSV-013 | HTF01-P-013 | FLD | 107-MC | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9027384 | 040.1 | RU2 COLD HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2532D-CB-000 | KS0001 |  |  |  | 01
HTF01 | HTF01-PI-016 | HTF01-P-016 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-PI-017 | HTF01-P-017 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-PI-018 | HTF01-P-018 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-PI-019 | HTF01-P-019 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-RO-001 | HTF01-R-001 | FLD | 108-GA | RESTRICTION ORIFICE PLATE | 100-HT-CS3A-C-902303 | 040.2 | GP1 COLD HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF01 | HTF01-RO-002 | HTF01-R-002 | FLD | 108-GB | RESTRICTION ORIFICE PLATE | 100-HT-CS3A-C-9029402 | 040.2 | GP2 COLD HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF01 | HTF01-RO-003 | HTF01-R-003 | FLD | 108-GB | RESTRICTION ORIFICE PLATE | 100-HT-CS3A-C-9029410 | 040.2 | GP2 COLD HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF01 | HTF01-RV-004 | HTF01-R-004 | FLD | 107-MA | PRESSURE VENT | 25-HT-CS3A-C-9027324 | 040.1 | ST1 RELIEF | -: 100 mbarg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | GROTH |  | KS0004 |  |  |  | 01
HTF01 | HTF01-RO-005 | HTF01-R-005 | FLD | 108-GD | RESTRICTION ORIFICE PLATE | 100-HT-CS3A-C-9029305 | 040.2 | C1 COLD HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF01 | HTF01-RO-006 | HTF01-R-006 | FLD | 108-GD | RESTRICTION ORIFICE PLATE | 100-HT-CS3A-D-9029407 | 040.2 | C1 COLD HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF01 | HTF01-RU4-AAH-002A | HTF01-RU4-A-002A | bar: PKG
HTF01 | HTF01-RU4-AAH-002B | HTF01-RU4-A-002B | bar: PKG
HTF01 | HTF01-SP-005 | HTF01-S-005 | MCC | 107-MA | DRIVE SPEED | MOTOR CONTROL CENTRE |  | CP5 COLD HTF TO RU1 and 2 | [13 empty] | DANFOSS | [5 empty] | 19 | bar: PKG
HTF01 | HTF01-SP-006 | HTF01-S-006 | MCC | 107-MA | DRIVE SPEED | MOTOR CONTROL CENTRE |  | CP5 COLD HTF TO RU3 | [13 empty] | DANFOSS | [5 empty] | 19 | bar: PKG
HTF01 | HTF01-SGS-RU4-AAH-001A | HTF01-SGS-RU4-A-001 | bar: PKG
HTF01 | HTF01-SGS-RU4-AAH-001B | HTF01-SGS-RU4-A-001B | bar: PKG
HTF01 | HTF01-SGS-RU4-AAH-003A | HTF01-SGS-RU4-A-003A | bar: PKG
HTF01 | HTF01-SGS-RU4-AAH-003B | HTF01-SGS-RU4-A-003B | bar: PKG
HTF01 | HTF01-TW-001 | HTF01-T-001 | FLD | 107-MA | THERMOWELL | 250-HT-CS3A-C-9027318 |  | HTF TEST WELL | -: 0.07% |  |  | 0 |  | Moore Industries |  | KT0004 |  |  |  | 01
HTF01 | HTF01-TW-002 | HTF01-T-002 | FLD | 107-MA | THERMOWELL | 250-HT-CS3A-C-9027307 |  | HTF TEST WELL | -: 0.07% |  |  | 0 |  | Moore Industries |  | KT0004 |  |  |  | 01
HTF01 | HTF01-TW-003 | HTF01-T-003 | FLD | 107-MA | THERMOWELL | 150-HT-CS3A-C-9027300 |  | HTF TEST WELL | -: 0.07% |  |  | 0 |  | Moore Industries |  | KT0004 |  |  |  | 01
HTF01 | HTF01-TE-004 | HTF01-T-004 | FLD | 107-MA | ELEMENT - TEMPERATURE - RTD | 150-HT-CS3A-C-9027305 |  | COLD HTF SUPPLY TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TI-004 | HTF01-T-004 | PCS | 107-MA | INDICATOR - TEMPERATURE |  |  | COLD HTF SUPPLY TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TT-004 | HTF01-T-004 | FLD | 107-MA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.1 | COLD HTF SUPPLY TEMP. | 6612 | -30 to 70 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 01
HTF01 | HTF01-TE-005 | HTF01-T-005 | FLD | 107-MA | ELEMENT - TEMPERATURE - RTD | 150-HT-CS3A-C-9029400 |  | COLD HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TI-005 | HTF01-T-005 | PCS | 107-MA | INDICATOR - TEMPERATURE |  |  | COLD HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TT-005 | HTF01-T-005 | FLD | 107-MA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.2 | COLD HTF RTN TEMPERATURE | 6613 | -30 to 170 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 01
HTF01 | HTF01-TE-007 | HTF01-T-007 | FLD | 107-MC | ELEMENT - TEMPERATURE - RTD | 150-HT-CS3A-C-9027312 |  | RU1 COLD HTF RTN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TI-007 | HTF01-T-007 | PCS | 107-MC | INDICATOR - TEMPERATURE |  |  | RU1 COLD HTF RTN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TT-007 | HTF01-T-007 | FLD | 107-MC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.1 | RU1 COLD HTF RTN | 6617 | -30 to 40 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG | KT0004 |  |  |  | 01
HTF01 | HTF01-TE-008 | HTF01-T-008 | FLD | 107-MC | ELEMENT - TEMPERATURE - RTD | 150-HT-CS3A-C-9027390 |  | RU1 COLD HTF SUPPLY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TI-008 | HTF01-T-008 | PCS | 107-MC | INDICATOR - TEMPERATURE |  |  | RU1 COLD HTF SUPPLY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TT-008 | HTF01-T-008 | FLD | 107-MC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.1 | RU1 COLD HTF SUPPLY | 6618 | -40 to 40 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG | KT0004 |  |  |  | 01
HTF01 | HTF01-TE-009 | HTF01-T-009 | FLD | 107-MC | ELEMENT - TEMPERATURE - RTD | 150-HT-CS3A-C-9027313 |  | RU2 COLD HTF RTN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TI-009 | HTF01-T-009 | PCS | 107-MC | INDICATOR - TEMPERATURE |  |  | RU2 COLD HTF RTN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TT-009 | HTF01-T-009 | FLD | 107-MC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.1 | RU2 COLD HTF RTN | 6619 | -30 to 40 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG | KT0004 |  |  |  | 01
HTF01 | HTF01-TE-010 | HTF01-T-010 | FLD | 107-MC | ELEMENT - TEMPERATURE - RTD | 150-HT-CS3A-C-9027380 |  | RU2 COLD HTF SUPPLY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TI-010 | HTF01-T-010 | PCS | 107-MC | INDICATOR - TEMPERATURE |  |  | RU2 COLD HTF SUPPLY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF01 | HTF01-TT-010 | HTF01-T-010 | FLD | 107-MC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.1 | RU2 COLD HTF SUPPLY | 6620 | -40 to 40 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG | KT0004 |  |  |  | 01
HTF01 | HTF01-TAH-011 | HTF01-T-011 | PCS | 107-MA | PCS high temperature alarm | PCS |  | RU3 HTF return temperature | PKG: 13075 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TAHH-011 | HTF01-T-011 | PCS | 107-MA | PCS high high temperature alarm | PCS |  | RU3 HTF return temperature | PKG: 13075 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TAL-011 | HTF01-T-011 | PCS | 107-MA | PCS low temperature alarm | PCS |  | RU3 HTF return temperature | PKG: 13075 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TALL-011 | HTF01-T-011 | PCS | 107-MA | PCS low low temperature alarm | PCS |  | RU3 HTF return temperature | PKG: 13075 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TE-011 | HTF01-T-011 | FLD | 107-MA | Temperature element | 150-HTR-CS3A-C-9027363 | 040.1 | RU3 HTF return temperature | PKG: 13075; -: -30 to 40oC |  |  |  |  | ROSEMOUNT | Pt-100_385 3 wire |  |  |  |  | 01
HTF01 | HTF01-TI-011 | HTF01-T-011 | PCS | 107-MA | PCS temperature indication | PCS |  | RU3 HTF return temperature | PKG: 13075; -: -30 to 40oC |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TT-011 | HTF01-T-011 | FLD | 107-MA | Temperature transmitter | 150-HTR-CS3A-C-9027363 | 040.1 | RU3 HTF return temperature | PKG: 13075; -: -30 to 40oC |  |  |  |  | ROSEMOUNT | 644HANAXAM5C4Q4 |  |  |  |  | 01
HTF01 | HTF01-TAH-012 | HTF01-T-012 | PCS | 107-MA | PCS high temperature alarm | PCS |  | RU3 HTF supply temperature | PKG: 13076 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TAHH-012 | HTF01-T-012 | PCS | 107-MA | PCS high high temperature alarm | PCS |  | RU3 HTF supply temperature | PKG: 13076 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TAL-012 | HTF01-T-012 | PCS | 107-MA | PCS low temperature alarm | PCS |  | RU3 HTF supply temperature | PKG: 13076 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TALL-012 | HTF01-T-012 | PCS | 107-MA | PCS low low temperature alarm | PCS |  | RU3 HTF supply temperature | PKG: 13076 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TE-012 | HTF01-T-012 | FLD | 107-MA | Temperature element | 150-HTF-CS3A-C-9027334 | 040.1 | RU3 HTF supply temperature | PKG: 13076; -: -40 to 40oC |  |  |  |  | ROSEMOUNT | Pt-100_385 3 wire |  |  |  |  | 01
HTF01 | HTF01-TI-012 | HTF01-T-012 | PCS | 107-MA | PCS temperature indication | PCS |  | RU3 HTF supply temperature | PKG: 13076; -: -40 to 40oC |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-TT-012 | HTF01-T-012 | FLD | 107-MA | Temperature transmitter | 150-HTF-CS3A-C-9027334 | 040.1 | RU3 HTF supply temperature | PKG: 13076; -: -40 to 40oC |  |  |  |  | ROSEMOUNT | 644HANAXAM5C4Q4 |  |  |  |  | 01
HTF01 | HTF01-TE-013 | HTF01-T-013 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TI-013 | HTF01-T-013 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TT-013 | HTF01-T-013 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TE-014 | HTF01-T-014 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TI-014 | HTF01-T-014 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TT-014 | HTF01-T-014 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TE-015 | HTF01-T-015 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TI-015 | HTF01-T-015 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TT-015 | HTF01-T-015 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TE-016 | HTF01-T-016 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TI-016 | HTF01-T-016 | [6 empty] | REF: REF; REQ: By request
HTF01 | HTF01-TT-016 | HTF01-T-016 | [6 empty] | REF: REF; REQ: By request
HTF02 | HTF02-CV-001 | HTF02-C-001 | FLD | 107-MB | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-C-9027306 | 040.1 | ST1 COLD HTF INLET | 7128 | - | - | REF | REQ | F | [5 empty] | 0 |  | WORCESTER | 52E | KV0017 |  |  |  | 01
HTF02 | HTF02-CY-001 | HTF02-C-001 | FLD | 107-MB | SOLENOID VALVE | RACK MOUNTED |  | ST1 COLD HTF INLET | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
HTF02 | HTF02-ZSC-001 | HTF02-C-001 | FLD | 107-MB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ST1 COLD HTF INLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
HTF02 | HTF02-ZSO-001 | HTF02-C-001 | FLD | 107-MB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ST1 COLD HTF INLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
HTF02 | HTF02-CV-002 | HTF02-C-002 | FLD | 107-MB | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9029150 | 040.3 | ST1 HOT HTF RTN | 6447 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | SAMSON | 241-7 / 3767-1 | KV0001 | TI702-SP-5053 |  |  | 01
HTF02 | HTF02-CV-003 | HTF02-C-003 | FLD | 107-MB | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9027408 | 040.1 | HOT HTF TO HTF01 | 7123 | - | - | REF | REQ | F | [5 empty] | 0 |  | WORCESTER | 52E | KV0017 |  |  |  | 01
HTF02 | HTF02-CY-003 | HTF02-C-003 | FLD | 107-MB | SOLENOID VALVE | RACK MOUNTED |  | HOT HTF TO HTF01 | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
HTF02 | HTF02-ZSC-003 | HTF02-C-003 | FLD | 107-MB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF TO HTF01 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
HTF02 | HTF02-ZSO-003 | HTF02-C-003 | FLD | 107-MB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF TO HTF01 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
HTF02 | HTF02-CV-004 | HTF02-C-004 | FLD | 107-MB | GLOBE VALVE - CONTROL - F.C. | 80-SLP-CS1A-HC-9028030 | 023.0 | HU1 STEAM SUPPLY | 6767 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | SAMSON | 241-7 / 3767-1 | KV0001 | TI702-SP-5053 |  |  | 01
HTF02 | HTF02-CV-005 | HTF02-C-005 | FLD | 108-FB | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9029170 | 040.3 | HOT HTF BYPASS | 6448 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | SAMSON | 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
HTF02 | HTF02-CV-006 | HTF02-C-006 | FLD | 107-MB | GLOBE VALVE - ON/OFF - STAYPUT | 50-HT-CS3A-D-9027422 | 040.3 | CV-002 BYPASS | 6775 | - | - | REF | REQ | F | [5 empty] | 0 |  | SAMSON | 241-7 | KV0001 |  | SPRING TO CLOSE |  | 01
HTF02 | HTF02-CY-006 | HTF02-C-006 | FLD | 107-MB | SOLENOID VALVE | RACK MOUNTED |  | CV-002 BYPASS | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
HTF02 | HTF02-ZSC-006 | HTF02-C-006 | FLD | 107-MB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CV-002 BYPASS | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
HTF02 | HTF02-ZSO-006 | HTF02-C-006 | FLD | 107-MB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CV-002 BYPASS | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
HTF02 | HTF02-DIC-001 | HTF02-D-001 | PCS | 107-MB | INDICATING CONTR. - MOTOR DRIVE |  |  | CP1 HOT HTF SUPPLY PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-DS-001 | HTF02-D-001 | MCC | 107-MB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | CP1 HOT HTF SUPPLY PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF02 | HTF02-DY-001 | HTF02-D-001 | MCC | 107-MB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | CP1 HOT HTF SUPPLY PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF02 | HTF02-DYC-001 | HTF02-D-001 | MCC | 107-MB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 040.1 | CP1 HOT HTF SUPPLY PUMP | 8664 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
HTF02 | HTF02-DIC-002 | HTF02-D-002 | PCS | 107-MB | INDICATING CONTR. - MOTOR DRIVE |  |  | CP2 HOT HTF SUPPLY PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-DS-002 | HTF02-D-002 | MCC | 107-MB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | CP2 HOT HTF SUPPLY PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF02 | HTF02-DY-002 | HTF02-D-002 | MCC | 107-MB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | CP2 HOT HTF SUPPLY PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
HTF02 | HTF02-DYC-002 | HTF02-D-002 | MCC | 107-MB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 040.1 | CP2 HOT HTF SUPPLY PUMP | 8665 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
HTF02 | HTF02-FIC-001 | HTF02-F-001 | PCS | 107-MB | INDICATING CONTROLLER - FLOW |  |  | HOT HTF SUPPLY FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-FT-001 | HTF02-F-001 | FLD | 107-MB | TRANSMITTER - FLOW | 100-HT-CS3A-D-9027405 | 040.1 | HOT HTF SUPPLY FLOW | 8243 | 0 to 90 m3/hr | +/- 2% | REF | 5 YR | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | 77FS1HJA211B04 | KF0008 | TI702-SP-5111 |  |  | 01
HTF02 | HTF02-LIC-001 | HTF02-L-001 | PCS | 107-MB | INDICATING CONTROLLER - LEVEL |  |  | ST1 LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-LIT-001 | HTF02-L-001 | FLD | 107-MB | TRANSMITTER - LEVEL | HTF02-ST1/L1/100 | 040.1 | ST1 LEVEL | 6713 | 0-3200 litres | +/- 2% | REF | 2 YR | C |  | I.S | AI |  |  | 11 | UTIL | FOXBORO | 143DP | KP0001 | TI702-SP-5109 |  |  | 01
HTF02 | HTF02-LAH-002 | HTF02-L-002 | PCS | 107-MB | ALARM - LEVEL - HIGH |  |  | ST1 HIGH LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-LSH-002 | HTF02-L-002 | FLD | 107-MB | SWITCH - LEVEL - HIGH | ST1/L2/100 | 040.1 | ST1 HIGH LEVEL | 6718 | Fixed | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MEGGIT MOBERY | DS3FR4N1PH8/66 | KL0005 | TI702-SP-5113 |  |  | 01
HTF02 | HTF02-PIC-001 | HTF02-P-001 | PCS | 107-MB | INDICATING CONTROLLER - PRESSURE |  |  | HOT HTF RTN PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-PIT-001 | HTF02-P-001 | FLD | 107-MB | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-HT-CS3A-D-9029150 | 040.3 | HOT HTF RTN PRESSURE | 6714 | 0 to 3 barg | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | UTIL | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5109 |  |  | 01
HTF02 | HTF02-PI-002 | HTF02-P-002 | FLD | 107-MB | PRESSURE GAUGE - DIAPHRAGM | DELETED | 040.1 | CP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 19
HTF02 | HTF02-PIT-002 | HTF02-P-002 | FLD | 107-MB | PRESSURE TRANSMITTER - DIAPHRAGM | 100-HT-CS3A-D-9027403 | 040.1 | CP1 DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C |  | I.S | AI |  |  | 0 | UTIL | ROSEMOUNT | 2088 | KP0001 | TI702-SP-5112 |  |  | 19
HTF02 | HTF02-PI-003 | HTF02-P-003 | FLD | 107-MB | PRESSURE GAUGE - DIAPHRAGM | 100-HT-CS3A-D-9027404 | 040.1 | CP2 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
HTF02 | HTF02-PI-004 | HTF02-P-004 | FLD | 107-MB | PRESSURE GAUGE - STEAM SYPHON | 100-SLP-CS1A-HC-9028030 | 040.1 | HU1 STEAM SUPPLY PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 (Note 2) | KP0006/3 |  |  |  | 01
HTF02 | HTF02-PI-005 | HTF02-P-005 | FLD | 107-MB | PRESSURE GAUGE - DIAPHRAGM | DELETED | 040.1 | HU1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 19
HTF02 | HTF02-PIT-005 | HTF02-P-005 | FLD | 107-MB | PRESSURE TRANSMITTER - DIAPHRAGM | 100-HT-CS3A-D-9027406 | 040.1 | CP1 DISCHARGE PRESSURE |  | 0 to 10 barg | +/- 5% | REF | REQ | C |  | I.S | AI |  |  | 0 | UTIL | ROSEMOUNT | 2088 | KP0001 | TI702-SP-5112 |  |  | 19
HTF02 | HTF02-PSV-008 | HTF02-P-008 | FLD | 107-MB | PRESSURE RELIEF VALVE | 40-HT-CS3A-D-9027414 | 040.1 | ST1 RELIEF | -: 3 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531F-C-B000 | KS0001 |  |  |  | 01
HTF02 | HTF02-PSV-010 | HTF02-P-010 | FLD | 107-MB | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9027418 | 040.1 | HU1 HOT HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
HTF02 | HTF02-PI-011 | HTF02-P-011 | FLD | 107-MB | PRESSURE GAUGE - DIAPHRAGM | 25-HT-CS3A-D-9027414 | 040.1 | ST1 PRESSURE | -: 0 to 1 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006 |  |  |  | 01
HTF02 | HTF02-RO-001 | HTF02-R-001 | FLD | 108-FA | RESTRICTION ORIFICE PLATE | 80-HT-CS3A-D-9029109 | 040.3 | GP1 HOT HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF02 | HTF02-RO-002 | HTF02-R-002 | FLD | 108-FB | RESTRICTION ORIFICE PLATE | 80-HT-CS3A-D-9029161 | 040.3 | GP2 HOT HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF02 | HTF02-RO-003 | HTF02-R-003 | FLD | 108-FB | RESTRICTION ORIFICE PLATE | 80-HT-CS3A-D-9029168 | 040.3 | GP2 HOT HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF02 | HTF02-RO-005 | HTF02-R-005 | FLD | 108-FD | RESTRICTION ORIFICE PLATE | 80-HT-CS3A-D-9029250 | 040.3 | C1 HOT HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF02 | HTF02-RO-006 | HTF02-R-006 | FLD | 108-FD | RESTRICTION ORIFICE PLATE | 80-HT-CS3A-D-9029257 | 040.3 | C1 HOT HTF MIN BYPASS | -: 1.5 m3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
HTF02 | HTF02-RO-007 | HTF02-R-007 | FLD | 107-MB | RESTRICTION ORIFICE PLATE | 40-HT-CS3A-D-9027306 | 040.1 | COLD HTF SUPPLY | -: 2100 kg/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | SITE FAB | N/A |  |  |  |  | 01
HTF02 | HTF02-RO-008 | HTF02-R-008 | FLD | 107-MB | RESTRICTION ORIFICE PLATE | 40-HT-CS3A-D-9027408 | 040.1 | HOT HTF SUPPLY | -: 2100 kg/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | SITE FAB | N/A |  |  |  |  | 01
HTF02 | HTF02-SP-001 | HTF02-S-001 | MCC | 107-MB | DRIVE SPEED | MOTOR CONTROL CENTRE |  | CP1 HOT HTF SUPPLY PUMP | I.S: N.I.S; DI: AO |  |  | 21 | UTIL | DANFOSS | [5 empty] | 19
HTF02 | HTF02-SP-002 | HTF02-S-002 | MCC | 107-MB | DRIVE SPEED | MOTOR CONTROL CENTRE |  | CP2 HOT HTF SUPPLY PUMP | I.S: N.I.S; DI: AO |  |  | 21 | UTIL | DANFOSS | [5 empty] | 19
HTF02 | HTF02-TI-001 | HTF02-T-001 | FLD | 107-MB | INDICATOR - TEMPERATURE | HTF02-ST1/T1 | 040.1 | ST1 TEMPERATURE | -: 0 to 200 degC; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | S5550/4 | KT0003 |  |  |  | 01
HTF02 | HTF02-TE-002 | HTF02-T-002 | FLD | 107-MB | ELEMENT - TEMPERATURE - RTD | 100-HT-CS3A-D-9027405 |  | CP1/2 OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-TI-002 | HTF02-T-002 | PCS | 107-MB | INDICATOR - TEMPERATURE |  |  | CP1/2 OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-TT-002 | HTF02-T-002 | FLD | 107-MB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.1 | CP1/2 OUTLET TEMPERATURE | 6614 | -30 to 170 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 01
HTF02 | HTF02-TE-003 | HTF02-T-003 | FLD | 107-MB | ELEMENT - TEMPERATURE - RTD | 100-HT-CS3A-D-9027406 |  | HOT HTF SUPPLY TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
HTF02 | HTF02-TIC-003 | HTF02-T-003 | PCS | 107-MB | INDICATING CONTROLLER - TEMPERATURE |  |  | HOT HTF SUPPLY TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
HTF02 | HTF02-TT-003 | HTF02-T-003 | FLD | 107-MB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.1 | HOT HTF SUPPLY TEMP. | 6615 | -30 to 170 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 01
HTF02 | HTF02-TI-004 | HTF02-T-004 | FLD | 107-MB | INDICATOR - TEMPERATURE | 100-HT-CS3A-D-9027406 | 040.1 | HOT HTF SUPPLY TEMP. | -: 0 to 200 degC; -: +/- 2%; REF: SHE; REQ: REQ; F: C |  |  | 0 |  | WIKA | S5550/4 | KT0003 |  |  |  | 01
HTF02 | HTF02-TE-005 | HTF02-T-005 | FLD | 107-MB | ELEMENT - TEMPERATURE - RTD | 100-HT-CS3A-D-9029150 |  | HOT HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-TI-005 | HTF02-T-005 | PCS | 107-MB | INDICATOR - TEMPERATURE |  |  | HOT HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
HTF02 | HTF02-TT-005 | HTF02-T-005 | FLD | 107-MB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.3 | HOT HTF RTN TEMPERATURE | 6616 | -30 to 170 degC | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 01
HTF01 | HTF01-FAH-004 | HTF-F-004 | PCS | 107-MA | PCS high flow alarm | PCS |  | RU3 HTF flow | PKG: 13077 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-FAHH-004 | HTF-F-004 | PCS | 107-MA | PCS high high flow alarm | PCS |  | RU3 HTF flow | PKG: 13077 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-FAL-004 | HTF-F-004 | PCS | 107-MA | PCS low flow alarm | PCS |  | RU3 HTF flow | PKG: 13077 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-FALL-004 | HTF-F-004 | PCS | 107-MA | PCS low low flow alarm | PCS |  | RU3 HTF flow | PKG: 13077 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-FI-004A | HTF-F-004 | PCS | 107-MA | Flow PCS indication | PCS |  | RU3 HTF flow | PKG: 13077; -: 40 - 200 m3/hr |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
HTF01 | HTF01-FI-004B | HTF-F-004 | FLD | 107-MA | Flow local indication | External | 040.1 | RU3 HTF flow | PKG: 13077; -: 40 - 200 m3/hr |  |  |  |  | BEKA | BA324D |  |  |  |  | 01
HTF01 | HTF01-FT-004 | HTF-F-004 | FLD | 107-MA | Flow transmitter | 150-HTF-CS3A-C-9027334 | 040.1 | RU3 HTF flow | PKG: 13077; -: 40 - 200 m3/hr; I.S: I.S; DI: AI |  |  |  | UTIL | ENDRESS + HAUSER | Prowirl 72F1F-SM0AARDAA4AA | KF0008/P1 | TI702-SP-5148 |  |  | 01
HTF01 | HTF01-FY-004 | HTF-F-004 | PCS | 107-MA | IS barrier | PCS |  | RU3 HTF flow | PKG: 13077 |  |  |  |  | PEPPERL + FUCHS | KFD0-SCS-Ex1.55 |  |  |  |  | 01
HTFMCC | HTFMCC-KWH-001 | HTFMCC-K-001 | PLC | N/A | POWER TOTALISER | HVAC MCC |  | HTF MCC Kw/h | I.S: N.I.S |  |  | 0 | [5 empty] | PULSED INPUT | AI | 01
HTF01 | HTF01-PDI-007 | HTF-P-007 | FLD | 107-MA | Differential pressure gauge | 150-HTF-CS3A-C-9027334 | 040.1 | HTF01-CP6 differential pressure gauge | PKG: 13078; -: 0 to 4 Barg |  |  |  |  | BOURDON SEDEME | MX7 A30 B19 G |  |  |  |  | 01
HTF01 | HTF01-PSV-014 | HTF-P-014 | FLD | 107-MA | HTF Pressure relief valve | 50-HTR-CS3A-C-9037364 | 040.1 | HTF Return Pressure relief valve | PKG: 13133; -: 10 barg |  |  |  |  | Broady | 2531D |  |  |  |  | 01
HVACMCC | HVACMCC-KWH-001 | HVACMCC-K-001 | PLC | N/A | POWER TOTALISER | HVAC MCC |  | HVAC MCC Kw/h | I.S: N.I.S |  |  | 0 | [5 empty] | PULSED INPUT | AI | 01
HYD | HYD-XA-001CM | HYD-X-001CM | CCR | C&E/693 | ALARM - AUDIBLE | CONTROL ROOM | 083.2 | H2 LEAK ALM. CONTROL ROOM | 8666 | - | - |  | REQ | F |  | I.S |  | DO |  | 42 | SGS | [6 empty] | 01
HYD | HYD-XA-001DA | HYD-X-001DA | HCR | C&E/693 | ALARM - AUDIBLE | HYDROG. CONTROL ROOM | 083.2 | H2 LEAK ALM. HYD. CONT. ROOM | 8667 | - | - |  | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24C |  | TI702-SP-5081 |  |  | 01
HYD | HYD-XA-001DB | HYD-X-001DB | FLD | C&E/693 | ALARM - AUDIBLE | HYDROG. PROCESS AREA | 083.2 | H2 LEAK ALM. HYDROG PROCESS | 8668 | - | - |  | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24C |  | TI702-SP-5081 |  |  | 01
HYD | HYD-XL-001DB | HYD-X-001DB | FLD | C&E/693 | ALARM - BEACON | HYDROG. PROCESS AREA | 083.2 | H2 LEAK ALM. HYDROG PROCESS | -: -; -: -; REQ: REQ; F: F; I.S: I.S | DO |  | 41 | SIS | COOPER MEDC | XB8-24C |  | TI702-SP-5080 |  |  | 01
HYD | HYD-XL-001DC | HYD-X-001DC | FLD | C&E/693 | ALARM - BEACON | HYDROG. ROOM DOOR | 083.2 | H2 LEAK ALM. HYDROG PROCESS | 8671 | - | - |  | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24C |  | TI702-SP-5080 |  |  | 01
HYD | HYD-XA-003DA | HYD-X-003 | HCR | C&E/693 | ALARM - AUDIBLE | HYDROG. CONTROL ROOM | 083.2 | GEN. ALM. HYDROG CONT. ROOM | 8669 | - | - |  | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24C |  | TI702-SP-5081 |  |  | 01
HYD | HYD-XA-003DB | HYD-X-003 | FLD | C&E/693 | ALARM - AUDIBLE | HYDROG. PROCESS AREA | 083.2 | GEN. ALM. HYDROG CONT. ROOM | 8670 | - | - |  | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24C |  | TI702-SP-5081 |  |  | 01
KL | KL-CV-010 | KL-C-010 | FLD | KILO | BALL VALVE - ON/OFF - F.C. | KILOLAB | KILO | KILOLAB WASTE TRANSFER | 8686 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
KL | KL-CY-010 | KL-C-010 | FLD | KILO | SOLENOID VALVE | FIELD CABINET |  | KILOLAB WASTE TRANSFER | I.S: I.S; DI: DO |  |  | 41 | UTIL | [6 empty] | 01
KL | KL-ZSC-010 | KL-C-010 | FLD | KILO | PROXIMITY SENSOR - CLOSED | MTD ON VALVE |  | KILOLAB WASTE TRANSFER | I.S: I.S; DI: DI |  |  | 31 | UTIL | [6 empty] | 01
KL | KL-ZSO-010 | KL-C-010 | FLD | KILO | PROXIMITY SENSOR - OPEN | MTD ON VALVE |  | KILOLAB WASTE TRANSFER | I.S: I.S; DI: DI |  |  | 31 | UTIL | [6 empty] | 01
LF01 | LF01-PDI-001 | LF01-P-001 | PKG | 107-BV | INDICATOR - DIFF PRESSURE | LF01 | 029.1 | EU8 FILTER DIFF PRESSURE | L8672 | 0 to 500 Pa | +/-25 Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDSH-001 | LF01-P-001 | PKG | 107-BV | SWITCH - PRESSURE - DIFF - HIGH | LF01 | 029.1 | EU8 FILTER DIFF PRESSURE | L8672 | 40 to 400 Pa | Actuating set point = 350Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDSL-001 | LF01-P-001 | PKG | 107-BV | SWITCH - PRESSURE - DIFF - LOW | LF01 | 029.1 | EU8 FILTER DIFF PRESSURE | L8672 | 4 to 400 Pa | Actuating set point = 90Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDI-002 | LF01-P-002 | PKG | 107-BV | INDICATOR - DIFF PRESSURE | LF01 | 029.1 | EU13 FILTER DIFF PRESSURE | L8673 | 0 to 500 pA | +/-25 Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDSH-002 | LF01-P-002 | PKG | 107-BV | SWITCH - PRESSURE - DIFF - HIGH | LF01 | 029.1 | EU13 FILTER DIFF PRESSURE | L8673 | 40 to 400 Pa | Actuating set point = 450Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDSL-002 | LF01-P-002 | PKG | 107-BV | SWITCH - PRESSURE - DIFF - LOW | LF01 | 029.1 | EU13 FILTER DIFF PRESSURE | L8673 | 4 to 400 Pa | Actuating set point = 300Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDI-003 | LF01-P-003 | PKG | 107-BV | INDICATOR - DIFF PRESSURE | LF01 | 029.1 | AIR FLOW IN DIFF PRESSURE | L8674 | 0 to 60 pA | +/-3 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDSH-003 | LF01-P-003 | PKG | 107-BV | SWITCH - PRESSURE - DIFF - HIGH | LF01 | 029.1 | AIR FLOW IN DIFF PRESSURE | L8674 | 13 to 500 Pa | Actuating set point = 52Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDSL-003 | LF01-P-003 | PKG | 107-BV | SWITCH - PRESSURE - DIFF - LOW | LF01 | 029.1 | AIR FLOW IN DIFF PRESSURE | L8674 | 13 to 500 Pa | Actuating set point = 13Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDI-004 | LF01-P-004 | PKG | 107-BV | INDICATOR - DIFF PRESSURE | LF01 | 029.1 | AIR FLOW OUT DIFF PRESSURE | L8675 | 0 to 60 pA | +/-3 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDSH-004 | LF01-P-004 | PKG | 107-BV | SWITCH - PRESSURE - DIFF - HIGH | LF01 | 029.1 | AIR FLOW OUT DIFF PRESSURE | L8675 | 13 to 500 Pa | Actuating set point = 55Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-PDSL-004 | LF01-P-004 | PKG | 107-BV | SWITCH - PRESSURE - DIFF - LOW | LF01 | 029.1 | AIR FLOW OUT DIFF PRESSURE | L8675 | 0 to 500 Pa | +/-25 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
LF01 | LF01-XA-001 | LF01-X-001 | PKG | 107-BV | ALARM - AUDIBLE | LF01 | 029.1 | COMMON ALARM | 8676 | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | FG1 | COOPER MEDC | DB5 |  | TI702-SP-5156 |  |  | 01
LF01 | LF01-XL-001 | LF01-X-001 | PKG | 107-BV | INDICATOR - LAMP | LF01 | 029.1 | COMMON ALARM |  | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | FG1 | EAO | 704.950.0 |  | TI702-SP-5155 |  |  | 01
LF01 | LF01-YA-001 | LF01-Y-001 | PCS | 107-BV | ALARM - COMMON |  |  | COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LF01 | LF01-YS-001 | LF01-Y-001 | PKG | 107-BV | COMM0N ALARM | LF01 | 029.1 | COMMON ALARM | 8672 | - | - | REF | 12 | F |  | I.S | DI |  |  | 32 | FG1 | FURNESS CONTROLS LTD | FCO54 |  | TI702-SP-5154 |  |  | 01
LF02 | LF02-HS-001 | LF02-H-001 | PKG | 107-PA | SWITCH - HAND OP. | DELETED | 029.2 | DELETED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-HS-002 | LF02-H-002 | PKG | 107-PA | SWITCH - HAND OP. | DELETED | 029.2 | DELETED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-HS-003 | LF02-H-003 | PKG | 107-PA | SWITCH - HAND OP. | DELETED | 029.2 | DELETED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-PDI-001 | LF02-P-001 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | DELETED | 029.2 | DELETED | -: 0 to 100 pA; -: +/- 1%; REF: SHE; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-PDSH-001 | LF02-P-001 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - HIGH | DELETED | 029.2 | DELETED | -: set @ commish.; -: +/- 1%; REF: SHE; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-PDSL-001 | LF02-P-001 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - LOW | DELETED | 029.2 | DELETED | -: set @ commish.; -: +/- 1%; REF: SHE; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-PDI-002 | LF02-P-002 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | DELETED | 029.2 | DELETED | -: 0 to 500 pA; -: +/- 5%; REF: SHE; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-PDSH-002 | LF02-P-002 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - HIGH | DELETED | 029.2 | DELETED | -: set @ commish.; -: +/- 5%; REF: SHE; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-PDSL-002 | LF02-P-002 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - LOW | DELETED | 029.2 | DELETED | -: set @ commish.; -: +/- 5%; REF: SHE; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-PDI-003 | LF02-P-003 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | DELETED | 029.2 | DELETED | -: 0 to 500 pA; -: +/- 5%; REF: SHE; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-PDSH-003 | LF02-P-003 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - HIGH | DELETED | 029.2 | DELETED | -: set @ commish.; -: +/- 5%; REF: SHE; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-PDSL-003 | LF02-P-003 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - LOW | DELETED | 029.2 | DELETED | -: set @ commish.; -: +/- 5%; REF: SHE; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-XA-001 | LF02-X-001 | PKG | 107-PA | ALARM - AUDIBLE | DELETED | 029.2 | DELETED | 8680 | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | UTIL |  |  |  |  | DELETED |  | 01
LF02 | LF02-XL-001 | LF02-X-001 | PKG | 107-PA | INDICATOR - LAMP | DELETED | 029.2 | DELETED |  | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | UTIL |  |  |  |  | DELETED |  | 01
LF02 | LF02-YA-001 | LF02-Y-001 | PCS | 107-PA | ALARM - COMMON | DELETED | 029.2 | DELETED | [11 empty] | 0 | [5 empty] | DELETED |  | 01
LF02 | LF02-YS-001 | LF02-Y-001 | PKG | 107-PA | COMMON ALARM | DELETED | 029.2 | DELETED | 8677 | - | - | REF | 12 | F |  | I.S | DI |  |  | 32 | UTIL |  |  |  |  | DELETED |  | 01
LF03 | LF03-HS-001 | LF03-H-001 | PKG | 107-PA | SWITCH - HAND OP. | LF03 | 029.3 | FAN STOP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | FAN STOP |  | 01
LF03 | LF03-HS-002 | LF03-H-002 | PKG | 107-PA | SWITCH - HAND OP. | LF03 | 029.3 | FAN START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | FAN START |  | 01
LF03 | LF03-HS-003 | LF03-H-003 | PKG | 107-PA | SWITCH - HAND OP. | LF03 | 029.3 | EMERGENCY STOP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | EMERGENCY STOP |  | 01
LF03 | LF03-PDI-001 | LF03-P-001 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | LF03 | 029.3 | AIR FLOW DIFF PRESSURE | L8681 | 0 to 125 Pa | +/-6 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
LF03 | LF03-PDSH-001 | LF03-P-001 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - HIGH | LF03 | 029.3 | AIR FLOW DIFF PRESSURE | L8681 | 13 to 500 Pa | Actuating set point = 80 Pa | SHE | 12 | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF03 | LF03-PDSL-001 | LF03-P-001 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - LOW | LF03 | 029.3 | AIR FLOW DIFF PRESSURE | L8681 | 13 to 500 Pa | Actuating set point = 60 Pa | SHE | 12 | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF03 | LF03-PS-001 | LF03-P-001 | FLD | 107-PA | SENSOR - PRESSURE | LF03 | 029.3 | DUCT - DIFFERENTIAL PRESSURE | -: +/- 1.5%; REF: SHE; REQ: 12; F: C | [10 empty] | 01
LF03 | LF03-PSV-001 | LF03-P-001 | FLD | 107-PA | PRESSURE SAFETY VALVE | UTILITIES AREA | 029.3 | PRESSURE | -: set @ 3 barg; -: +/- 10%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
LF03 | LF03-PDI-002 | LF03-P-002 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | LF03 | 029.3 | EU13 FILTER DIFF PRESSURE | L8682 | 0 to 500 pA | +/-25 Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF03 | LF03-PDSH-002 | LF03-P-002 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - HIGH | LF03 | 029.3 | EU13 FILTER DIFF PRESSURE | L8682 | 200 to 1000 Pa | Actuating set point = 350Pa | REF | By Request | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF03 | LF03-PDSL-002 | LF03-P-002 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - LOW | LF03 | 029.3 | EU13 FILTER DIFF PRESSURE | L8682 | 40 to 400 Pa | Actuating set point = 150 Pa | REF | By Request | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF03 | LF03-PDI-003 | LF03-P-003 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | LF03 | 029.3 | EU8 FILTER DIFF PRESSURE | L8683 | 0 to 500 pA | +/-25 Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF03 | LF03-PDSH-003 | LF03-P-003 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - HIGH | LF03 | 029.3 | EU8 FILTER DIFF PRESSURE | L8683 | 200 to 1000 Pa | Actuating set point = 350 Pa | REF | By Request | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF03 | LF03-PDSL-003 | LF03-P-003 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - LOW | LF03 | 029.3 | EU8 FILTER DIFF PRESSURE | L8683 | 40 to 400 Pa | Actuating set point = 50 Pa | REF | By Request | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF03 | LF03-TS-001 | LF03-T-001 | PKG | 107-PA | SENSOR - TEMPERATURE | LF03 | 029.3 | DUCT - TEMPERATURE | -: +/- 1.5%; REF: REF; REQ: 12; F: C | [10 empty] | 01
LF03 | LF03-XA-001 | LF03-X-001 | PKG | 107-PA | ALARM - AUDIBLE | LF03 | 029.3 | COMMON ALARM | 8684 | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | UTIL | COOPER MEDC | DB5 |  | TI702-SP-5156 |  |  | 01
LF03 | LF03-XL-001 | LF03-X-001 | PKG | 107-PA | INDICATOR - LAMP | LF03 | 029.3 | COMMON ALARM |  | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | UTIL | EAO | 704.950.0 |  | TI702-SP-5155 |  |  | 01
LF03 | LF03-YA-001 | LF03-Y-001 | PCS | 107-PA | ALARM - COMMON |  |  | COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LF03 | LF03-YS-001 | LF03-Y-001 | PKG | 107-PA | COMMON ALARM |  | 029.3 | COMMON ALARM | 8681 | - | - | REF | 12 | F |  | I.S | DI |  |  | 32 | UTIL | FURNESS CONTROLS LTD | FCO54 |  | TI702-SP-5154 |  |  | 01
LF04 | LF04-HS-001 | LF04-H-001 | PKG | 107-PA | SWITCH - HAND OP. | LF04 | 029.4 | FAN STOP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | FAN STOP |  | 01
LF04 | LF04-HS-002 | LF04-H-002 | PKG | 107-PA | SWITCH - HAND OP. | LF04 | 029.4 | FAN START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | FAN START |  | 01
LF04 | LF04-HS-003 | LF04-H-003 | PKG | 107-PA | SWITCH - HAND OP. | LF04 | 029.4 | EMERGENCY STOP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | EMERGENCY STOP |  | 01
LF04 | LF04-PDI-001 | LF04-P-001 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | LF04 | 029.4 | AIR FLOW DIFF PRESSURE | L8685 | 0 to 125 Pa | +/-6 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
LF04 | LF04-PDSH-001 | LF04-P-001 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - HIGH | LF04 | 029.4 | AIR FLOW DIFF PRESSURE | L8685 | 13 to 500 Pa | Actuating set point = 80Pa | SHE | 12 | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF04 | LF04-PDSL-001 | LF04-P-001 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - LOW | LF04 | 029.4 | AIR FLOW DIFF PRESSURE | L8685 | 13 to 500 Pa | Actuating set point = 60 Pa | SHE | 12 | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF04 | LF04-PS-001 | LF04-P-001 | FLD | 107-PA | SENSOR - PRESSURE | LF04 | 029.4 | DUCT - DIFFERENTIAL PRESSURE | -: +/- 1.5%; REF: SHE; REQ: 12; F: C | [10 empty] | 01
LF04 | LF04-PDI-002 | LF04-P-002 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | LF04 | 029.4 | EU13 FILTER DIFF PRESSURE | L8686 | 0 to 500 pA | +/-25Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF04 | LF04-PDSH-002 | LF04-P-002 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - HIGH | LF04 | 029.4 | EU13 FILTER DIFF PRESSURE | L8686 | 200 to 1000 Pa | Actuating set point = 350 Pa | REF | By Request | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF04 | LF04-PDSL-002 | LF04-P-002 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - LOW | LF04 | 029.4 | EU13 FILTER DIFF PRESSURE | L8686 | 40 to 400 Pa | Actuating set point = 150 Pa | REF | By Request | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF04 | LF04-PDI-003 | LF04-P-003 | PKG | 107-PA | INDICATOR - DIFF PRESSURE | LF04 | 029.4 | EU8 FILTER DIFF PRESSURE | L8687 | 0 to 500 pA | +/-25 Pa | REF | By Request | C | [5 empty] | 0 | [7 empty] | 01
LF04 | LF04-PDSH-003 | LF04-P-003 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - HIGH | LF04 | 029.4 | EU8 FILTER DIFF PRESSURE | L8687 | 200 to 1000 Pa | Actuating set point = 350 Pa | REF | By Request | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF04 | LF04-PDSL-003 | LF04-P-003 | PKG | 107-PA | SWITCH - PRESSURE - DIFF - LOW | LF04 | 029.4 | EU8 FILTER DIFF PRESSURE | L8687 | 40 to 400 Pa | Actuating set point = 50Pa | REF | By Request | C | [5 empty] | 0 | [5 empty] | FINAL SET @ COMMISS. |  | 01
LF04 | LF04-TS-001 | LF04-T-001 | FLD | 107-PA | SENSOR - TEMPERATURE | LF04 | 029.4 | DUCT - TEMPERATURE | -: +/- 1.5%; REF: REF; REQ: 12; F: C | [10 empty] | 01
LF04 | LF04-XA-001 | LF04-X-001 | PKG | 107-PA | ALARM - AUDIBLE | LF04 | 029.4 | COMMON ALARM | 8688 | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | UTIL | COOPER MEDC | DB5 |  | TI702-SP-5156 |  |  | 01
LF04 | LF04-XL-001 | LF04-X-001 | PKG | 107-PA | INDICATOR - LAMP | LF04 | 029.4 | COMMON ALARM |  | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | UTIL | EAO | 704.950.0 |  | TI702-SP-5155 |  |  | 01
LF04 | LF04-YA-001 | LF04-Y-001 | PCS | 107-PA | ALARM - COMMON |  |  | COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LF04 | LF04-YS-001 | LF04-Y-001 | PKG | 107-PA | COMMON ALARM |  | 029.4 | COMMON ALARM | 8685 | - | - | REF | 12 | F |  | I.S | DI |  |  | 32 | UTIL | FURNESS CONTROLS LTD | FCO54 |  | TI702-SP-5154 |  |  | 01
LR01 | LR1-BD-001 | LR1-B-001 | FLD | 107-RA | RUPTURE DISC | 25-P-HS1A-0-9027633 | 137.0 | SV1 BURSTING DISC | -: 5.0 barg; -: -; I.S: I.S |  |  | 0 | LR1 | BS & B | BAS+ |  | TI702-SP-5123 |  |  | 01
LR01 | LR1-YSAL-001 | LR1-B-001 | PCS | 107-RA | ALARM - RUPTURE DISC FAIL |  | 137.0 | SV1 BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-YSL-001 | LR1-B-001 | FLD | 107-RA | BURST DETECTOR |  | 137.0 | SV1 BURSTING DISC | 6662 |  | - |  | 12 | F |  | I.S | DI |  |  | 32 | LR1 | [6 empty] | 01
LR01 | LR1-BD-002 | LR1-B-002 | FLD | 107-RA | RUPTURE DISC | 40-P-HS6A-0-9027622 | 137.0 | LR1-EJ01 BURSTING DISC | -: 22.0 barg; -: -; I.S: I.S |  |  | 0 | LR1 | BS & B | BAS+ |  | TI702-SP-5123 |  |  | 01
LR01 | LR1-YSAL-002 | LR1-B-002 | PCS | 107-RA | ALARM - RUPTURE DISC FAIL |  |  | LR1-EJ01 BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-YSL-002 | LR1-B-002 | FLD | 107-RA | BURST DETECTOR |  | 137.0 | LR1-EJ01 BURSTING DISC | 6665 |  | - |  | 12 | F |  | I.S | DI |  |  | 32 | LR1 | [6 empty] | 01
LR01 | LR1-CV-001 | LR1-C-001 | FLD | 107-RA | GLOBE VALVE - CONTROL - F.C. | 15-H-SS6C-0-9027607 | 137.0 | HYDROGEN FLOW CONTROL | 6668 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | LR1 | SAMSON | 3730-2 POSITIONER |  | TI702-SP-5052 |  |  | 01
LR01 | LR1-US-001 | LR1-C-001 | PCS | 107-RA | FUNCTION - MIN SELECTOR |  |  | HYDROGEN FLOW CONTROL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-CV-002A | LR1-C-002A | FLD | 107-RA | GLOBE VALVE - CONTROL - F.O. | 40-HT-CS3A-C-9027557 | 137.0 | COLD HTF RETURN | 6671 | 0 T0 100% | - |  | 12 | F | SIL | I.S | AO |  |  | 21 | LR1 | SAMSON | 3767-1 POSITIONER |  | TI702-SP-5053 |  |  | 01
LR01 | LR1-CY-002A | LR1-C-002A | FLD | 107-RA | SOLENOID VALVE | MTD ON VALVE | 137.0 | COLD HTF RETURN | I.S: I.S | DO |  | 41 | SIS | SAMSON | 3767-104 SOLENOID |  | TI702-SP-5054 |  |  | 01
LR01 | LR1-CV-002B | LR1-C-002B | FLD | 107-RA | GLOBE VALVE - CONTROL - F.C. | 40-HT-CS3A-H-9027556 | 137.0 | HOT HTF RETURN | 6944 | 0 T0 100% | - |  | 12 | F | SIL | I.S | AO |  |  | 21 | LR1 | SAMSON | 3767-1 POSITIONER |  | TI702-SP-5053 |  |  | 01
LR01 | LR1-CY-002B | LR1-C-002B | FLD | 107-RA | SOLENOID VALVE | MTD ON VALVE | 137.0 | HOT HTF RETURN | I.S: I.S | DO |  | 41 | SIS | SAMSON | 3767-104 SOLENOID |  | TI702-SP-5054 |  |  | 01
LR01 | LR1-CV-005A | LR1-C-005A | FLD | 107-RA | GLOBE VALVE - CONTROL - F.O. | 40-HT-CS3A-C-9027565 | 137.0 | CONDENSER COLD HTF RTN | 6351 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | LR1 | SAMSON | 3767-1 POSITIONER |  | TI702-SP-5053 |  |  | 01
LR01 | LR1-CV-005B | LR1-C-005B | FLD | 107-RA | GLOBE VALVE - CONTROL - F.C. | 40-HT-CS3A-C-9027564 | 137.0 | CONDENSER HOT HTF RTN | 6708 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | LR1 | SAMSON | 3767-1 POSITIONER |  | TI702-SP-5053 |  |  | 01
LR01 | LR1-CV-008 | LR1-C-008 | FLD | 107-RA | GLOBE VALVE - CONTROL - F.C. | 15-P-HS6A-0-9027630 | 137.0 | HIGH PRESSURE VENT CONTROL | 6724 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | LR1 | SAMSON | 3767-1 POSITIONER |  | TI702-SP-5053 |  |  | 01
LR01 | LR1-PIC-008 | LR1-C-008 | PCS | 107-RA | INDICATING CONTROLLER - PRESSURE |  |  | HIGH PRESSURE VENT CONTROL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-UY-008 | LR1-C-008 | PCS | 107-RA | FUNCTION - DP/DT |  |  | HIGH PRESSURE VENT CONTROL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-CV-010 | LR1-C-010 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 25-P-HS6A-0-9027616 | 137.0 | LIQUID INLET | 6725 | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-010 | LR1-C-010 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-010 | LR1-C-010 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-010 | LR1-C-010 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-011 | LR1-C-011 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 25-P-HS6A-0-9027616 | 137.0 | LIQUID INLET | 6859 | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-011 | LR1-C-011 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-011 | LR1-C-011 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-011 | LR1-C-011 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-012 | LR1-C-012 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 40-P-HS6A-0-9027610 | 137.0 | HYDROGEN SHUT OFF | 6886 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 | [7 empty] | 01
LR01 | LR1-CY-012A | LR1-C-012 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | HYDROGEN SHUT OFF | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-CY-012B | LR1-C-012 | FLD | 107-RA | SOLENOID VALVE | MTD ON VALVE | 137.0 | HYDROGEN SHUT OFF | REF: SHE; I.S: I.S | DO |  | 41 | SIS | RGS | EP000/ia |  | TI702-SP-5101 |  |  | 01
LR01 | LR1-ZSC-012 | LR1-C-012 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | HYDROGEN SHUT OFF | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-012 | LR1-C-012 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | HYDROGEN SHUT OFF | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-013 | LR1-C-013 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 25-P-HS6A-0-9027655 | 137.0 | CATALYST INLET | 6919 | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-013 | LR1-C-013 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | CATALYST INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-013 | LR1-C-013 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | CATALYST INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-013 | LR1-C-013 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | CATALYST INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-014 | LR1-C-014 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 25-P-HS6A-0-9027655 | 137.0 | CATALYST VESSEL OUTLET | 6965 | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-014 | LR1-C-014 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | CATALYST VESSEL OUTLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-014 | LR1-C-014 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | CATALYST VESSEL OUTLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-014 | LR1-C-014 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | CATALYST VESSEL OUTLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-015 | LR1-C-015 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 25-P-HS6A-0-9027630 | 137.0 | VENT ISOLATION | 6966 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-015 | LR1-C-015 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | VENT ISOLATION | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-015 | LR1-C-015 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | VENT ISOLATION | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-015 | LR1-C-015 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | VENT ISOLATION | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-016 | LR1-C-016 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 25-P-HS6A-0-9027632 | 137.0 | LOW PRESSURE VENT | 6967 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-016 | LR1-C-016 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | LOW PRESSURE VENT | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-016 | LR1-C-016 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | LOW PRESSURE VENT | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-016 | LR1-C-016 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | LOW PRESSURE VENT | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-018 | LR1-C-018 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 25-N-SS1C-0-9027624 | 137.0 | NITROGEN SHUT OFF | 6969 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-018 | LR1-C-018 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | NITROGEN SHUT OFF | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-018 | LR1-C-018 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | NITROGEN SHUT OFF | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-018 | LR1-C-018 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | NITROGEN SHUT OFF | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-019 | LR1-C-019 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 40-P-HS6A-0-9027622 | 137.0 | NITROGEN LINE ISOLATION | 6970 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-019 | LR1-C-019 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | NITROGEN LINE ISOLATION | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-019 | LR1-C-019 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | NITROGEN LINE ISOLATION | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-019 | LR1-C-019 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | NITROGEN LINE ISOLATION | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-020 | LR1-C-020 | FLD | 107-RA | BALL VALVE - ON/OFF - F.O. | 15-P-SS1C-0-9027626 | 137.0 | NITROGEN BLEED | 6971 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-020 | LR1-C-020 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | NITROGEN BLEED | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-020 | LR1-C-020 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | NITROGEN BLEED | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-020 | LR1-C-020 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | NITROGEN BLEED | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-021 | LR1-C-021 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 15-P-HS1A-0-9027618 | 137.0 | CATALYST VESSEL LIQUID INLET | 6972 | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-021 | LR1-C-021 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | CATALYST VESSEL LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-021 | LR1-C-021 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | CATALYST VESSEL LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-021 | LR1-C-021 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | CATALYST VESSEL LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-022 | LR1-C-022 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 20-P-HS1A-0-9027649 | 137.0 | CATALYST VESSEL VENT | 6973 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-022 | LR1-C-022 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | CATALYST VESSEL VENT | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-022 | LR1-C-022 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | CATALYST VESSEL VENT | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-022 | LR1-C-022 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | CATALYST VESSEL VENT | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-023 | LR1-C-023 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 15-P-HS1A-0-9027646 | 137.0 | CATALYST VESSEL N2 SUPPLY | 6974 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-023 | LR1-C-023 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | CATALYST VESSEL N2 SUPPLY | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-023 | LR1-C-023 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | CATALYST VESSEL N2 SUPPLY | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-023 | LR1-C-023 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | CATALYST VESSEL N2 SUPPLY | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-024 | LR1-C-024 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 15-H-GCU-0-9027571 | 137.0 | HYDROGEN CYLINDER SHUT OFF | 6975 | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-024 | LR1-C-024 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | HYDROGEN CYLINDER SHUT OFF | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-024 | LR1-C-024 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | HYDROGEN CYLINDER SHUT OFF | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-024 | LR1-C-024 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | HYDROGEN CYLINDER SHUT OFF | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-025 | LR1-C-025 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 15-H-GCU-0-9027702 | 137.0 | HYDROGEN CYLINDER SHUT OFF | 6976 | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-025 | LR1-C-025 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | HYDROGEN CYLINDER SHUT OFF | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-025 | LR1-C-025 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | HYDROGEN CYLINDER SHUT OFF | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-025 | LR1-C-025 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | HYDROGEN CYLINDER SHUT OFF | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-026 | LR1-C-026 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 25-P-HS6A-H-9027637 | 137.0 | DISCHARGE | 6977 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-026 | LR1-C-026 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | DISCHARGE | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-026 | LR1-C-026 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | DISCHARGE | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-026 | LR1-C-026 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | DISCHARGE | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-027 | LR1-C-027 | FLD | 107-RA | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-C-9027555 | 137.0 | COLD HTF SUPPLY | 6978 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 | [7 empty] | 01
LR01 | LR1-CY-027A | LR1-C-027 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-CY-027B | LR1-C-027 | FLD | 107-RA | SOLENOID VALVE | MTD ON VALVE | 137.0 | COLD HTF SUPPLY | REF: SHE; I.S: I.S | DO |  | 41 | SIS | RGS | EP000/ia |  | TI702-SP-5101 |  |  | 01
LR01 | LR1-ZSC-027 | LR1-C-027 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-027 | LR1-C-027 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-028 | LR1-C-028 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-H-9027554 | 137.0 | HOT HTF SUPPLY | 6979 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 | [7 empty] | 01
LR01 | LR1-CY-028 | LR1-C-028 | FLD | 107-RA | SOLENOID VALVE | MTD ON VALVE | 137.0 | HOT HTF SUPPLY | REF: SHE; I.S: I.S | DO |  | 41 | SIS | RGS | EP000/ia |  | TI702-SP-5101 |  |  | 01
LR01 | LR1-ZSC-028 | LR1-C-028 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-028 | LR1-C-028 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-029 | LR1-C-029 | FLD | 107-RA | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-C-9027563 | 137.0 | CONDENSER COLD HTF SUPPLY | 6980 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-029 | LR1-C-029 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | CONDENSER COLD HTF SUPPLY | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-029 | LR1-C-029 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | CONDENSER COLD HTF SUPPLY | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-029 | LR1-C-029 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | CONDENSER COLD HTF SUPPLY | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-030 | LR1-C-030 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-H-9027562 | 137.0 | CONDENSER HOT HTF SUPPLY | 6981 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-ZSC-030 | LR1-C-030 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | CONDENSER HOT HTF SUPPLY | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-030 | LR1-C-030 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | CONDENSER HOT HTF SUPPLY | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-031 | LR1-C-031 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 15-NHP-SS6C-0-9027606 | 137.0 | NITROGEN | 6987 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-031 | LR1-C-031 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | NITROGEN | I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-031 | LR1-C-031 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | NITROGEN | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-031 | LR1-C-031 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | NITROGEN | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-032 | LR1-C-032 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 15-P-HS6A-0-9027617 | 137.0 | SOLVENT WASH | 6988 | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-032 | LR1-C-032 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | SOLVENT WASH | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-032 | LR1-C-032 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | SOLVENT WASH | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-032 | LR1-C-032 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | SOLVENT WASH | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-CV-033 | LR1-C-033 | FLD | 107-RA | BALL VALVE - ON/OFF - F.C. | 15-P-HS6A-0-9027617 | 137.0 | SOLVENT WASH | 6989 | - | - | SHE | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-CY-033 | LR1-C-033 | FLD | 107-RA | SOLENOID VALVE | FIELD PANEL IE27199 | 137.0 | SOLVENT WASH | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | LR1 | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
LR01 | LR1-ZSC-033 | LR1-C-033 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED | MTD ON VALVE | 137.0 | SOLVENT WASH | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-ZSO-033 | LR1-C-033 | FLD | 107-RA | PROXIMITY SENSOR - OPEN | MTD ON VALVE | 137.0 | SOLVENT WASH | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-DIC-001 | LR1-D-001 | PCS | 107-RA | INDICATING CONTR. - MOTOR DRIVE |  |  | CATALYST VESSEL AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-DS-001 | LR1-D-001 | MCC | 107-RA | DRIVE - AVAILABLE | MCC-P |  | CATALYST VESSEL AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | LR1 | [6 empty] | 01
LR01 | LR1-DY-001 | LR1-D-001 | MCC | 107-RA | DRIVE - RUNNING | MCC-P |  | CATALYST VESSEL AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | LR1 | [6 empty] | 01
LR01 | LR1-DYC-001 | LR1-D-001 | MCC | 107-RA | DRIVE - START/STOP | MCC-P |  | CATALYST VESSEL AGITATOR | 7068 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | LR1 | [6 empty] | 01
LR01 | LR1-DIC-002 | LR1-D-002 | PCS | 107-RA | INDICATING CONTR. - MOTOR DRIVE |  |  | REACTION PUMP | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-DS-002 | LR1-D-002 | MCC | 107-RA | DRIVE - AVAILABLE | MCC-PE |  | REACTION PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | LR1 | [6 empty] | 01
LR01 | LR1-DY-002 | LR1-D-002 | MCC | 107-RA | DRIVE - RUNNING | MCC-PE |  | REACTION PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | LR1 | [6 empty] | 01
LR01 | LR1-DYC-002 | LR1-D-002 | MCC | 107-RA | DRIVE - START/STOP | MCC-PE |  | REACTION PUMP | 7074 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | LR1 | [6 empty] | 01
LR01 | LR1-DIC-003 | LR1-D-003 | PCS | 107-RA | INDICATING CONTR. - MOTOR DRIVE |  |  | HEAT EXCHANGER HTF PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-DS-003 | LR1-D-003 | MCC | 107-RA | DRIVE - AVAILABLE | MCC-PE |  | HEAT EXCHANGER HTF PUMP | I.S: N.I.S; DI: DI |  |  | 35 | LR1 | [6 empty] | 01
LR01 | LR1-DY-003 | LR1-D-003 | MCC | 107-RA | DRIVE - RUNNING | MCC-PE |  | HEAT EXCHANGER HTF PUMP | I.S: N.I.S; DI: DI |  |  | 35 | LR1 | [6 empty] | 01
LR01 | LR1-DYC-003 | LR1-D-003 | MCC | 107-RA | DRIVE - START/STOP | MCC-PE |  | HEAT EXCHANGER HTF PUMP | 7159 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | LR1 | [6 empty] | 01
LR01 | LR1-DIC-004 | LR1-D-004 | PCS | 107-RA | INDICATING CONTR. - MOTOR DRIVE |  |  | VENT CONDENSER HTF PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-DS-004 | LR1-D-004 | MCC | 107-RA | DRIVE - AVAILABLE | MCC-P |  | VENT CONDENSER HTF PUMP | I.S: N.I.S; DI: DI |  |  | 35 | LR1 | [6 empty] | 01
LR01 | LR1-DY-004 | LR1-D-004 | MCC | 107-RA | DRIVE - RUNNING | MCC-P |  | VENT CONDENSER HTF PUMP | I.S: N.I.S; DI: DI |  |  | 35 | LR1 | [6 empty] | 01
LR01 | LR1-DYC-004 | LR1-D-004 | MCC | 107-RA | DRIVE - START/STOP | MCC-P |  | VENT CONDENSER HTF PUMP | 7160 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | LR1 | [6 empty] | 01
LR01 | LR1-FIC-001 | LR1-F-001 | PCS | 107-RA | INDICATING CONTROLLER - FLOW |  |  | HYDROGEN FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-FIT-001A | LR1-F-001 | FLD | 107-RA | TRANSMITTER - FLOW | 15-H-SS6C-0-9027607 | 137.0 | HYDROGEN FLOW | 7164 | 0-850 N l/hr | +/- 0.28% | REF | 5 YR | C |  | N.I.S | AI |  |  | 13 | LRI | ENDRESS + HAUSER | Promass 63F |  |  | FLOWRATE |  | 01
LR01 | LR1-FIT-001B | LR1-F-001 | FLD | 107-RA | TRANSMITTER - FLOW |  | 137.0 | HYDROGEN FLOW | 7164 | 0.01 N l/pulse | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | LR1 |  |  |  |  | TOTALISED FLOW |  | 01
LR01 | LR1-FQI-001 | LR1-F-001 | PCS | 107-RA | INDICATOR - FLOW/TOTALISER |  |  | HYDROGEN FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-FI-002 | LR1-F-002 | PCS | 107-RA | INDICATOR - FLOW |  |  | DRUM SOLVENT LINE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-FIT-002A | LR1-F-002 | FLD | 107-RA | TRANSMITTER - FLOW | 25-P-SS1C-0-9027611 | 137.0 | DRUM SOLVENT LINE | 7165 | 0 to 2500 l/hr | +/- 0.1% | REF | 5 YR | C |  | I.S | AI |  |  | 13 | LRI | EMERSON | Micro Motion F-Series |  |  | FLOWRATE |  | 01 | 20
LR01 | LR1-FIT-002B | LR1-F-002 | FLD | 107-RA | TRANSMITTER - FLOW |  | 137.0 | DRUM SOLVENT LINE | 7165 | 0.01 l/pulse | +/- 0.1% | REF | 5 YR | C |  | I.S | DI |  |  | 36 | LR1 |  |  |  |  | TOTALISED FLOW |  | 01 | 20
LR01 | LR1-FQI-002 | LR1-F-002 | PCS | 107-RA | INDICATOR - FLOW/TOTALISER |  |  | DRUM SOLVENT LINE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-FI-003 | LR1-F-003 | PCS | 107-RA | INDICATOR - FLOW |  |  | BULK SOLVENT LINE 3 | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-FIT-003A | LR1-F-003 | FLD | 107-RA | TRANSMITTER - FLOW | 25-SO-SS1C-0-9027601 | 137.0 | BULK SOLVENT LINE 3 | 7167 | 0 to 2500 l/hr | +/- 0.1% | REF | 5 YR | C |  | I.S | AI |  |  | 13 | LRI | EMERSON | Micro Motion F-Series |  |  | FLOWRATE |  | 01 | 20
LR01 | LR1-FIT-003B | LR1-F-003 | FLD | 107-RA | TRANSMITTER - FLOW |  | 137.0 | BULK SOLVENT LINE 3 | 7167 | 0.01 l/pulse | +/- 0.1% | REF | 5 YR | C |  | I.S | DI |  |  | 36 | LR1 |  |  |  |  | TOTALISED FLOW |  | 01 | 20
LR01 | LR1-FQI-003 | LR1-F-003 | PCS | 107-RA | INDICATOR - FLOW/TOTALISER |  |  | BULK SOLVENT LINE 3 | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-FI-004 | LR1-F-004 | PCS | 107-RA | INDICATOR - FLOW |  |  | BULK SOLVENT LINE 4 | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-FIT-004A | LR1-F-004 | FLD | 107-RA | TRANSMITTER - FLOW | 25-SO-SS1C-0-9027602 | 137.0 | BULK SOLVENT LINE 4 | 7169 | 0 to 2500 l/hr | +/- 0.1% | REF | 5 YR | C |  | I.S | AI |  |  | 13 | LRI | EMERSON | Micro Motion F-Series |  |  | FLOWRATE |  | 01 | 20
LR01 | LR1-FIT-004B | LR1-F-004 | FLD | 107-RA | TRANSMITTER - FLOW |  | 137.0 | BULK SOLVENT LINE 4 | 7169 | 0.01 l/pulse | +/- 0.1% | REF | 5 YR | C |  | I.S | DI |  |  | 36 | LR1 |  |  |  |  | TOTALISED FLOW |  | 01 | 20
LR01 | LR1-FQI-004 | LR1-F-004 | PCS | 107-RA | INDICATOR - FLOW/TOTALISER |  |  | BULK SOLVENT LINE 4 | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-FAL-005 | LR1-F-005 | PCS | 107-RA | ALARM - FLOW - LOW |  |  | NITROGEN TO PROCESS VENT | REF: SHE |  |  | 0 |  | KROHNE | DK800/R/K1 |  |  |  |  | 38
LR01 | LR1-FI-005 | LR1-F-005 | FLD | 107-RA | VA FLOW METER | 15-N-SS1C-0-9027634 | 137.0 | NITROGEN TO PROCESS VENT | -: 0 to 2 Nm3/hr; -: +/- 5%; REF: SHE; REQ: REQ; F: F |  |  | 0 |  | KROHNE | [5 empty] | 01
LR01 | LR1-FSL-005 | LR1-F-005 | FLD | 107-RA | SWITCH - FLOW - LOW |  | 137.0 | NITROGEN TO PROCESS VENT | 7170 | set @ | - | SHE | 5 YR | F |  | I.S | DI |  |  | 31 | LR1 | PEPPERL + FUCHS | RC15-14-N3 |  | TI702-SP-5124 |  |  | 01
LR01 | LR1-FAL-006 | LR1-F-006 | PCS | 107-RA | ALARM - FLOW - LOW |  |  | NITROGEN TO CATCH TANK | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-FI-006 | LR1-F-006 | FLD | 107-RA | VA FLOW METER | 15-N-SS1C-0-9027620 | 137.0 | NITROGEN TO CATCH TANK | -: 0 to 2 Nm3/hr; -: +/- 5%; REF: SHE; REQ: REQ; F: F |  |  | 0 |  | KROHNE | [5 empty] | 01
LR01 | LR1-FSL-006 | LR1-F-006 | FLD | 107-RA | SWITCH - FLOW - LOW |  | 137.0 | NITROGEN TO CATCH TANK | 7171 | set @ | - | SHE | 5 YR | F |  | I.S | DI |  |  | 31 | LR1 | PEPPERL + FUCHS | RC15-14-N3 |  | TI702-SP-5124 |  |  | 01
LR01 | LR1-HV-001 | LR1-H-001 | FLD | 107-RA | HAND VALVE | 25-P-HS6A-H-9027640 | 137.0 | CATALYST FILTRATION | 7172 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-HZSC-001 | LR1-H-001 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED |  | 137.0 | CATALYST FILTRATION | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-HS-001A | LR1-H-001A | FLD | 107-RA | SWITCH - PUSHBUTTON | LR1 PACKAGE | 137.0 | CRASH COOLING | 7173 | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 32 | SIS | STAHL | 8040/1198X-10L07BA35 |  | TI702-SP-5145 |  |  | 01
LR01 | LR1-HS-001B | LR1-H-001B | FLD | 107-RA | SWITCH - PUSHBUTTON | LR1 LOP ROOM | 137.0 | CRASH COOLING | 7173 | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 32 | SIS | STAHL | 8040/1198X-10L07BA35 |  | TI702-SP-5145 |  |  | 01
LR01 | LR1-HV-002 | LR1-H-002 | FLD | 107-RA | HAND VALVE | 25-P-HS6A-H-9027641 | 137.0 | CATALST FILTRATION | 7177 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-HZSC-002 | LR1-H-002 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED |  | 137.0 | CATALST FILTRATION | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-HV-003 | LR1-H-003 | FLD | 107-RA | HAND VALVE | 25-P-HS6A-H-9027637 | 137.0 | DISCHARGE ISOLATION | 7195 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-HZSC-003 | LR1-H-003 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED |  | 137.0 | DISCHARGE ISOLATION | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-HV-005 | LR1-H-005 | FLD | 107-RA | HAND VALVE | 25-P-HS6A-H-9027657 | 137.0 | CONDENSER ISOLATION | 7235 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-HZSC-005 | LR1-H-005 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED |  | 137.0 | CONDENSER ISOLATION | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-HV-006 | LR1-H-006 | FLD | 107-RA | HAND VALVE | 25-P-HS6A-H-9027628 | 137.0 | CONDENSER ISOLATION | 7236 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-HZSC-006 | LR1-H-006 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED |  | 137.0 | CONDENSER ISOLATION | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-HV-007 | LR1-H-007 | FLD | 107-RA | HAND VALVE | 25-N-SS1C-0-9027619 | 137.0 | NITROGEN SUPPLY TO VENTS | 7237 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
LR01 | LR1-HZSO-007 | LR1-H-007 | FLD | 107-RA | PROXIMITY SENSOR - CLOSED |  | 137.0 | NITROGEN SUPPLY TO VENTS | I.S: I.S; DI: DI |  |  | 31 | LR1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
LR01 | LR1-HS-010 | LR1-H-010 | FLD | 107-RA | SWITCH - PUSHBUTTON | HYDROG CONTROL ROOM | 137.0 | STOP HYDROGEN SUPPLY | 7257 | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 35 | SGS | CEAG | [5 empty] | 01
LR01 | LR1-HS-011 | LR1-H-011 | FLD | 107-RA | SWITCH - PUSHBUTTON | HYDROG CONTROL ROOM | 137.0 | CRASH COOLING | 7258 | - | - | SHE | 12 | F | SIL | N.I.S |  | DI |  | 35 | SGS | CEAG | [5 empty] | 01
LR01 | LR1-LAH-001 | LR1-L-001 | PCS | 107-RA | ALARM - LEVEL - HIGH |  |  | CATALYST VESSEL | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-LSH-001 | LR1-L-001 | FLD | 107-RA | SWITCH - LEVEL - HIGH | SV1 | 137.0 | CATALYST VESSEL | 7288 | - | - | SHE | 12 | F |  | I.S | DI |  |  | 31 | LR1 | ENDRESS + HAUSER | Liquiphant FTL 50 |  | TI702-SP-5127 |  |  | 01
LR01 | LR1-LAH-002 | LR1-L-002 | PCS | 107-RA | ALARM - LEVEL - HIGH |  |  | CATCH TANK | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-LSH-002 | LR1-L-002 | FLD | 107-RA | SWITCH - LEVEL - HIGH | 25-P-SS1C-0-9027656 | 137.0 | CATCH TANK | 7290 | - | - | SHE | 12 | F |  | I.S | DI |  |  | 31 | LR1 | ENDRESS + HAUSER | Liquiphant FTL 51 |  | TI702-SP-5064 |  |  | 01
LR01 | LR1-LAL-003 | LR1-L-003 | PCS | 107-RA | ALARM - LEVEL - LOW |  |  | REACTION PUMP SEAL POT | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-LSL-003 | LR1-L-003 | FLD | 107-RA | SWITCH - LEVEL - LOW | LR1-P01 SEAL POT | 137.0 | REACTION PUMP SEAL POT | 7291 | - | - | SHE | 12 | F |  | I.S | DI |  |  | 31 | LR1 | EAGLE BURGMANN | SPS2063-00 |  | TI702-SP-5128 |  |  | 01
LR01 | LR1-LAH-004 | LR1-L-004 | PCS | 107-RA | ALARM - LEVEL - HIGH |  |  | PROCESS VENT | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-LSH-004 | LR1-L-004 | FLD | 107-RA | SWITCH - LEVEL - HIGH | 25-W-SS1C-0-9027631 | 137.0 | PROCESS VENT | 7359 | - | - | SHE | 12 | F |  | I.S | DI |  |  | 31 | LR1 | ENDRESS + HAUSER | Liquiphant FTL 50 |  | TI702-SP-5127 |  |  | 01
LR01 | LR1-PAH-001 | LR1-P-001 | PCS | 107-RA | ALARM - PRESSURE - HIGH |  |  | PRESSURE (HIGH RANGE) | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PAL-001 | LR1-P-001 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | PRESSURE (HIGH RANGE) | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PIC-001 | LR1-P-001 | PCS | 107-RA | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE (HIGH RANGE) | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PIT-001 | LR1-P-001 | FLD | 107-RA | TRANSMITTER - PRESSURE - DIAPHRAGM | 40-P-HS6A-0-9027610 | 137.0 | PRESSURE (HIGH RANGE) | 7360 | -1 to 40 barg | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | LR1 | ENDRESS + HAUSER | PMP635 |  | TI702-SP-5125 |  |  | 01
LR01 | LR1-PSAH-001 | LR1-P-001 | PCS | 107-RA | ALARM - PRESSURE - HIGH |  |  | PRESSURE (HIGH RANGE) | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PRV-001 | LR1-P-001V | FLD | 107-RA | CONTROL VALVE SELF ACTUATING | 25-N-SS1C-0-9027603 | 137.0 | NITROGEN TO MHT-06/-07 | -: set @ 2 barg; -: +/- 5%; REF: SHE; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PI-002 | LR1-P-002 | PCS | 107-RA | INDICATOR - PRESSURE |  |  | PRESSURE (LOW RANGE) | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PIT-002 | LR1-P-002 | FLD | 107-RA | TRANSMITTER - PRESSURE - DIAPHRAGM | 40-P-HS6A-0-9027610 | 137.0 | PRESSURE (LOW RANGE) | 7361 | -1 to 7 barg | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | LR1 | ENDRESS + HAUSER | PMP635 |  | TI702-SP-5125 |  |  | 01
LR01 | LR1-PRV-002 | LR1-P-002V | FLD | 107-RA | CONTROL VALVE SELF ACTUATING | 15-N-SS1C-0-9027645 | 137.0 | NITROGEN TO SV1-AG01 | -: set @ 3 barg; -: +/- 5%; REF: SHE; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PI-003 | LR1-P-003 | PCS | 107-RA | INDICATOR - PRESSURE |  |  | PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PIT-003 | LR1-P-003 | FLD | 107-RA | TRANSMITTER - PRESSURE - DIAPHRAGM | LR1-EJ01 | 137.0 | PRESSURE | 7379 | -1 to 40 barg | +/- 1% | SHE | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S2T |  | TI702-SP-5056 |  |  | 46
LR01 | LR1-PSAH-003 | LR1-P-003 | PCS | 107-RA | ALARM - PRESSURE - HIGH |  |  | PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PSAHH-003 | LR1-P-003 | SGS | 107-RA | ALARM - PRESSURE - HIGH |  |  | PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PRV-003 | LR1-P-003V | FLD | 107-RA | CONTROL VALVE SELF ACTUATING | 15-N-SS1C-0-9027620 | 137.0 | NITROGEN TO RELIEF VENT | -: set @ 1 barg; -: +/- 5%; REF: SHE; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PAH-004 | LR1-P-004 | PCS | 107-RA | ALARM - PRESSURE - HIGH |  |  | CATALST VESSEL PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PI-004 | LR1-P-004 | PCS | 107-RA | INDICATOR - PRESSURE |  |  | CATALST VESSEL PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PIT-004 | LR1-P-004 | FLD | 107-RA | TRANSMITTER - PRESSURE - DIAPHRAGM | 25-P-HS1A-0-9027653 | 137.0 | CATALST VESSEL PRESSURE | 7380 | 0 to 6 barg | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | LR1 | ENDRESS + HAUSER | PMP635 |  | TI702-SP-5125 |  |  | 01
LR01 | LR1-PRV-004 | LR1-P-004V | FLD | 107-RA | CONTROL VALVE SELF ACTUATING | 15-H-GCU-0-9027571 | 137.0 | HP HYDROGEN SUPPLY | -: set @ 19 barg; -: +/- 5%; REF: SHE; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PRV-005 | LR1-P-005V | FLD | 107-RA | CONTROL VALVE SELF ACTUATING | 15-N-SS1C-0-9027634 | 137.0 | NITROGEN TO PROCESS VENT | -: set @ 1 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PAL-006 | LR1-P-006 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | HYDROGEN SUPPLY PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PI-006 | LR1-P-006 | PCS | 107-RA | INDICATOR - PRESSURE |  |  | HYDROGEN SUPPLY PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PIT-006 | LR1-P-006 | FLD | 107-RA | TRANSMITTER - PRESSURE - DIAPHRAGM | 15-H-GCU-0-9027702 | 137.0 | HYDROGEN SUPPLY PRESSURE | 7391 | 0 to 250 barg | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | LR1 | ENDRESS + HAUSER | PMP635 |  | TI702-SP-5125 |  |  | 01
LR01 | LR1-PSALL-006 | LR1-P-006 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | HYDROGEN SUPPLY PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PRV-006 | LR1-P-006V | FLD | 107-RA | CONTROL VALVE SELF ACTUATING | 15-NHP-SS6C-0-9027573 | 137.0 | HP NITROGEN SUPPLY | -: set @ 19 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PAH-007 | LR1-P-007 | PCS | 107-RA | ALARM - PRESSURE - HIGH |  |  | REACTION PUMP SEAL PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PAL-007 | LR1-P-007 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | REACTION PUMP SEAL PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PI-007 | LR1-P-007 | PCS | 107-RA | INDICATOR - PRESSURE |  |  | REACTION PUMP SEAL PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-PIT-007 | LR1-P-007 | FLD | 107-RA | TRANSMITTER - PRESSURE | LR1-P01 SEAL POT | 137.0 | REACTION PUMP SEAL PRESSURE | 7420 | 0 to 50 barg | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | LR1 | ENDRESS + HAUSER | PMP635 |  | TI702-SP-5125 |  |  | 01
LR01 | LR1-PRV-007 | LR1-P-007V | FLD | 107-RA | CONTROL VALVE SELF ACTUATING | 15-NHP-GCU-0-9027574 | 137.0 | HP NITROGEN TO LR1-P01 SEAL | -: set @ 37 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PAH-008 | LR1-P-008 | PCS | 107-RA | ALARM - PRESSURE - HIGH |  |  | REACTION PUMP PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PSH-008 | LR1-P-008 | FLD | 107-RA | SWITCH - PRESSURE - HIGH | LR1-P01 | 137.0 | REACTION PUMP PRESSURE | 7438 | set @ 1.5 barg | +/- 5% | REF | 12 | F |  | I.S | DI |  |  | 31 | LR1 | BARKSDALE | P1H-M85SS-P2-T-EXI |  | TI702-SP-5129 |  |  | 01
LR01 | LR1-PRV-008 | LR1-P-008V | PKG | 107-RA | CONTROL VALVE SELF ACTUATING | SAMPLING SYSTEM | 137.0 | NITROGEN TO SAMPLE SYSTEM | -: set@0.5-1 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PAL-009 | LR1-P-009 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | PRESSURE HEAT TRANSFER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PI-009 | LR1-P-009 | FLD | 107-RA | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-H-9027679 | 137.0 | PRESSURE HEAT TRANSFER | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 |  | WIKA | 232.50 |  |  |  |  | 01
LR01 | LR1-PSL-009 | LR1-P-009 | FLD | 107-RA | SWITCH - PRESSURE - LOW |  | 137.0 | PRESSURE HEAT TRANSFER | 8779 | set @ | - | REF | 12 | F |  | I.S | DI |  |  | 31 | LR1 | PEPPERL + FUCHS | SJ3,5-N |  | TI702-SP-5055 |  |  | 01
LR01 | LR1-PRV-009 | LR1-P-009V | PKG | 107-RA | CONTROL VALVE SELF ACTUATING | 15-IA-SS1U-0-9027582 | 137.0 | LR1-DP-1 SPEED CONTROL | -: set A/R; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PAL-010 | LR1-P-010 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | PRESSURE HEAT TRANSFER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PI-010 | LR1-P-010 | FLD | 107-RA | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-H-9027560 | 137.0 | PRESSURE HEAT TRANSFER | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 |  | WIKA | 232.50 |  |  |  |  | 01
LR01 | LR1-PSL-010 | LR1-P-010 | FLD | 107-RA | SWITCH - PRESSURE - LOW |  | 137.0 | PRESSURE HEAT TRANSFER | 8543 | set @ commiss | +/- 5% | REF | 12 | F |  | I.S | DI |  |  | 31 | LR1 | PEPPERL + FUCHS | SJ3,5-N |  | TI702-SP-5055 |  |  | 01
LR01 | LR1-PRV-010 | LR1-P-010V | FLD | 107-RA | CONTROL VALVE SELF ACTUATING | 15-1A-SS1U-0-9028438 | 137.0 | LOP ROOM INSTRUMENT AIR | -: 0 to 17 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  |  | LR1 | NORGREN | B46G-4GK-AD3-RMN |  |  |  |  | 01
LR01 | LR1-PI-012 | LR1-P-012 | FLD | 107-RA | PRESSURE GAUGE | 15-H-GCU-0-9027571 | 137.0 | HP HYDROGEN SUPPLY | -: 0 to 69 barg; -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | LR1 | WIKA | 130.15 |  |  |  |  | 01
LR01 | LR1-PI-013 | LR1-P-013 | FLD | 107-RA | PRESSURE GAUGE - DIAPHRAGM | 50-P-HS6A-H-9027639 | 137.0 | LR1-P01 DISCHARGE | -: 0 to 40 barg; -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | LR1 | WIKA | 232.50 |  |  |  |  | 01
LR01 | LR1-PAL-014 | LR1-P-014 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | PRESSURE N2 GAS CYLINDER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PI-014 | LR1-P-014 | PCS | 107-RA | INDICATOR - PRESSURE |  |  | PRESSURE N2 GAS CYLINDER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PIT-014 | LR1-P-014 | FLD | 107-RA | TRANSMITTER - PRESSURE | 15-NHP-SS6C-0-9027573 | 137.0 | PRESSURE N2 GAS CYLINDER | 8547 | 0 to 250 barg | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | LR1 | ENDRESS + HAUSER | PMP635 |  | TI702-SP-5125 |  |  | 01
LR01 | LR1-PSALL-014 | LR1-P-014 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | PRESSURE N2 GAS CYLINDER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PI-015 | LR1-P-015 | FLD | 107-RA | PRESSURE GAUGE | 15-NHP-SS6C-0-9027573 | 137.0 | HP NITROGEN SUPPLY | -: 0 to 69 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 130.15 |  |  |  |  | 01
LR01 | LR1-PI-016 | LR1-P-016 | PKG | 107-RA | PRESSURE GAUGE | SAMPLING SYSTEM | 137.0 | NITROGEN TO SAMPLE SYSTEM | -: 0 to 5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50 |  |  |  |  | 01
LR01 | LR1-PI-017 | LR1-P-017 | PCS | 107-RA | INDICATOR - PRESSURE |  |  | HEAT EXCH OUTLET PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PIT-017 | LR1-P-017 | FLD | 107-RA | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-HS6A-H-9027644 | 137.0 | HEAT EXCH OUTLET PRESSURE | 8613 | 0 to 40 barg | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | LR1 | ENDRESS + HAUSER | PMP635 |  | TI702-SP-5125 |  |  | 01
LR01 | LR1-PAL-018 | LR1-P-018 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | HYDROGEN SUPPLY PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PI-018 | LR1-P-018 | PCS | 107-RA | INDICATOR - PRESSURE |  |  | HYDROGEN SUPPLY PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PIT-018 | LR1-P-018 | FLD | 107-RA | TRANSMITTER - PRESSURE - DIAPHRAGM | 15-H-GCU-0-9027702 | 137.0 | HYDROGEN SUPPLY PRESSURE | 8549 | 0 to 250 barg | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | LR1 | ENDRESS + HAUSER | PMP635 |  | TI702-SP-5125 |  |  | 01
LR01 | LR1-PSALL-018 | LR1-P-018 | PCS | 107-RA | ALARM - PRESSURE - LOW |  |  | HYDROGEN SUPPLY PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-PI-019 | LR1-P-019 | PKG | 107-RA | PRESSURE GAUGE | MHT-07 | 137.0 | MHT-07 PRESSURE | -: -1 to 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PSV-020 | LR1-P-020 | PKG | 107-RA | PRESSURE RELIEF VALVE | MHT-07 | 137.0 | MHT-07 RELIEF | -: Set @ 6.5 barg; -: +/- 5%; REF: SHE; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PI-021 | LR1-P-021 | PKG | 107-RA | PRESSURE GAUGE | LR1-PRV-009 | 137.0 | LR1-PRV-009 OUTLET | -: ?? barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PI-022 | LR1-P-022 | PKG | 107-RA | PRESSURE GAUGE | 15-N-SS1U-0-9027581 | 137.0 | LR1-DP-01 NITROGEN SUPPLY | -: ?? barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-PI-023 | LR1-P-023 | PKG | 107-RA | PRESSURE GAUGE | SV01-AG1 SEAL POT | 137.0 | SV01-AG1 SEAL PRESSURE | -: -1 to 9.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  |  |  | WIKA | 232.30 |  |  |  |  | 01
LR01 | LR1-PI-024 | LR1-P-024 | FLD | 107-RA | PRESSURE GAUGE | WITH LR1-PRV-004 | 137.0 | HP HYDROGEN SUPPLY | -: 0 to 275 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  |  |  | WIKA | 130.15 |  |  |  |  | 01
LR01 | LR1-PI-025 | LR1-P-025 | FLD | 107-RA | PRESSURE GAUGE | WITH LR1-PRV-005 | 137.0 | HP NITROGEN SUPPLY | -: 0 to 275 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  |  |  | WIKA | 130.15 |  |  |  |  | 01
LR01 | LR1-PI-026 | LR1-P-026 | FLD | 107-RA | PRESSURE GAUGE | WITH LR1-PRV-006 | 137.0 | HP NITROGEN SUPPLY | -: 0 to 69 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  |  |  | WIKA | 130.15 |  |  |  |  | 01
LR01 | LR1-PI-027 | LR1-P-027 | FLD | 107-RA | PRESSURE GAUGE | WITH LR1-PRV-007 | 137.0 | HP NITROGEN SUPPLY | -: 0 to 275 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  |  |  | WIKA | 130.15 |  |  |  |  | 01
LR01 | LR1-PRV-028 | LR1-P-028 | FLD | 107-RA | CONTROL VALVE SELF ACTUATING | 15-N-SS1C-0-902???? | 137.0 | LP NITROGEN TO SEAL POT | -: Set @ 4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
LR01 | LR1-RV-001 | LR1-R-001 | FLD | 107-RA | RELIEF VALVE | 15-H-SS6C-0-9027578 | 137.0 | HP HYDROGEN RELIEF | -: set @ 20 barg; -: +/- 5%; REF: SHE; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-RO-001 | LR1-R-001R | FLD | 107-RA | RESTRICTION ORIFICE PLATE | 15-HT-CS3A-C-9027672 | 137.0 | COLD HTF | -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
LR01 | LR1-RV-002 | LR1-R-002 | FLD | 107-RA | RELIEF VALVE | 15-RV-GCU-0-9027577 | 137.0 | HP NITROGEN RELIEF | -: set @ 20 barg; -: +/- 5%; REF: SHE; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-RO-002 | LR1-R-002R | FLD | 107-RA | RESTRICTION ORIFICE PLATE | 15-HT-CS3A-H-9027675 | 137.0 | HOT HTF | -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
LR01 | LR1-RV-003 | LR1-R-003 | FLD | 107-RA | RELIEF VALVE | 50-HT-CS3A-H-9027550 | 137.0 | HTF RELIEF | -: set @ 10 barg; -: +/- 5%; REF: SHE; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-RO-003 | LR1-R-003R | FLD | 107-RA | RESTRICTION ORIFICE PLATE | 50-HT-CS3A-H-9027679 | 137.0 | LR1-JP01 DISCHARGE | -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
LR01 | LR1-RV-004 | LR1-R-004 | FLD | 107-RA | RELIEF VALVE | 15-P-SS6C-0-9027664 | 137.0 | LR1-P01 SEAL RELIEF | -: set @ 40 barg; -: +/- 5%; REF: SHE; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
LR01 | LR1-RO-004 | LR1-R-004R | FLD | 107-RA | RESTRICTION ORIFICE PLATE | 50-HT-CS3A-H-9027560 | 137.0 | LR1-JP02 DISCHARGE | -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
LR01 | LR1-RV-005 | LR1-R-005 | FLD | 107-RA | RELIEF VALVE | SV01-AG1 SEAL POT | 137.0 | SV01-AG1 SEAL RELIEF | -: set @ 4.5 barg; -: +/- 5%; REF: SHE; REQ: 24; F: C |  |  |  |  | Swagelok | SS-RL3M4F4-R7 |  |  |  |  | 01
LR01 | LR1-RO-005 | LR1-R-005R | FLD | 107-RA | RESTRICTION ORIFICE PLATE | 15-N-SS1C-0-9027567 | 137.0 | NITROGEN TO SAMPLE SYSTEM | -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
LR01 | LR1-RO-006 | LR1-R-006 | FLD | 107-RA | RESTRICTION ORIFICE PLATE | DELETED | 137.0 | DELETED | -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | DELETED |  | 01
LR01 | LR1-RO-007 | LR1-R-007 | FLD | 107-RA | RESTRICTION ORIFICE PLATE | DELETED | 137.0 | DELETED | -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | DELETED |  | 01
LR01 | LR1-RO-008 | LR1-R-008 | FLD | 107-RA | RESTRICTION ORIFICE PLATE | DELETED | 137.0 | DELETED | -: +/- 5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | DELETED |  | 01
LR01 | LR1-TAH-001 | LR1-T-001 | PCS | 107-RA | ALARM - TEMPERATURE - HIGH |  |  | CONTENTS TEMPERATURE (OUTLET) | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-TE-001 | LR1-T-001 | FLD | 107-RA | ELEMENT & THERMOWELL | 80-P-HS6A-H-9027636 | 137.0 | CONTENTS TEMPERATURE (OUTLET) | REF: GxP/SHE | [8 empty] | DUPLEX WITH TE-002 |  | 01
LR01 | LR1-TI-001 | LR1-T-001 | FLD | 107-RA | INDICATOR - TEMPERATURE | ADJ TO TRANSMITTER | 137.0 | CONTENTS TEMPERATURE (OUTLET) | -: -30 to 170 degC; -: +/- 1%; REF: GxP/SHE; REQ: 12; F: C |  |  |  |  | MOORE INDUSTRIES | PSD |  | TI702-SP-5048 |  |  | 01
LR01 | LR1-TIC-001 | LR1-T-001 | PCS | 107-RA | INDICATING CONTROLLER - TEMPERATURE |  |  | CONTENTS TEMPERATURE (OUTLET) | REF: SHE |  |  | 0 | [5 empty] | MASTER |  | 01
LR01 | LR1-TSAH-001 | LR1-T-001 | PCS | 107-RA | ALARM - TEMPERATURE - HIGH |  |  | CONTENTS TEMPERATURE (OUTLET) | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-TT-001 | LR1-T-001 | FLD | 107-RA | TRANSMITTER - TEMPERATURE | ADJ TO ELEMENT | 137.0 | CONTENTS TEMPERATURE (OUTLET) | 8597 | -30 to 170 degC | +/- 1% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | LR1 | MOORE INDUSTRIES | TRX / PRG 4 |  | TI702-SP-5048 |  |  | 01
LR01 | LR1-TE-002 | LR1-T-002 | FLD | 107-RA | ELEMENT & THERMOWELL | 80-P-HS6A-H-9027636 | 137.0 | CONTENTS TEMPERATURE (OUTLET) | REF: GxP/SHE | [8 empty] | DUPLEX WITH TE-001 |  | 01
LR01 | LR1-TI-002A | LR1-T-002 | PCS | 107-RA | INDICATOR - TEMPERATURE |  |  | CONTENTS TEMPERATURE (OUTLET) | REF: GxP/SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-TI-002B | LR1-T-002 | FLD | 107-RA | INDICATOR - TEMPERATURE | ADJ TO TRANSMITTER | 137.0 | CONTENTS TEMPERATURE (OUTLET) | -: -30 to 170 degC; -: +/- 1%; REF: SHE; REQ: 12; F: C |  |  |  |  | MOORE INDUSTRIES | PSD |  | TI702-SP-5048 |  |  | 01
LR01 | LR1-TT-002 | LR1-T-002 | FLD | 107-RA | TRANSMITTER - TEMPERATURE | ADJ TO ELEMENT | 137.0 | CONTENTS TEMPERATURE (OUTLET) | 8670 | -30 to 170 degC | +/- 1% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | LR1 | MOORE INDUSTRIES | TRX / PRG 4 |  | TI702-SP-5048 |  |  | 01
LR01 | LR1-TI-003 | LR1-T-003 | PCS | 107-RA | INDICATOR - TEMPERATURE |  |  | TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-TSAH-003 | LR1-T-003 | PCS | 107-RA | ALARM - TEMPERATURE - HIGH |  |  | TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-TSAHH-003 | LR1-T-003 | SGS | 107-RA | ALARM - PRESSURE - HIGH |  |  | TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-TT-003 | LR1-T-003 | FLD | 107-RA | TRANSMITTER - TEMPERATURE | 80-P-HS6A-H-9027636 | 137.0 | TEMPERATURE | 8799 | -30 to 170 degC | +/- 1% | SHE | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | MOORE INDUSTRIES | STZ/PRG/4-20MA/12-30DC[LH1CS] |  | TI702-SP-5144 |  |  | 01
LR01 | LR1-TIC-004 | LR1-T-004 | PCS | 107-RA | INDICATING CONTROLLER - TEMPERATURE |  |  | HTF RETURN TEMPERATURE | REF: SHE |  |  | 0 | [5 empty] | SLAVE |  | 01
LR01 | LR1-TT-004 | LR1-T-004 | FLD | 107-RA | TRANSMITTER - TEMPERATURE | 50-HT-CS3A-H-9027677 | 137.0 | HTF RETURN TEMPERATURE | 8898 | -30 to 170 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | LR1 | MOORE INDUSTRIES | TRX/PRG |  | TI702-SP-5047 |  |  | 01
LR01 | LR1-UY-001 | LR1-T-004 | PCS | 107-RA | FUNCTION - SPLITRANGE |  |  | HTF RETURN TEMPERATURE | REF: REF |  |  | 0 | [5 empty] | OUTPUTS TO CV-002A & CV-002B |  | 01
LR01 | LR1-TAH-005 | LR1-T-005 | PCS | 107-RA | ALARM - TEMPERATURE - HIGH |  |  | CONDENSER RETURN TEMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-TIC-005 | LR1-T-005 | PCS | 107-RA | INDICATING CONTROLLER - TEMPERATURE |  |  | CONDENSER RETURN TEMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
LR01 | LR1-TT-005 | LR1-T-005 | FLD | 107-RA | TRANSMITTER - TEMPERATURE | 50-HT-CS3A-H-9027568 | 137.0 | CONDENSER RETURN TEMP | 8736 | -30 to 170 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | LR1 | MOORE INDUSTRIES | TRX/PRG |  | TI702-SP-5047 |  |  | 01
LR01 | LR1-UY-005 | LR1-T-005 | PCS | 107-RA | FUNCTION - SPLITRANGE |  |  | CONDENSER RETURN TEMP | [11 empty] | 0 | [5 empty] | OUTPUTS TO CV-005A & CV-005B |  | 01 | bar: PKG
LR01 | LR1-TAH-006 | LR1-T-006 | PCS | 107-RA | ALARM - TEMPERATURE - HIGH |  |  | REACTION PUMP SEAL TEMP | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-TI-006 | LR1-T-006 | PCS | 107-RA | INDICATOR - TEMPERATURE |  |  | REACTION PUMP SEAL TEMP | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-TI-006A | LR1-T-006 | FLD | 107-RA | INDICATOR - TEMPERATURE | LR1-P01 SEAL POT | 137.0 | REACTION PUMP SEAL TEMP | -: 0 to 200 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C | [5 empty] | BERGMANN |  |  | SPI 2063 |  | 01
LR01 | LR1-TT-006 | LR1-T-006 | FLD | 107-RA | TRANSMITTER - TEMPERATURE | LR1-P01 SEAL POT | 137.0 | REACTION PUMP SEAL TEMP | 11130 | 0 to 100 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | LR1 | MOORE INDUSTRIES | TRX / PRG 4 |  | TI702-SP-5047 |  |  | 01
LR01 | LR1-TI-007 | LR1-T-007 | PCS | 107-RA | INDICATOR - TEMPERATURE |  |  | HEAT EXCHANGER OUTLET TEMP | REF: SHE |  |  | 0 | [7 empty] | 01
LR01 | LR1-TT-007 | LR1-T-007 | FLD | 107-RA | TRANSMITTER - TEMPERATURE | 50-P-HS6A-H-9027644 | 137.0 | HEAT EXCHANGER OUTLET TEMP | 11131 | -30 to 170 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | LR1 | MOORE INDUSTRIES | TRX/PRG |  | TI702-SP-5047 |  |  | 01
LR01 | LR1-TW-010 | LR1-T-010 | FLD | 107-RA | THERMOWELL | 50-HT-CS3A-H-9027679 | 137.0 | HEAT TRANSFER TEST | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
MBF01 | MBF01-PSV-001 | MBF01-P-001 | FLD | 107-MA | PRESSURE SAFETY VALVE | MBF01 | 151.1 | PRV-001 PRESSURE | -: 10 barg; -: +/- 10%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
MBF01 | MBF01-PI-002 | MBF01-P-002 | FLD | 107-MA | PRESSURE GAUGE | MBF01 | 151.1 | PI-002 PRESSURE | -: 0 to 16 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
MB | MB-HS-003AN | MB-X-003 | FLD | C&E/693 | SWITCH - PUSHBUTTON | MILL. & BLEND GND FLOOR | 083.2 | GEN. ALM. MILL & BLENDING | 8089 | - | - | REF | REQ | F |  | I.S |  | DI |  | 32 | SIS | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5076 |  |  | 01
MB | MB-XA-003AN | MB-X-003 | FLD | C&E/693 | ALARM - AUDIBLE | MILL. & BLEND GND FLOOR | 083.2 | GEN. ALM. MILL & BLENDING |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | DB7-24B |  | TI702-SP-5035 |  |  | 01
MB | MB-XL-003AN | MB-X-003 | FLD | C&E/693 | ALARM - BEACON | MILL. & BLEND GND FLOOR | 083.2 | GEN. ALM. MILL & BLENDING |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | COOPER MEDC | XB8-24B |  | TI702-SP-5016 |  |  | 01
MC01 | MC01-CYL-01 | MC01-C-01 | PKG | 02738 | HYDRAULIC CYLINDER | MC01 |  | LIFT HOIST | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-FCV-01 | MC01-F-01 | PKG | 02738 | FLOW CONTROL VALVE | MC01 |  | HOIST OPTION | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-01 | MC01-M-01 | PKG | 02738 | 3 WAY MANUAL VALVE | MC01 PANEL |  | INLET A/B SELECT | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-02 | MC01-M-02 | PKG | 02738 | 3 WAY MANUAL VALVE | MC01 |  | COLUMN INLET | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-03 | MC01-M-03 | PKG | 02738 | MANUAL VALVE | MC01 |  | COLUMN VENT | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-04 | MC01-M-04 | PKG | 02738 | MANUAL VALVE | MC01 |  | COLUMN VAC BREAK | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-05 | MC01-M-05 | PKG | 02738 | MANUAL VALVE | MC01 |  | VACUUM BREAK | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-06 | MC01-M-06 | PKG | 02738 | 3 WAY MANUAL VALVE | MC01 PANEL |  | OUTLET 1 / 2 SELECT | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-07 | MC01-M-07 | PKG | 02738 | MANUAL VALVE | MC01 PANEL |  | RADIAL COMP TANK INLET | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-08 | MC01-M-08 | PKG | 02738 | 3 WAY MANUAL VALVE | MC01 PANEL |  | MC01-P1 AIR SUPPLY/VENT | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-09 | MC01-M-09 | PKG | 02738 | 3 WAY MANUAL VALVE | MC01 PANEL |  | TANK N2 SUPPLY/EXHAUST | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-10 | MC01-M-10 | PKG | 02738 | MANUAL VALVE | MC01 |  | COLUMN DRAIN | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-11 | MC01-M-11 | PKG | 02738 | MANUAL NEEDLE VALVE | MC01 PANEL |  | MC01-P1 RATE | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-12 | MC01-M-12 | PKG | 02738 | MANUAL VALVE | MC01 |  | AIR TO MC01-P2 | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-MV-13 | MC01-M-13 | PKG | 02738 | MANUAL VALVE | MC01 PANEL |  | HOIST LIFT/LOWER | REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-PG-01 | MC01-P-01 | PKG | 02738 | PRESSURE GAUGE | MC01 PANEL |  | MC01-P1 OUTLET | -: 0 to 200psi; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-PRR-01 | MC01-P-01A | PKG | 02738 | AIR PRESSURE REGULATOR | MC01 |  | MAIN AIR SUPPLY | -: set @ 75psi; -: +/- 10%; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-PSV-01 | MC01-P-01S | PKG | 02738 | PRESSURE RELIEF VALVE | MC01 |  | AIR SUPPLY RELIEF | -: set @ 100psi; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-PG-02 | MC01-P-02 | PKG | 02738 | PRESSURE GAUGE | MC01 PANEL |  | COLUMN PRESSURE | -: 0 to 200psi; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-PSV-02 | MC01-P-02S | PKG | 02738 | PRESSURE RELIEF VALVE | MC01 |  | COLUMN RELIEF | -: set @ 170psi; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-PG-03 | MC01-P-03 | PKG | 02738 | PRESSURE GAUGE | MC01 |  | TANK PRESSURE | -: 0 to 200psi; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-PSV-03 | MC01-P-03S | PKG | 02738 | PRESSURE RELIEF VALVE | MC01 |  | TANK RELIEF | -: set @ 125psi; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-PSV-04 | MC01-P-04 | PKG | 02738 | PRESSURE RELIEF VALVE | MC01 |  | HYDRAULIC RELIEF | -: set @ 600psi; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MC01 | MC01-PSV-05 | MC01-P-05 | PKG | 02738 | PRESSURE RELIEF VALVE | MC01 |  | HYDRAULIC RELIEF | -: set @ 600psi; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [5 empty] | MOBILE CHROMAT UNIT |  | 01
MCCPE | MCCPE-KWH-001 | MCCPE-K-001 | PLC | N/A | POWER TOTALISER | HVAC MCC |  | MCC-PE Kw/h | PKG: 8846; I.S: N.I.S |  |  | 0 | [5 empty] | PULSED INPUT | AI | 01
MCCP | MCCP-KWH-001 | MCCP-K-001 | PLC | N/A | POWER TOTALISER | HVAC MCC |  | MCC-P Kw/h | PKG: 8842; I.S: N.I.S |  |  | 0 | [5 empty] | PULSED INPUT | AI | 01
MCD01 | MCD01-CV-001 | MCD01-C-001 | PKG | 107-HA | SOLENOID VALVE | MCD01 | 107.0 | N2 TO FILTER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-DA-001 | MCD01-D-001 | LCP | 107-HA | INDICATOR - MOTOR TRIPPED | MCD01 LOCAL PANEL | 107.0 | MOTOR TRIPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-DI-001 | MCD01-D-001A | LCP | 107-HA | INDICATOR - MOTOR RUN FWD | MCD01 LOCAL PANEL | 107.0 | MOTOR RUN FORWARD | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-DI-002 | MCD01-D-002 | LCP | 107-HA | INDICATOR - MOTOR RUN REV | MCD01 LOCAL PANEL | 107.0 | MOTOR RUN REVERSE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HV-001 | MCD01-H-001 | PKG | 107-HA | DISCHARGE VALVE | MCD01/100 | 107.0 | DISCHARGE VALVE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HZLC-001 | MCD01-H-001 | LCP | 107-HA | INDICATOR LAMP - CLOSED | MCD01 LOCAL PANEL | 107.0 | DISCHARGE VALVE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HZLO-001 | MCD01-H-001 | LCP | 107-HA | INDICATOR LAMP - OPEN | MCD01 LOCAL PANEL | 107.0 | DISCHARGE VALVE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HZSC-001 | MCD01-H-001 | PKG | 107-HA | SWITCH - DISCHARGE CLOSED | MTD. ON VALVE |  | DISCHARGE VALVE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
MCD01 | MCD01-HZSO-001 | MCD01-H-001 | PKG | 107-HA | SWITCH - DISCHARGE OPEN | MTD. ON VALVE |  | DISCHARGE VALVE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
MCD01 | MCD01-HS-002 | MCD01-H-002 | LCP | 107-HA | SWITCH - DUST FILTER CLEAN | MCD01 LOCAL PANEL | 107.0 | DUST FILTER CLEAN | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HS-003 | MCD01-H-003 | LCP | 107-HA | SWITCH - MOTOR RUN FWD | MCD01 LOCAL PANEL | 107.0 | MOTOR RUN FORWARD | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HS-004 | MCD01-H-004 | LCP | 107-HA | SWITCH - MOTOR RUN REV | MCD01 LOCAL PANEL | 107.0 | MOTOR RUN REVERSE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HS-005 | MCD01-H-005 | LCP | 107-HA | SWITCH - MOTOR STOP | MCD01 LOCAL PANEL | 107.0 | MOTOR STOP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HS-006 | MCD01-H-006 | LCP | 107-HA | SWITCH - LAMP TEST | MCD01 LOCAL PANEL | 107.0 | LAMP TEST | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HS-007 | MCD01-H-007 | LCP | 107-HA | SWITCH - EMERGENCY STOP | MCD01 LOCAL PANEL | 107.0 | EMERGENCY STOP | -: -; -: -; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HS-008 | MCD01-H-008 | LCP | 107-HA | SWITCH - MAIN SUPPLY | MCD01 LOCAL PANEL | 107.0 | MAIN SUPPLY | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-HS-009 | MCD01-H-009 | LCP | 107-HA | SWITCH - SIGHT LAMP ON/OFF | MCD01 LOCAL PANEL | 107.0 | SIGHT LAMP ON/OFF | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-II-001 | MCD01-I-001 | LCP | 107-HA | INDICATOR - CURRENT | MCD01 LOCAL PANEL | 107.0 | CURRENT INDICATOR | -: 0 to 4 amp; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-KI-001 | MCD01-K-001 | LCP | 107-HA | INDICATOR - TIME | MCD01 LOCAL PANEL | 107.0 | ELAPSED TIME | -: hours; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-PI-001 | MCD01-P-001 | PKG | 107-HA | PRESSURE GAUGE | MCD01 | 107.0 | PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-PSV-003 | MCD01-P-003 | PKG | 107-HA | PRESSURE RELIEF VALVE | MCD01 | 107.0 | HOT WATER RELIEF | -: 5 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-SE-001 | MCD01-S-001 | PKG | 107-HA | ELEMENT - SPEED | MCD01 | 107.0 | AGITATOR SPEED | -: 0 to 190 rpm; -: -; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-SI-001 | MCD01-S-001 | LCP | 107-HA | INDICATOR - SPEED | MCD01 LOCAL PANEL | 107.0 | AGITATOR SPEED | -: 0 to 190 rpm; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-TE-001 | MCD01-T-001 | PKG | 107-HA | ELEMENT - TEMPERATURE - RTD | MCD01 | 107.0 | TEMPERATURE | -: 0 to 100 degC; -: +/- 0.5%; REF: SHE; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-TI-001 | MCD01-T-001 | LCP | 107-HA | INDICATOR - TEMPERATURE | MCD01 LOCAL PANEL | 107.0 | TEMPERATURE | -: 0 to 100 degC; -: +/- 0.5%; REF: SHE; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-TT-001 | MCD01-T-001 | LCP | 107-HA | TRANSMITTER - TEMPERATURE | MCD01 | 107.0 | TEMPERATURE | -: 0 to 100 degC; -: +/- 0.5%; REF: SHE; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-YA-001 | MCD01-Y-001 | LCP | 107-HA | ALARM - COMMON | MCD01 LOCAL PANEL | 107.0 | DRYER OPEN | -: -; -: -; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-YS-001 | MCD01-Y-001 | PKG | 107-HA | SWITCH - POSITION | MCD01 | 107.0 | DRYER OPEN | -: -; -: -; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-YL-002 | MCD01-Y-002 | LCP | 107-HA | INDICATOR - CONE OPEN | MCD01 LOCAL PANEL | 107.0 | CONE OPEN | -: -; -: -; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCD01 | MCD01-YL-003 | MCD01-Y-003 | LCP | 107-HA | INDICATOR - SIGHT LAMP ON | MCD01 LOCAL PANEL | 107.0 | SIGHT LAMP ON | -: -; -: -; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
MCE01 | MCE01-CV-001 | MCE01-C-001 | PKG | 107-HQ | BALL VALVE - ON/OFF - F.C. | MCE01 | 174.0 | HEAVIES OUTLET ISOLATION |  | N/A | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | [5 empty] | 01
MCE01 | MCE01-CY-001 | MCE01-C-001 | LCP | 107-HQ | SOLENOID VALVE | MCE01 | 174.0 | FOR ALL ISOLATION VALVE | -: N/A |  |  |  |  | PACKAGE | [5 empty] | 01
MCE01 | MCE01-CV-002 | MCE01-C-002 | PKG | 107-HQ | BALL VALVE - ON/OFF - F.C. | MCE01 | 174.0 | LIGHTS OUTLET ISOLATION |  | N/A | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | [5 empty] | 01
MCE01 | MCE01-CV-003 | MCE01-C-003 | PKG | 107-HQ | BALL VALVE - ON/OFF - F.C. | MCE01 | 174.0 | HEAVIES INLET ISOLATION |  | N/A | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | [5 empty] | 01
MCE01 | MCE01-CV-004 | MCE01-C-004 | PKG | 107-HQ | BALL VALVE - ON/OFF - F.C. | MCE01 | 174.0 | LIGHTS INLET ISOLATION |  | N/A | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | AMP-3 |  |  |  |  | 01
MCE01 | MCE01-CV-005 | MCE01-C-005 | PKG | 107-HQ | BALL VALVE - ON/OFF - F.C. | MCE01 | 174.0 | VENT ISOLATION |  | N/A |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | UTIL | XOMOX TUFLIN | [5 empty] | 01
MCE01 | MCE01-DIC-001 | MCE01-D-001 | LCP | 107-HQ | MOTOR CONTROL | MCE01 | 174.0 | AGITATOR MOTOR CONTROLLER | L14380 | 0 to 3000rpm | 1% |  | By Request | - | - | N.I.S | DI | 1 |  | 35 | UTIL | PACKAGE | [5 empty] | 01
MCE01 | MCE01-FI-001 | MCE01-F-001 | LCP | 107-HQ | VA FLOW METER | MCE01 | 174.0 | PURGE N2 FLOW INDICATION | PKG: L14380; -: 0-180 Nl/hr; -: 1%; REQ: By Request |  |  |  |  | PACKAGE | [5 empty] | 01
MCE01 | MCE01-FSL-001 | MCE01-F-001 | LCP | 107-HQ | SWITCH ON VA FLOW METER | MCE01 | 174.0 | PURGE N2 LOW FLOW | PKG: L14380; -: On to off; -: 1%; REF: SHE; REQ: By Request |  |  |  |  | PACKAGE | [5 empty] | 01
MCE01 | MCE01-FI-002 | MCE01-F-002 | PKG | 107-HQ | MASS FLOW METER / INDICATOR | MCE01 | 174.0 | HEAVIES INLET FLOW | L14380 | 0-400 kg/hr | 5% |  | 60 | - | - | I.S | DO | 1 |  | 41 | UTIL | ENDRESS + HAUSER | Promass 80 |  |  |  |  | 01
MCE01 | MCE01-FI-003 | MCE01-F-003 | PKG | 107-HQ | MASS FLOW METER / INDICATOR | MCE01 | 174.0 | LIGHTS INLET FLOW | L14380 | 0-400 kg/hr | 5% |  | 60 | - | - | I.S | DI | 1 |  | 31 | UTIL | ENDRESS + HAUSER | Promass 80 |  |  |  |  | 01
MCE01 | MCE01-PSL-001 | MCE01-P-001 | LCP | 107-HQ | PRESSURE SWITCH | MCE01 | 174.0 | N2 PRESSUER LOW | PKG: L14380; -: 0 to 500mbar/actuating point 5; -: 5%; REF: SHE; REQ: By Request |  |  |  |  | PACKAGE | [5 empty] | 01
MCE01 | MCE01-PSH-002 | MCE01-P-002 | LCP | 107-HQ | PRESSURE SWITCH | MCE01 | 174.0 | N2 PRESSUER HIGH | PKG: L14380; -: 0 to 500mbar/actuating point 5; -: 5%; REF: SHE; REQ: By Request |  |  |  |  | PACKAGE | [5 empty] | 01
MCE01 | MCE01-PIT-003 | MCE01-P-003 | PKG | 107-HQ | PRESSURE TRANSMITTER WITH INDICATOR | MCE01 | 174.0 | CENTRIFUGUE PRESSURE | L14380 | 0 to 50mbar | 1% | OPS | 24 | - | - | I.S | DI | 1 |  | 31 | UTIL | ROSEMOUNT | 3051 S |  |  |  |  | 01
MCE01 | MCE01-PSHL-003 | MCE01-P-003 | LCP | 107-HQ | TRIPAMP | MCE01 | 174.0 | OVER / UNDER PRESSURE TRIP | L14380 | 0 to 100% | 2% | OPS | 24 | - | - | [6 empty] | PEPPERL + FUCHS | KFD2-CRG-Ex1.0 |  |  |  |  | 01
MCE01 | MCE01-SC-002 | MCE01-S-001 | LCP | 107-HQ | POTENTIOMETER | MCE01 | 174.0 | AGITATOR SPEED ADJUSTMENT | L14380 | 0 to 3000rpm | 1% | N/A | By Request | - | - | [6 empty] | PACKAGE | [5 empty] | 01
MCE01 | MCE01-SI-001 | MCE01-S-001 | LCP | 107-HQ | DIGITAL INDICATOR | MCE01 | 174.0 | AGITATOR SPEED | L14380 | 0-3000 rpm | 5% | N/A | By Request | - | - | [6 empty] | PACKAGE | [5 empty] | 01
MCE01 | MCE01-TE-001 | MCE01-T-001 | PKG | 107-HQ | PT100 PROBE | MCE01 | 174.0 | HOTEST POINT MONITOR | L14380 | 0 to 200degC | 1% | SHE | By Request | F | Ops | N.I.S | DO | 1 |  | 42 | UTIL | PACKAGE | [5 empty] | 01
MCE01 | MCE01-TSH-001 | MCE01-T-001 | LCP | 107-HQ | TRIPAMP | MCE01 | 174.0 | HOTEST POINT TEMP' SWITCH | L14380 | 0 to 200degC | 1% | SHE | By Request | C | Ref | [6 empty] | PEPPERL + FUCHS | KFD2-GU-EX1 |  |  |  |  | 01
MCF05 | MCF05-PI-001 | MCF05-P-001 | FLD | 107-HL | INDICATOR - PRESSURE | MCF05 | 139.5 | TANK PRESSURE | REQ: By Request; F: C |  |  |  |  | WIKA | 63mm c/w diaphragm |  |  |  |  | 01
MCF10 | MCF10-PI-001 | MCF10-P-001 | PKG | 107-HR | INDICATOR - PRESSURE | MCF10 | 139.10 | INLET PRESSURE | REQ: By Request; F: C |  |  |  |  | Wika | 232-50 / 990-22. |  |  |  |  | 01
MCF10 | MCF10-PI-002 | MCF10-P-002 | PKG | 107-HR | INDICATOR - PRESSURE | MCF10 | 139.10 | OUTLET PRESSURE | REQ: By Request; F: C |  |  |  |  | Wika | 232-50 / 990-22. |  |  |  |  | 01
MCF13 | MCF13-PI-001 | MCF13-P-001 | FLD | 107-HK | INDICATOR - PRESSURE | MCF13 | 139.13 | TANK PRESSURE | REQ: By Request; F: C |  |  |  |  | ARMATURENBAU | 40mm c/w diaphragm |  |  |  |  | 01
MCF19 | MCF19-PI-001 | MCF19-P-001 | FLD | 107-HK | INDICATOR - PRESSURE | MCF19 | 139.19 | TANK PRESSURE | REQ: By Request; F: C |  |  |  |  | WIKA | DIAPHRAGM MODEL: 990.27 |  |  |  |  | 01
MCF20 | MCF20-PI-001 | MCF20-P-001 | FLD | 107-HK | INDICATOR - PRESSURE | MCF20 | 139.2 | INLET PRESSURE | -: -1 to 5barg; -: 1%; REF: REF; REQ: By Request |  |  |  |  | WIKA |  | T2201-DS-PI-001 |  |  |  |  | v16
MCF20 | MCF20-PI-002 | MCF20-P-002 | FLD | 107-HK | INDICATOR - PRESSURE | MCF20 | 139.2 | OUTLET PRESSURE | -: -1 to 5barg; -: 1%; REF: REF; REQ: By Request |  |  |  |  | WIKA |  | T2201-DS-PI-001 |  |  |  |  | v16
MCP01 | MCP01-PI-001 | MCP01-P-001 | FLD | 107-PB | Pressure indicator (mounted on regulator PRV01) | Service area | 155.0 | CIP nitrogen supply inertion pressure | -: 0 to 100 mbarg |  |  |  |  | Esme | [5 empty] | 01
MCP01 | MCP01-PRV-001 | MCP01-P-001 | FLD | 107-PB | Pressure regulator | Service area | 155.0 | CIP nitrogen supply inertion pressure | [19 empty] | 01 | bar: PKG
MCP01 | MCP01-PI-002 | MCP01-P-002 | FLD | 107-PB | Pressure indicator (mounted on regulator PRV02) | CIP Skid | 155.0 | CIP pump air pressure | [19 empty] | 01 | bar: PKG
MCP01 | MCP01-PRV-002 | MCP01-P-002 | FLD | 107-PB | Pressure regulator | CIP Skid | 155.0 | CIP pump air pressure | [19 empty] | 01 | bar: PKG
MCP01 | MCP01-PI-004 | MCP01-P-004 | FLD | 107-PB | Pressure indicator | CIP skid | 155.0 | CIP pump discharge pressure | -: 0 to 7 barg |  |  |  |  | WIKA | 432.50.100 |  |  |  |  | 01
MCP01 | MCP01-PI-005 | MCP01-P-005 | FLD | 107-PB | Pressure indicator | CIP skid | 155.0 | CIP clean solvent vessel pressure | -: 0 to 100 mbarg |  |  |  |  | WIKA | 432.56.100 |  |  |  |  | 01
MCP01 | MCP01-PI-006 | MCP01-P-006 | FLD | 107-PB | Pressure indicator | CIP skid | 155.0 | CIP waste solvent vessel pressure | -: 0 to 100 mbarg |  |  |  |  | WIKA | 432.56.100 |  |  |  |  | 01
MCP01 | MCP01-PSV-001 | MCP01-PSV-001 | FLD | 107-PB | Pressure relief valve | Mounted on MCP01-ST1 | 155.0 | ST1 Pressure relief valve | -: 6.0 barg |  |  |  |  | STAITECH | Type 483 |  |  |  |  | 01
MCP01 | MCP01-PSV-002 | MCP01-PSV-002 | FLD | 107-PB | Pressure relief valve | Mounted on MCP01-ST2 | 155.0 | ST2 Pressure relief valve | -: 6.0 barg |  |  |  |  | STAITECH | Type 483 |  |  |  |  | 01
MCP01 | MCP01-PSV-003 | MCP01-PSV-003 | FLD | 107-PB | Pressure relief valve |  | 155.0 | CIP pump air supply pressure relief valve | -: 5.0 barg |  |  |  |  | NORGREN | V64H-EGD-RMN |  |  |  |  | 01
MCP01 | MCP01-CV-001 | MCP-C-001 | FLD | 107-PB | CIP pump air supply reset valve | 25-CA-SS1U-0-9028478 | 155.0 | CIP pump air supply reset | [19 empty] | 01 | bar: PKG
MCP01 | MCP01-HS-001 | MCP-C-001 | FLD | 107-PB | CIP pump air supply reset push button/solenoid valve | Service area | 155.0 | CIP pump air supply reset | [13 empty] | NORGREN | 03041502 |  |  |  |  | 01 | bar: PKG
MCP01 | MCP01-XV-001A | MCP-C-001 | FLD | 107-PB | CIP pump air supply reset latching solenoid valve | Service area | 155.0 | CIP pump air supply reset | [13 empty] | NORGREN | S/667/40 |  |  |  |  | 01 | bar: PKG
MCP01 | MCP01-CV-002 | MCP-C-002 | FLD | 107-PB | CIP Vent 3-way valve | 25-SV-GR1A-0-9027250 | 155.0 | CIP Vent 3-way valve | PKG: 12438 |  |  |  |  | Habonim | [5 empty] | 01
MCP01 | MCP01-CY-002A | MCP-C-002 | FLD | 107-PB | CIP Vent 3-way valve solenoid valve A | Mounted on valve | 155.0 | CIP Vent 3-way valve | PKG: 12438 |  |  |  |  | RGS | E2519CA00B |  |  |  |  | 01
MCP01 | MCP01-CY-002B | MCP-C-002 | FLD | 107-PB | CIP Vent 3-way valve solenoid valve B | Mounted on valve | 155.0 | CIP Vent 3-way valve | PKG: 12438 |  |  |  |  | RGS | E2519CA00B |  |  |  |  | 01
MCP01 | MCP01-CYY-002A | MCP-C-002 | MI01-MCP | 107-PB | IS Barrier | MI01 Main Control Panel | 155.0 | CIP Vent 3-way valve | PKG: 12438 |  |  |  |  | PEPPERL + FUCHS | KFD0-CS-Ex2.51P |  |  |  |  | 01
MCP01 | MCP01-CYY-002B | MCP-C-002 | MI01-MCP | 107-PB | IS Barrier | MI01 Main Control Panel | 155.0 | CIP Vent 3-way valve | PKG: 12438 |  |  |  |  | PEPPERL + FUCHS | KFD0-CS-Ex2.51P |  |  |  |  | 01
MCP01 | MCP01-ZS0-002 | MCP-C-002 | FLD | 107-PB | CIP Vent 3-way valve position sensor A | Mounted on valve | 155.0 | CIP Vent 3-way valve | PKG: 12438 |  |  |  |  | PEPPERL + FUCHS | [5 empty] | 01
MCP01 | MCP01-ZSC-002 | MCP-C-002 | FLD | 107-PB | CIP Vent 3-way valve position sensor B | Mounted on valve | 155.0 | CIP Vent 3-way valve | PKG: 12438 |  |  |  |  | PEPPERL + FUCHS | [5 empty] | 01
MCP01 | MCP01-ZY0-002 | MCP-C-002 | MI01-MCP | 107-PB | IS Barrier | MI01 Main Control Panel | 155.0 | CIP Vent 3-way valve | PKG: 12438 |  |  |  |  | PEPPERL + FUCHS | KFD2-ST2-Ex2 |  |  |  |  | 01
MCP01 | MCP01-ZYC-002 | MCP-C-002 | MI01-MCP | 107-PB | IS Barrier | MI01 Main Control Panel | 155.0 | CIP Vent 3-way valve | PKG: 12438 |  |  |  |  | PEPPERL + FUCHS | KFD2-ST2-Ex2 |  |  |  |  | 01
MCR01 | MCR01-CV-001A | MCR01-C-001A | PKG | 107-SD | CONTROL VALVE | MCR01 | 175.0 | PROCESS BACK PRESSURE CONTROL | -: 0 to 50 %; REF: N/A; REQ: N/A; F: N/A; I.S: I.S | AO |  |  |  | SAMSON | 3510 | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-001B | MCR01-C-001B | PKG | 107-SD | CONTROL VALVE | MCR01 | 175.0 | PROCESS BACK PRESSURE CONTROL | -: 50 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SAMSON | 3510 | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-002 | MCR01-C-002 | PKG | 107-SD | ACTUATED 3 PORT DIVERTER VALVE | MCR01 | 175.0 | PROCESS WASTE/PRODUCT DIVERTER | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-002 | MCR01-C-002 | PKG | 107-SD | SOLENOID VALVE | RACK MOUNTED | 175.0 | PROCESS WASTE/PRODUCT DIVERTER | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSC-002 | MCR01-C-002 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | PROCESS TO WASTE | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSO-002 | MCR01-C-002 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | PROCESS TO PRODUCT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-014 | MCR01-C-014 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF COLD RETURN | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33O | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-014 | MCR01-C-014 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV014 AND CV015 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-015 | MCR01-C-015 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF HOT RETURN | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33C | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-024 | MCR01-C-024 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF COLD RETURN | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33O | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-024 | MCR01-C-024 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV024 AND CV025 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-025 | MCR01-C-025 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF HOT RETURN | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33C | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-034 | MCR01-C-034 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF COLD RETURN | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33O | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-034 | MCR01-C-034 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV034 AND CV035 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-035 | MCR01-C-035 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF HOT RETURN | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33C | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-041 | MCR01-C-041 | PKG | 107-SD | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P040 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-041 | MCR01-C-041 | PKG | 107-SD | SOLENOID VALVE | RACK MOUNTED | 175.0 | P040 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSC-041 | MCR01-C-041 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P040 SUCTION ISOL VALVE CLOSED | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSO-041 | MCR01-C-041 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P040 SUCTION ISOL VALVE OPEN | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-051 | MCR01-C-051 | PKG | 107-SD | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P050 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-051 | MCR01-C-051 | PKG | 107-SD | SOLENOID VALVE | RACK MOUNTED | 175.0 | P050 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSC-051 | MCR01-C-051 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P050 SUCTION ISOL VALVE CLOSED | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSO-051 | MCR01-C-051 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P050 SUCTION ISOL VALVE OPEN | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-061 | MCR01-C-061 | PKG | 107-SD | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P060 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-061 | MCR01-C-061 | PKG | 107-SD | SOLENOID VALVE | RACK MOUNTED | 175.0 | P060 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSC-061 | MCR01-C-061 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P060 SUCTION ISOL VALVE CLOSED | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSO-061 | MCR01-C-061 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P060 SUCTION ISOL VALVE OPEN | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-071 | MCR01-C-071 | PKG | 107-SD | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P070 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-071 | MCR01-C-071 | PKG | 107-SD | SOLENOID VALVE | RACK MOUNTED | 175.0 | P070 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSC-071 | MCR01-C-071 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P070 SUCTION ISOL VALVE CLOSED | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSO-071 | MCR01-C-071 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P070 SUCTION ISOL VALVE OPEN | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-081 | MCR01-C-081 | PKG | 107-SD | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P080 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-081 | MCR01-C-081 | PKG | 107-SD | SOLENOID VALVE | RACK MOUNTED | 175.0 | P080 SUCTION ISOLATION VALVE | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSC-081 | MCR01-C-081 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P080 SUCTION ISOL VALVE CLOSED | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-ZSO-081 | MCR01-C-081 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P080 SUCTION ISOL VALVE OPEN | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-111 | MCR01-C-111 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF INLET TO PFR 100 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-111 | MCR01-C-111 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV111 AND CV112 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-112 | MCR01-C-112 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF OUTLET FROM PFR 100 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-121 | MCR01-C-121 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF INLET TO PFR 100 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-121 | MCR01-C-121 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV121 AND CV122 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-122 | MCR01-C-122 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF OUTLET FROM PFR 100 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-131 | MCR01-C-131 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF INLET TO PFR 100 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-131 | MCR01-C-131 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV131 AND CV132 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-132 | MCR01-C-132 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF OUTLET FROM PFR 100 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-211 | MCR01-C-211 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF INLET TO PFR 200 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-211 | MCR01-C-211 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV211 AND CV212 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-212 | MCR01-C-212 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF OUTLET FROM PFR 200 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-221 | MCR01-C-221 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF INLET TO PFR 200 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-221 | MCR01-C-221 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV221 AND CV222 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-222 | MCR01-C-222 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF OUTLET FROM PFR 200 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-231 | MCR01-C-231 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF INLET TO PFR 200 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-231 | MCR01-C-231 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV231 AND CV232 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-232 | MCR01-C-232 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF OUTLET FROM PFR 200 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-311 | MCR01-C-311 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF INLET TO PFR 300 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-311 | MCR01-C-311 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV311 AND CV312 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-312 | MCR01-C-312 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF OUTLET FROM PFR 300 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-321 | MCR01-C-321 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF INLET TO PFR 300 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-321 | MCR01-C-321 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV321 AND CV322 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-322 | MCR01-C-322 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF OUTLET FROM PFR 300 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-331 | MCR01-C-331 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF INLET TO PFR 300 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-331 | MCR01-C-331 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV331 AND CV332 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-332 | MCR01-C-332 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF OUTLET FROM PFR 300 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-411 | MCR01-C-411 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF INLET TO PFR 400 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-411 | MCR01-C-411 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV411 AND CV412 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-412 | MCR01-C-412 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF OUTLET FROM PFR 400 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-421 | MCR01-C-421 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF INLET TO PFR 400 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-421 | MCR01-C-421 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV421 AND CV422 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-422 | MCR01-C-422 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF OUTLET FROM PFR 400 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-431 | MCR01-C-431 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF INLET TO PFR 400 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-431 | MCR01-C-431 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV431 AND CV432 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-432 | MCR01-C-432 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF OUTLET FROM PFR 400 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-511 | MCR01-C-511 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF INLET TO PFR 500 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-511 | MCR01-C-511 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV511 AND CV512 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-512 | MCR01-C-512 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF OUTLET FROM PFR 500 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-521 | MCR01-C-521 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF INLET TO PFR 500 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-521 | MCR01-C-521 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV521 AND CV522 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-522 | MCR01-C-522 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF OUTLET FROM PFR 500 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-531 | MCR01-C-531 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF INLET TO PFR 500 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-531 | MCR01-C-531 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV531 AND CV532 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-532 | MCR01-C-532 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF OUTLET FROM PFR 500 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-611 | MCR01-C-611 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF INLET TO PFR 600 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-611 | MCR01-C-611 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV611 AND CV612 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-612 | MCR01-C-612 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 010 HTF OUTLET FROM PFR 600 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-621 | MCR01-C-621 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF INLET TO PFR 600 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-621 | MCR01-C-621 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV621 AND CV622 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-622 | MCR01-C-622 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 020 HTF OUTLET FROM PFR 600 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CV-631 | MCR01-C-631 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF INLET TO PFR 600 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-CY-631 | MCR01-C-631 | LCP | 107-SA | SOLENOID VALVE | RACK MOUNTED | 175.0 | VALVE CV631 AND CV632 | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-CV-632 | MCR01-C-632 | PKG | 107-SA | ACTUATED 2 PORT VALVE | MCR01 | 175.0 | P 030 HTF OUTLET FROM PFR 600 | REF: N/A; REQ: N/A; F: N/A |  |  |  |  | SWAGELOK | SS 63TWP8P10 33CDM | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-DIC-010 | MCR01-D-010 | LCP | 107-SA | INDICATING CONTR. - MOTOR DRIVE |  | 175.0 | P 010 PUMP | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DS-010 | MCR01-D-010 | LCP | 107-SA | DRIVE - AVAILABLE | LCP | 175.0 | P 010 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DY-010 | MCR01-D-010 | LCP | 107-SA | DRIVE - RUNNING | LCP | 175.0 | P 010 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DYC-010 | MCR01-D-010 | LCP | 107-SA | DRIVE - START/STOP | LCP | 175.0 | P 010 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DIC-020 | MCR01-D-020 | LCP | 107-SA | INDICATING CONTR. - MOTOR DRIVE |  | 175.0 | P 020 PUMP | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DS-020 | MCR01-D-020 | LCP | 107-SA | DRIVE - AVAILABLE | LCP | 175.0 | P 020 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DY-020 | MCR01-D-020 | LCP | 107-SA | DRIVE - RUNNING | LCP | 175.0 | P 020 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DYC-020 | MCR01-D-020 | LCP | 107-SA | DRIVE - START/STOP | LCP | 175.0 | P 020 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DIC-030 | MCR01-D-030 | LCP | 107-SA | INDICATING CONTR. - MOTOR DRIVE |  | 175.0 | P 030 PUMP | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DS-030 | MCR01-D-030 | LCP | 107-SA | DRIVE - AVAILABLE | LCP | 175.0 | P 030 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DY-030 | MCR01-D-030 | LCP | 107-SA | DRIVE - RUNNING | LCP | 175.0 | P 030 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DYC-030 | MCR01-D-030 | LCP | 107-SA | DRIVE - START/STOP | LCP | 175.0 | P 030 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DIC-040 | MCR01-D-040 | LCP | 107-SD | INDICATING CONTR. - MOTOR DRIVE |  | 175.0 | P 040 PUMP | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DS-040 | MCR01-D-040 | LCP | 107-SC | DRIVE - AVAILABLE | LCP | 175.0 | P 040 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DY-040 | MCR01-D-040 | LCP | 107-SC | DRIVE - RUNNING | LCP | 175.0 | P 040 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DYC-040 | MCR01-D-040 | LCP | 107-SD | DRIVE - START/STOP | LCP | 175.0 | P 040 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DIC-050 | MCR01-D-050 | LCP | 107-SD | INDICATING CONTR. - MOTOR DRIVE |  | 175.0 | P 050 PUMP | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DS-050 | MCR01-D-050 | LCP | 107-SC | DRIVE - AVAILABLE | LCP | 175.0 | P 050 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DY-050 | MCR01-D-050 | LCP | 107-SC | DRIVE - RUNNING | LCP | 175.0 | P 050 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DYC-050 | MCR01-D-050 | LCP | 107-SD | DRIVE - START/STOP | LCP | 175.0 | P 050 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DIC-060 | MCR01-D-060 | LCP | 107-SD | INDICATING CONTR. - MOTOR DRIVE |  | 175.0 | P 060 PUMP | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DS-060 | MCR01-D-060 | LCP | 107-SC | DRIVE - AVAILABLE | LCP | 175.0 | P 060 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DY-060 | MCR01-D-060 | LCP | 107-SC | DRIVE - RUNNING | LCP | 175.0 | P 060 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DYC-060 | MCR01-D-060 | LCP | 107-SD | DRIVE - START/STOP | LCP | 175.0 | P 060 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DIC-070 | MCR01-D-070 | LCP | 107-SD | INDICATING CONTR. - MOTOR DRIVE |  | 175.0 | P 070 PUMP | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DS-070 | MCR01-D-070 | LCP | 107-SC | DRIVE - AVAILABLE | LCP | 175.0 | P 070 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DY-070 | MCR01-D-070 | LCP | 107-SC | DRIVE - RUNNING | LCP | 175.0 | P 070 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DYC-070 | MCR01-D-070 | LCP | 107-SD | DRIVE - START/STOP | LCP | 175.0 | P 070 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DIC-080 | MCR01-D-080 | LCP | 107-SD | INDICATING CONTR. - MOTOR DRIVE |  | 175.0 | P 080 PUMP | REF: N/A; REQ: N/A; F: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DS-080 | MCR01-D-080 | LCP | 107-SC | DRIVE - AVAILABLE | LCP | 175.0 | P 080 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DY-080 | MCR01-D-080 | LCP | 107-SC | DRIVE - RUNNING | LCP | 175.0 | P 080 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-DYC-080 | MCR01-D-080 | LCP | 107-SD | DRIVE - START/STOP | LCP | 175.0 | P 080 PUMP | REF: N/A; REQ: N/A; F: N/A; I.S: N.I.S | DO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-FT-001 | MCR01-F-001 | PKG | 107-SD | FLOW TRANSMITTER | MCR01 | 175.0 | MCR01 OUTLET FLOW | -: 0 to 400 ml/min; -: +/-1%; REQ: 60; F: C; I.S: I.S | AI |  |  |  | EMERSON | ELITE CMF025 | KF002/P3 |  | Removed from Use |  | 50
MCR01 | MCR01-FT-001A | MCR01-F-001A | PKG | 107-SD | FLOW TRANSMITTER | MCR01 | 175.0 | MCR01 OUTLET FLOW | -: 0 to 400 ml/min; -: +/-1%; REQ: 60; F: C; I.S: I.S | AI |  |  |  | EMERSON | ELITE CMF010 | KF002/P3 |  | Removed from Use |  | 50
MCR01 | MCR01-FS-011 | MCR01-F-011 | PKG | 107-SA | FLOW SWITCH | MCR01 | 175.0 | P010 HTF FLOW | REF: Ref; REQ: By Req; F: F; I.S: I.S | [8 empty] | Removed from Use |  | 50
MCR01 | MCR01-FS-021 | MCR01-F-021 | PKG | 107-SA | FLOW SWITCH | MCR01 | 175.0 | P020 HTF FLOW | REF: Ref; REQ: By Req; F: F; I.S: I.S | [8 empty] | Removed from Use |  | 50
MCR01 | MCR01-FS-031 | MCR01-F-031 | PKG | 107-SA | FLOW SWITCH | MCR01 | 175.0 | P030 HTF FLOW | REF: Ref; REQ: By Req; F: F; I.S: I.S | [8 empty] | Removed from Use |  | 50
MCR01 | MCR01-FT-041 | MCR01-F-041 | PKG | 107-SD | FLOW TRANSMITTER | MCR01 | 175.0 | P 040 OUTLET FLOW | -: 0 to 400 ml/min; -: +/-1%; REQ: 60; F: C; I.S: I.S | AI |  |  |  | EMERSON | ELITE CMF025 | KF002/P3 |  | Removed from Use |  | 50
MCR01 | MCR01-FT-041A | MCR01-F-041A | PKG | 107-SD | FLOW TRANSMITTER | MCR01 | 175.0 | P 040 OUTLET FLOW | -: 0 to 400 ml/min; -: +/-1%; REQ: 60; F: C; I.S: I.S | AI |  |  |  | EMERSON | ELITE CMF010 | KF002/P3 |  | Removed from Use |  | 50
MCR01 | MCR01-FT-051 | MCR01-F-051 | PKG | 107-SD | FLOW TRANSMITTER | MCR01 | 175.0 | P 050 OUTLET FLOW | -: 0 to 400 ml/min; -: +/-1%; REQ: 60; F: C; I.S: I.S | AI |  |  |  | EMERSON | ELITE CMF010 | KF002/P3 |  | Removed from Use |  | 50
MCR01 | MCR01-FT-061 | MCR01-F-061 | PKG | 107-SD | FLOW TRANSMITTER | MCR01 | 175.0 | P 060 OUTLET FLOW | -: 0 to 400 ml/min; -: +/-1%; REQ: 60; F: C; I.S: I.S | AI |  |  |  | EMERSON | ELITE CMF010 | KF002/P3 |  | Removed from Use |  | 50
MCR01 | MCR01-FT-071 | MCR01-F-071 | PKG | 107-SD | FLOW TRANSMITTER | MCR01 | 175.0 | P 070 OUTLET FLOW | -: 0 to 400 ml/min; -: +/-1%; REQ: 60; F: C; I.S: I.S | AI |  |  |  | EMERSON | ELITE CMF010 | KF002/P3 |  | Removed from Use |  | 50
MCR01 | MCR01-FT-081 | MCR01-F-081 | PKG | 107-SD | FLOW TRANSMITTER | MCR01 | 175.0 | P 080 OUTLET FLOW | -: 0 to 400 ml/min; -: +/-1%; REQ: 60; F: C; I.S: I.S | AI |  |  |  | EMERSON | ELITE CMF010 | KF002/P3 |  | Removed from Use |  | 50
MCR01 | MCR01-FS-101 | MCR01-F-101 | PKG | 107-SA | FLOW SWITCH | MCR01 | 175.0 | PFR100 JACKET HTF FLOW SWITCH |  | 0-500 l/hr | +/- 5% | Ref | By Req | F |  | I.S |  | DI |  |  |  | KHRONE | H250 | KF0027/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-FS-201 | MCR01-F-201 | PKG | 107-SA | FLOW SWITCH | MCR01 | 175.0 | PFR200 JACKET HTF FLOW SWITCH |  | 0-500 l/hr | +/- 5% | Ref | By Req | F |  | I.S |  | DI |  |  |  | KHRONE | H250 | KF0027/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-FS-301 | MCR01-F-301 | PKG | 107-SA | FLOW SWITCH | MCR01 | 175.0 | PFR300 JACKET HTF FLOW SWITCH |  | 0-500 l/hr | +/- 5% | Ref | By Req | F |  | I.S |  | DI |  |  |  | KHRONE | H250 | KF0027/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-FS-401 | MCR01-F-401 | PKG | 107-SA | FLOW SWITCH | MCR01 | 175.0 | PFR400 JACKET HTF FLOW SWITCH |  | 0-500 l/hr | +/- 5% | Ref | By Req | F |  | I.S |  | DI |  |  |  | KHRONE | H250 | KF0027/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-FS-501 | MCR01-F-501 | PKG | 107-SA | FLOW SWITCH | MCR01 | 175.0 | PFR500 JACKET HTF FLOW SWITCH |  | 0-500 l/hr | +/- 5% | Ref | By Req | F |  | I.S |  | DI |  |  |  | KHRONE | H250 | KF0027/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-FS-601 | MCR01-F-601 | PKG | 107-SA | FLOW SWITCH | MCR01 | 175.0 | PFR600 JACKET HTF FLOW SWITCH |  | 0-500 l/hr | +/- 5% | Ref | By Req | F |  | I.S |  | DI |  |  |  | KHRONE | H250 | KF0027/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-001 | MCR01-H-001 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | COLD HTF LOOP BACK PR CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-002 | MCR01-H-002 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | HOT HTF LOOP BACK PR CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-003 | MCR01-H-003 | PKG | 107-SD | HAND 3 PORT DIVERTER VALVE | MCR01 | 175.0 | P 040 INLET FROM SOLVENT/PRODUCT | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSC-003 | MCR01-H-003 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P 040 INLET FROM SOLVENT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSO-003 | MCR01-H-003 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P 040 INLET FROM PRODUCT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-004 | MCR01-H-004 | PKG | 107-SD | HAND 3 PORT DIVERTER VALVE | MCR01 | 175.0 | P 050 INLET FROM SOLVENT/PRODUCT | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSC-004 | MCR01-H-004 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P 050 INLET FROM SOLVENT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSO-004 | MCR01-H-004 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P 050 INLET FROM PRODUCT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-005 | MCR01-H-005 | PKG | 107-SD | HAND 3 PORT DIVERTER VALVE | MCR01 | 175.0 | P 060 INLET FROM SOLVENT/PRODUCT | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSC-005 | MCR01-H-005 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P 060 INLET FROM SOLVENT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSO-005 | MCR01-H-005 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P 060 INLET FROM PRODUCT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-006 | MCR01-H-006 | PKG | 107-SD | HAND 3 PORT DIVERTER VALVE | MCR01 | 175.0 | P 070 INLET FROM SOLVENT/PRODUCT | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSC-006 | MCR01-H-006 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P 070 INLET FROM SOLVENT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSO-006 | MCR01-H-006 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P 070 INLET FROM PRODUCT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-007 | MCR01-H-007 | PKG | 107-SD | HAND 3 PORT DIVERTER VALVE | MCR01 | 175.0 | P 080 INLET FROM SOLVENT/PRODUCT | REF: N/A; REQ: N/A; F: N/A | [6 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSC-007 | MCR01-H-007 | PKG | 107-SD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 175.0 | P 080 INLET FROM SOLVENT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HZSO-007 | MCR01-H-007 | PKG | 107-SD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 175.0 | P 080 INLET FROM PRODUCT | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | KV0007/P5 |  | Removed from Use |  | 50
MCR01 | MCR01-HS-009 | MCR01-H-009 | LCP | 107-SC | HAND SWITCH | LCP | 175.0 | EMERGENCY STOP | REF: N/A; REQ: N/A; F: N/A; I.S: I.S | DI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-011 | MCR01-H-011 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | P 010 LOOP BACK PR CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-021 | MCR01-H-021 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | P 010 LOOP BACK PR CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-031 | MCR01-H-031 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | P 010 LOOP BACK PR CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-101 | MCR01-H-101 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | PFR 100 HTF FLOW CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-201 | MCR01-H-201 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | PFR 200 HTF FLOW CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-301 | MCR01-H-301 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | PFR 300 HTF FLOW CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-401 | MCR01-H-401 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | PFR 400 HTF FLOW CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-501 | MCR01-H-501 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | PFR 500 HTF FLOW CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-HCV-601 | MCR01-H-601 | PKG | 107-SA | FLOW CONTROL HAND VALVE | MCR01 | 175.0 | PFR 600 HTF FLOW CONTROL | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A |  |  |  |  | HABONIM | AN 47 P | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-PIT-001 | MCR01-P-001 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | PROCESS BACK PRESSURE |  | -1 to 10 barg | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PT-002 | MCR01-P-002 | PKG | 107-SA | PRESSURE TRANSMITTER | MCR01 | 175.0 | COLD HTF PRESSURE |  | 0 to 6 barg | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PSV-003 | MCR01-P-003 | PKG | 107-SA | PRESSURE RELIEF VALVE | MCR01 | 175.0 | HTF RETURN LOOP PRESSURE RELIEF | -: 9 barg; REF: N/A; REQ: N/A; F: F |  |  |  |  | BROADY | 2600 | KS0001/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-PT-003 | MCR01-P-003 | PKG | 107-SA | PRESSURE TRANSMITTER | MCR01 | 175.0 | HOT HTF PRESSURE |  | 0 to 6 barg | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PRV-004 | MCR01-P-004 | PKG | 107-SD | PRESSURE REDUCING VALVE | MCR01 | 175.0 | NITROGEN INLET TO SKID | REF: N/A; REQ: N/A; F: F | [6 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-PSV-005 | MCR01-P-005 | PKG | 107-SC | PRESSURE RELIEF VALVE | MCR01 | 175.0 | PROCESS INLET VALVE BY-PASS | -: 9 barg; REF: N/A; REQ: N/A; F: F |  |  |  |  | BROADY | 2600 | KS0001/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-PSV-006 | MCR01-P-006 | PKG | 107-SC | PRESSURE RELIEF VALVE | MCR01 | 175.0 | PROCESS INLET VALVE BY-PASS | REF: N/A; REQ: N/A; F: F |  |  |  |  | BROADY | 2600 | KS0001/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-DPI-011 | MCR01-P-011 | PKG | 107-SA | DIFFERENTIAL PRESSURE GAUGE | MCR01 | 175.0 | P 010 DIFFERENTIAL PRESSURE |  | 0-4 barg | +/- 5% | REF | By Req | C |  | N/A | [5 empty] | WIKA | 732.51 | KP0006-P11 |  | Removed from Use |  | 50
MCR01 | MCR01-DPI-021 | MCR01-P-021 | PKG | 107-SA | DIFFERENTIAL PRESSURE GAUGE | MCR01 | 175.0 | P 020 DIFFERENTIAL PRESSURE |  | 0-4 barg | +/- 5% | REF | By Req | C |  | N/A | [5 empty] | WIKA | 732.51 | KP0006-P11 |  | Removed from Use |  | 50
MCR01 | MCR01-DPI-031 | MCR01-P-031 | PKG | 107-SA | DIFFERENTIAL PRESSURE GAUGE | MCR01 | 175.0 | P 030 DIFFERENTIAL PRESSURE |  | 0-4 barg | +/- 5% | REF | By Req | C |  | N/A | [5 empty] | WIKA | 732.51 | KP0006-P11 |  | Removed from Use |  | 50
MCR01 | MCR01-PIT-042 | MCR01-P-042 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | P 040 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PIT-052 | MCR01-P-052 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | P 050 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PIT-062 | MCR01-P-062 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | P 060 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PIT-072 | MCR01-P-072 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | P 070 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PIT-082 | MCR01-P-082 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | P 080 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PT-101 | MCR01-P-101 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | PFR100 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | SHE | 12 | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PT-201 | MCR01-P-201 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | PFR200 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | SHE | 12 | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PT-301 | MCR01-P-301 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | PFR300 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | SHE | 12 | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PT-401 | MCR01-P-401 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | PFR400 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | SHE | 12 | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PT-402 | MCR01-P-402 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | PFR400 MID LENGTH PRESSURE |  | -1 to 10 barg | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PT-501 | MCR01-P-501 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | PFR500 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | SHE | 12 | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-PT-601 | MCR01-P-601 | PKG | 107-SD | PRESSURE TRANSMITTER | MCR01 | 175.0 | PFR600 OUTLET PRESSURE |  | -1 to 10 barg | +/- 1% | SHE | 12 | C |  | I.S |  | AI |  |  |  | ROSEMOUNT | 3051T | KP0001-P5 |  | Removed from Use |  | 50
MCR01 | MCR01-RO-011 | MCR01-R-011 | PKG | 107-SA | RESTRICTION ORIFICE | MCR01 | 175.0 | P010 HTF FLOW | REF: N/A; REQ: N/A; F: N/A; I.S: N/A | [8 empty] | Removed from Use |  | 50
MCR01 | MCR01-RO-021 | MCR01-R-021 | PKG | 107-SA | RESTRICTION ORIFICE | MCR01 | 175.0 | P020 HTF FLOW | REF: N/A; REQ: N/A; F: N/A; I.S: N/A | [8 empty] | Removed from Use |  | 50
MCR01 | MCR01-RO-031 | MCR01-R-031 | PKG | 107-SA | RESTRICTION ORIFICE | MCR01 | 175.0 | P030 HTF FLOW | REF: N/A; REQ: N/A; F: N/A; I.S: N/A | [8 empty] | Removed from Use |  | 50
MCR01 | MCR01-SIC-040 | MCR01-S-040 | PKG | 107-SD | DC VSD DRIVE INPUT | LCP | 175.0 | P 040 PUMP SPEED | -: 0 to 6000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-SI-042 | MCR01-S-042 | PKG | 107-SD | P040 SPEED | MCR01 | 175.0 | P040 PUMP SPEED | -: 0 to 4000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-SIC-050 | MCR01-S-050 | PKG | 107-SD | DC VSD DRIVE INPUT | LCP | 175.0 | P 050 PUMP SPEED | -: 0 to 6000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-SI-052 | MCR01-S-052 | PKG | 107-SD | P050 SPEED | MCR01 | 175.0 | P050 PUMP SPEED | -: 0 to 4000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-SIC-060 | MCR01-S-060 | PKG | 107-SD | DC VSD DRIVE INPUT | LCP | 175.0 | P 060 PUMP SPEED | -: 0 to 6000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-SI-062 | MCR01-S-062 | PKG | 107-SD | P060 SPEED | MCR01 | 175.0 | P060 PUMP SPEED | -: 0 to 4000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-SIC-070 | MCR01-S-070 | PKG | 107-SD | DC VSD DRIVE INPUT | LCP | 175.0 | P 070 PUMP SPEED | -: 0 to 6000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-SI-072 | MCR01-S-072 | PKG | 107-SD | P070 SPEED | MCR01 | 175.0 | P070 PUMP SPEED | -: 0 to 4000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-SIC-080 | MCR01-S-080 | PKG | 107-SD | DC VSD DRIVE INPUT | LCP | 175.0 | P 080 PUMP SPEED | -: 0 to 6000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AO | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-SI-082 | MCR01-S-082 | PKG | 107-SD | P080 SPEED | MCR01 | 175.0 | P080 PUMP SPEED | -: 0 to 4000 rpm; REF: Ref; REQ: By Req; F: F; I.S: N.I.S | AI | [5 empty] | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-001 | MCR01-T-001 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | COLD HTF LOOP TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-002 | MCR01-T-002 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | HOT HTF LOOP TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-011 | MCR01-T-011 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | P 010 HTF LOOP TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TCV-012 | MCR01-T-012 | PKG | 107-SA | FLOW CONTROL VALVE | MCR01 | 175.0 | P 010 HTF LOOP COLD CTRL VALVE | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A; I.S: I.S | AO |  |  |  | HABONIM | AN 47 | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-TCV-013 | MCR01-T-013 | PKG | 107-SA | FLOW CONTROL VALVE | MCR01 | 175.0 | P 010 HTF LOOP HOT CONTROL VALVE | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A; I.S: I.S | AO |  |  |  | HABONIM | AN 47 | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-TSH-014 | MCR01-T-014 | PKG | 107-SA | TEMPERATURE SWITCH | MCR01 | 175.0 | P010 BEARING TEMPERATURE | REF: SHE; REQ: 12; F: F; I.S: I.S | [8 empty] | Removed from Use |  | 50
MCR01 | MCR01-TT-021 | MCR01-T-021 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | P 020 HTF LOOP TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TCV-022 | MCR01-T-022 | PKG | 107-SA | FLOW CONTROL VALVE | MCR01 | 175.0 | P 020 HTF LOOP COLD CTRL VALVE | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A; I.S: I.S | AO |  |  |  | HABONIM | AN 47 | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-TCV-023 | MCR01-T-023 | PKG | 107-SA | FLOW CONTROL VALVE | MCR01 | 175.0 | P 020 HTF LOOP HOT CONTROL VALVE | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A; I.S: I.S | AO |  |  |  | HABONIM | AN 47 | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-TSH-024 | MCR01-T-024 | PKG | 107-SA | TEMPERATURE SWITCH | MCR01 | 175.0 | P020 BEARING TEMPERATURE | REF: SHE; REQ: 12; F: F; I.S: I.S | [8 empty] | Removed from Use |  | 50
MCR01 | MCR01-TT-031 | MCR01-T-031 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | P 030 HTF LOOP TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TCV-032 | MCR01-T-032 | PKG | 107-SA | FLOW CONTROL VALVE | MCR01 | 175.0 | P 020 HTF LOOP COLD CTRL VALVE | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A; I.S: I.S | AO |  |  |  | HABONIM | AN 47 | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-TCV-033 | MCR01-T-033 | PKG | 107-SA | FLOW CONTROL VALVE | MCR01 | 175.0 | P 030 HTF LOOP HOT CONTROL VALVE | -: 0 to 100 %; REF: N/A; REQ: N/A; F: N/A; I.S: I.S | AO |  |  |  | HABONIM | AN 47 | KV0004/P2 |  | Removed from Use |  | 50
MCR01 | MCR01-TSH-034 | MCR01-T-034 | PKG | 107-SA | TEMPERATURE SWITCH | MCR01 | 175.0 | P030 BEARING TEMPERATURE | REF: SHE; REQ: 12; F: F; I.S: I.S | [8 empty] | Removed from Use |  | 50
MCR01 | MCR01-TT-041 | MCR01-T-041 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | P 040 OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-051 | MCR01-T-051 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | P 050 OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-061 | MCR01-T-061 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | P 060 OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-071 | MCR01-T-071 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | P 070 OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-081 | MCR01-T-081 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | P 080 OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-101 | MCR01-T-101 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 100 PROCESS OUTLET TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-102 | MCR01-T-102 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 100 HTF OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-103 | MCR01-T-103 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR100 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-104 | MCR01-T-104 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR100 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-105 | MCR01-T-105 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR100 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-106 | MCR01-T-106 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR100 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-107 | MCR01-T-107 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR100 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-108 | MCR01-T-108 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR100 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-201 | MCR01-T-201 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 100 PROCESS OUTLET TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-202 | MCR01-T-202 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 200 HTF OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-203 | MCR01-T-203 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR200 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-204 | MCR01-T-204 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR200 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-205 | MCR01-T-205 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR200 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-206 | MCR01-T-206 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR200 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-207 | MCR01-T-207 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR200 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-208 | MCR01-T-208 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR200 INTERMEDIATE TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  |  | CUSTOM - Thermocouple | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-301 | MCR01-T-301 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 100 PROCESS OUTLET TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-302 | MCR01-T-302 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 300 HTF OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-303 | MCR01-T-303 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 300 INTERMEDIATE TEMPERATURE | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-401 | MCR01-T-401 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 100 PROCESS OUTLET TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-402 | MCR01-T-402 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 400 HTF OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-403 | MCR01-T-403 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 400 INTERMEDIATE TEMPERATURE | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-404 | MCR01-T-404 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 400 INTERMEDIATE TEMPERATURE | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-405 | MCR01-T-405 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 400 INTERMEDIATE TEMPERATURE | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-501 | MCR01-T-501 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 100 PROCESS OUTLET TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-502 | MCR01-T-502 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 500 HTF OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MCR01 | MCR01-TT-601 | MCR01-T-601 | PKG | 107-SD | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 100 PROCESS OUTLET TEMP | -: -30 to 170 C; REQ: 12; F: C; I.S: I.S | AI |  |  |  | ALFA LAVAL | TC/TE Typ K 5290090-001 | N/A |  | Removed from Use |  | 50
MCR01 | MCR01-TT-602 | MCR01-T-602 | PKG | 107-SA | TEMPERATURE TRANSMITTER | MCR01 | 175.0 | PFR 600 HTF OUTLET TEMPERATURE |  | -30 to 170 C | +/- 1% | REF | By Req | C |  | I.S |  | AI |  |  |  | NORTHDOWNS INST | CUSTOM | KT0004/P4 |  | Removed from Use |  | 50
MDC | MDC-KWH-001 | MDC-K-001 | PLC | N/A | POWER TOTALISER | HVAC MCC |  | MDC INCOMER #1 Kw/h | PKG: 8827; I.S: N.I.S |  |  | 0 | [5 empty] | PULSED INPUT | AI | 01
MDC | MDC-KWH-002 | MDC-K-002 | PLC | N/A | POWER TOTALISER | HVAC MCC |  | MDC INCOMER #2 Kw/h | PKG: 8837; I.S: N.I.S |  |  | 0 | [5 empty] | PULSED INPUT | AI | 01
MDH01 | MDH01-TC-001 | MDH01-T-001 | PKG | N/A | TEMPERATURE CONTROLLER | MDH01 | 144.2 | TEMPERATURE CONTROL | -: set @ commiss; -: +/- 0.5%; REF: SHE; REQ: REQ; F: C | [10 empty] | 01
MDH01 | MDH01-TSH-002 | MDH01-T-002 | PKG | N/A | TEMPERATURE SWITCH - HIGH | MDH01 | 144.2 | HIGH TEMPERATURE CUTOUT | -: set @ commiss; -: +/- 0.5%; REF: SHE; REQ: REQ; F: C | [10 empty] | 01
MDH02 | MDH02-TC-001 | MDH02-T-001 | PKG | N/A | TEMPERATURE CONTROLLER | MDH02 | 144.3 | TEMPERATURE CONTROL | -: set @ commiss; -: +/- 0.5%; REF: SHE; REQ: REQ; F: C | [10 empty] | 01
MDH02 | MDH02-TSH-002 | MDH02-T-002 | PKG | N/A | TEMPERATURE SWITCH - HIGH | MDH02 | 144.3 | HIGH TEMPERATURE CUTOUT | -: set @ commiss; -: +/- 0.5%; REF: SHE; REQ: REQ; F: C | [10 empty] | 01
| MEA01-AI-001 | MEA01-A-001 | PCS | 902-007-002-000-00210 | PROTEA FTIR ANALYSER | 3RD FLOOR - PROTEA FTIR ANALYSER | 182 | DCM CONCENTRATION | -: 0-1000ppm | [8 empty] | Analogue output from Protea FTIR |  |  | 15
| MEA01-AI-002 | MEA01-A-001 | PCS | 902-007-002-000-00210 | PROTEA FTIR ANALYSER | 3RD FLOOR - PROTEA FTIR ANALYSER | 182 | HCL CONCENTRATION | -: 0-10ppm | [8 empty] | Analogue output from Protea FTIR |  |  | 15
| MEA01-AI-003 | MEA01-A-001 | PCS | 902-007-002-000-00210 | PROTEA FTIR ANALYSER | 3RD FLOOR - PROTEA FTIR ANALYSER | 182 | NH3 CONCENTRATION | -: 0-20ppm | [8 empty] | Analogue output from Protea FTIR |  |  | 15
| MEA01-AI-004 | MEA01-A-001 | PCS | 902-007-002-000-00210 | PROTEA FTIR ANALYSER | 3RD FLOOR - PROTEA FTIR ANALYSER | 182 | ACETONITRILE CONCENTRATION | -: 0-1000ppm | [8 empty] | Analogue output from Protea FTIR |  |  | 15
| MEA01-AI-005 | MEA01-A-001 | PCS | 902-007-002-000-00210 | PROTEA FTIR ANALYSER | 3RD FLOOR - PROTEA FTIR ANALYSER | 182 | DMAC CONCENTRATION | -: 0-100ppm | [8 empty] | Analogue output from Protea FTIR |  |  | 15
| MEA01-AI-006 | MEA01-A-001 | PCS | 902-007-002-000-00210 | PROTEA FTIR ANALYSER | 3RD FLOOR - PROTEA FTIR ANALYSER | 182 | DMF CONCENTRATION | -: 0-100ppm | [8 empty] | Analogue output from Protea FTIR |  |  | 15
| MEA01-AIT-001 | MEA01-A-001 | PCS | 902-007-002-000-00210 | PROTEA FTIR ANALYSER | 3RD FLOOR - PROTEA FTIR ANALYSER | 182 | CONTINUOUS EMISSIONS MONITORING SYSTEM | REF: SHE; REQ: 6; F: C |  |  |  |  | PROTEA | PROTIR 204M | [5 empty] | 15
| MEA01-AI-007 | MEA01-A-007 | PCS | 902-007-002-000-00210 | DRAEGER LEL DETECTOR | 3RD FLOOR - DRAEGER LEL PANEL | 182 | %LEL MONITORING | PKG: L16233; -: 0-100%
| MEA01-AIT-007 | MEA01-A-007 | FLD | 902-007-002-000-00210 | DRAEGER LEL DETECTOR | 3RD FLOOR - DRAEGER LEL PANEL | 182 | %LEL MONITORING | L16233 | 0-100% | +/- 0.5% | SHE | 6 | C | [7 empty] | DRAEGER | POLYTRON 8700 IR | [5 empty] | 15
| MEA01-CV-001 | MEA01-C-001 | FLD | 902-007-002-000-00210 | SOLENOID VALVE | 3RD FLOOR | 182 | SC01 SAMPLE VALVE TO PROTEA | [13 empty] | ASCO | [6 empty] | 15 | bar: PKG
| MEA01-CY-001 | MEA01-C-001 | PCS | 902-007-002-000-00210 | RELAY | 3RD FLOOR | 182 | SC01 SAMPLE VALVE TO PROTEA | PKG: L16226 | [11 empty] | 15
| MEA01-CV-002 | MEA01-C-002 | FLD | 902-007-002-000-00210 | SOLENOID VALVE | 3RD FLOOR | 182 | SC02 SAMPLE VALVE TO PROTEA | [13 empty] | ASCO | [6 empty] | 15 | bar: PKG
| MEA01-CY-002 | MEA01-C-002 | PCS | 902-007-002-000-00210 | RELAY | 3RD FLOOR | 182 | SC02 SAMPLE VALVE TO PROTEA | PKG: L16227 | [11 empty] | 15
| MEA01-CV-003 | MEA01-C-003 | FLD | 902-007-002-000-00210 | SOLENOID VALVE | 3RD FLOOR | 182 | SC03 SAMPLE VALVE TO PROTEA | [13 empty] | ASCO | [6 empty] | 15 | bar: PKG
| MEA01-CY-003 | MEA01-C-003 | PCS | 902-007-002-000-00210 | RELAY | 3RD FLOOR | 182 | SC03 SAMPLE VALVE TO PROTEA | PKG: L16228 | [11 empty] | 15
| MEA01-CV-004 | MEA01-C-004 | FLD | 902-007-002-000-00210 | SOLENOID VALVE | 3RD FLOOR - DRAEGER LEL PANEL | 182 | SC01 SAMPLE VALVE TO LEL DETECTOR | [13 empty] | ASCO | [6 empty] | 15 | bar: PKG
| MEA01-CY-004 | MEA01-C-004 | PCS | 902-007-002-000-00210 | RELAY | 3RD FLOOR - DRAEGER LEL PANEL | 182 | SC01 SAMPLE VALVE TO LEL DETECTOR | PKG: L16229 | [11 empty] | 15
| MEA01-CV-005 | MEA01-C-005 | FLD | 902-007-002-000-00210 | SOLENOID VALVE | 3RD FLOOR - DRAEGER LEL PANEL | 182 | SC02 SAMPLE VALVE TO LEL DETECTOR | [13 empty] | ASCO | [6 empty] | 15 | bar: PKG
| MEA01-CY-005 | MEA01-C-005 | PCS | 902-007-002-000-00210 | RELAY | 3RD FLOOR - DRAEGER LEL PANEL | 182 | SC02 SAMPLE VALVE TO LEL DETECTOR | PKG: L16230 | [11 empty] | 15
| MEA01-CV-006 | MEA01-C-006 | FLD | 902-007-002-000-00210 | SOLENOID VALVE | 3RD FLOOR - DRAEGER LEL PANEL | 182 | SC03 SAMPLE VALVE TO LEL DETECTOR | [13 empty] | ASCO | [6 empty] | 15 | bar: PKG
| MEA01-CY-006 | MEA01-C-006 | PCS | 902-007-002-000-00210 | RELAY | 3RD FLOOR - DRAEGER LEL PANEL | 182 | SC03 SAMPLE VALVE TO LEL DETECTOR | PKG: L16231 | [11 empty] | 15
| MEA01-CV-007 | MEA01-C-007 | FLD | 902-007-002-000-00210 | SOLENOID VALVE | 3RD FLOOR - DRAEGER LEL PANEL | 182 | SPAN GAS DIVERTER VALVE TO LEL DETECTOR | [13 empty] | ASCO | [6 empty] | 15 | bar: PKG
| MEA01-CY-007 | MEA01-C-007 | PCS | 902-007-002-000-00210 | RELAY | 3RD FLOOR - DRAEGER LEL PANEL | 182 | SPAN GAS DIVERTER VALVE TO LEL DETECTOR | PKG: L16232 | [11 empty] | 15
| MEA01-FI-001 | MEA01-F-001 | FLD | 902-007-002-000-00210 | INDICATOR - FLOW | 3RD FLOOR - DRAEGER LEL PANEL | 182 | LEL DETECTOR FLOW | -: 0.16-1.5ltr/min; REF: SHE; REQ: 12; F: F |  |  |  |  | KROHNE | DK32 | [5 empty] | 15
| MEA01-FSL-001 | MEA01-F-001 | PCS | 902-007-002-000-00210 | SWITCH FLOW LOW | 3RD FLOOR - DRAEGER LEL PANEL | 182 | LEL DETECTOR FLOW | PKG: L16234; -: set @ 0.32ltr/min; REF: SHE; REQ: 12; F: F |  |  |  |  | KROHNE | DK32 | [5 empty] | 15
| MEA01-FI-002 | MEA01-F-002 | FLD | 902-007-002-000-00210 | INDICATOR - FLOW | 3RD FLOOR - DRAEGER LEL PANEL | 182 | LEL DETECTOR DRYER AIR FLOW | -: 0.4-5ltr/min |  |  |  |  | BROOKS | MR3A14SVVT 01C11902628 | [5 empty] | 15
| MEA01-PI-001 | MEA01-P-001 | FLD | 902-007-002-000-00210 | PRESSURE GAUGE | 3RD FLOOR - DRAEGER LEL PANEL | 182 | COMPRESSED AIR SUPPLY TO MEA01-EJ-002 | -: 0-11bar |  |  |  |  | NORGREN | [6 empty] | 15
| MEA01-PRV-001 | MEA01-P-001 | FLD | 902-007-002-000-00210 | CONTROL VALVE SELF ACTUATING | 3RD FLOOR - DRAEGER LEL PANEL | 182 | COMPRESSED AIR SUPPLY TO MEA01-EJ-002 | -: set @ 2barg |  |  |  |  | NORGREN | R72G | [5 empty] | 15
| MEA01-PI-002 | MEA01-P-002 | FLD | 902-007-002-000-00210 | PRESSURE GAUGE | 3RD FLOOR - DRAEGER LEL PANEL | 182 | COMPRESSED AIR SUPPLY TO MEA01-EJ-001 | -: 0-11bar |  |  |  |  | NORGREN | [6 empty] | 15
| MEA01-PRV-002 | MEA01-P-002 | FLD | 902-007-002-000-00210 | CONTROL VALVE SELF ACTUATING | 3RD FLOOR - DRAEGER LEL PANEL | 182 | COMPRESSED AIR SUPPLY TO MEA01-EJ-001 | -: set @ 4barg |  |  |  |  | NORGREN | R72G | [5 empty] | 15
| MEA01-PI-003 | MEA01-P-003 | FLD | 902-007-002-000-00210 | PRESSURE GAUGE | 3RD FLOOR - DRAEGER LEL SPAN GAS | 182 | SPAN GAS CYLINDER PRESSURE | -: 0-100bar | [11 empty] | 15
| MEA01-PRV-003 | MEA01-P-003 | FLD | 902-007-002-000-00210 | CONTROL VALVE SELF ACTUATING | 3RD FLOOR - DRAEGER LEL SPAN GAS | 182 | SPAN GAS ON DEMAND REGULATOR | -: 0-3ltr/min | [5 empty] | E0230SS | [5 empty] | 15
| MEA01-XA-001 | MEA01-X-001 | PCS | 902-007-002-000-00210 | ALARM - STATUS | 3RD FLOOR - PROTEA FTIR ANALYSER | 182 | COMMON ALARM | [17 empty] | Digital output from Protea FTIR |  |  | 15 | bar: PKG
| MEA01-XA-002 | MEA01-X-002 | PCS | 902-007-002-000-00210 | ALARM - STATUS | 3RD FLOOR - PROTEA FTIR ANALYSER | 182 | PROCESS ALARM | REF: SHE; REQ: 12; F: F | [8 empty] | Digital output from Protea FTIR |  |  | 15
MES01 | MES01-BD-001 | MES01-B-001 | FLD | 107-HF | RUPTURE DISC | 40-P-PT1A-C-9025592 |  | RC1 BURSTING DISC | 6733 | 6.0 barg | - |  | - | - | - | I.S | DI | 1 |  | 32 | GP1 | BS&B | SPR-7 / BAS + | KS0003/P4 | TI702-SP-5077 |  |  | 01
MES01 | MES01-BD-001 | MES01-B-001 | FLD | 107-HF | RUPTURE DISC | REPLACED | 109.0 | REPLACED | 6733 | 1.0 barg | - | N/A | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | FRS | KS0003 |  | REPLACED |  | 01
MES01 | MES01-YI-001 | MES01-B-001 | PCS | 107-HF | ALARM - RUPTURE DISC FAIL | REPLACED |  | REPLACED | [11 empty] | 0 | [5 empty] | REPLACED |  | 01
MES01 | MES01-YI-001 | MES01-B-001 | PCS | 107-HF | ALARM - RUPTURE DISC FAIL |  |  | RC1 BURSTING DISC | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-BD-002 | MES01-B-002 | FLD | 107-HF | RUPTURE DISC | 50-RV-CS1A-0-9026734 |  | PROCESS RELIEF | 6761 | 1.0 barg | - |  | - | - | - | I.S | DI | 1 |  | 32 | GP1 | BS&B | SPR-7 / BAS + | KS0003/P4 | TI702-SP-5077 |  |  | 01
MES01 | MES01-BD-002 | MES01-B-002 | FLD | 107-HF | RUPTURE DISC | REPLACED | 009.0 | REPLACED | 6761 | 1.0 barg | - | N/A | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | FRS | KS0003 |  | REPLACED | D2 | 01
MES01 | MES01-YI-002 | MES01-B-002 | PCS | 107-HF | ALARM - RUPTURE DISC FAIL | REPLACED |  | REPLACED | [11 empty] | 0 | [5 empty] | REPLACED |  | 01
MES01 | MES01-YI-002 | MES01-B-002 | PCS | 107-HF | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-CV-001 | MES01-C-001 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 15-N-SS1U-0-9028735 | 043.2 | 6 BAR N2 SUPPLY | 7079 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
MES01 | MES01-CY-001 | MES01-C-001 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | 6 BAR N2 SUPPLY | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-001 | MES01-C-001 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-001 | MES01-C-001 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-006 | MES01-C-006 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-H-9025589 |  | TO VC1 | 13230 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-006 | MES01-C-006 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | TO VC1 | 13230 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-006 | MES01-C-006 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO VC1 | 13230 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-006 | MES01-C-006 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO VC1 | 13230 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-012 | MES01-C-012 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9025561 | 036.1 | DRYER VACUUM | 7283 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MES01 | MES01-CY-012 | MES01-C-012 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | DRYER VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-012 | MES01-C-012 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DRYER VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-012 | MES01-C-012 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DRYER VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-013 | MES01-C-013 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9025559 | 008.2 | SCRUBBER 02 | 7256 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MES01 | MES01-CY-013 | MES01-C-013 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-013 | MES01-C-013 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-013 | MES01-C-013 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-014 | MES01-C-014 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-H-9025593 |  | RC10 INLET | 13231 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-014 | MES01-C-014 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | RC10 INLET | 13231 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-014 | MES01-C-014 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RC10 INLET | 13231 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-014 | MES01-C-014 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RC10 INLET | 13231 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-015 | MES01-C-015 | FLD | 107-HF | V-BALL VALVE - CONTROL - F.C. | 40-VP-PT1A-0-9025561 | 109.0 | DRYER VACUUM | 6853 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
MES01 | MES01-CV-016 | MES01-C-016 | FLD | 107-HF | V-BALL VALVE - CONTROL - F.C. | 40-P-PT1A-0-9025559 | 109.0 | SCRUBBER 02 | 6819 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
MES01 | MES01-CV-017 | MES01-C-017 | FLD | 107-HF | V-BALL VALVE - CONTROL - F.C. | 25-N-SS1U-0-9028665 |  | NITROGEN TO RC10 | 13232 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004/P1 | TI702-SP-5008 |  |  | 01
MES01 | MES01-CV-018 | MES01-C-018 | FLD | 107-HF | V-BALL VALVE - CONTROL - F.C. | RETAGGED MES01-CV-017 | 109.0 | RETAGGED MES01-CV-017 | 6840 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC | AKH-3 | KV0004 |  | RETAGGED MES01-CV-017 |  | 01
MES01 | MES01-CV-018 | MES01-C-018 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9025574 |  | TP1 DISCHARGE | 13233 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-018 | MES01-C-018 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | TP1 DISCHARGE | 13233 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-018 | MES01-C-018 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TP1 DISCHARGE | 13233 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-018 | MES01-C-018 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TP1 DISCHARGE | 13233 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-021 | MES01-C-021 | FLD | 107-HF | V-BALL VALVE - CONTROL - F.C. | 50-SV-GR1A-0-9026207 |  | GLOVEBOX TO LEV | 13234 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | GP1 | HABONIM / MOORE | 31 SERIES V-FLOW / 760EA15EAAGNNB8 POSITIONER | KV0004/P1 | TI702-SP-5090 |  |  | 01
MES01 | MES01-CV-022 | MES01-C-022 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 50-SV-GR1A-0-9026207 |  | ACID SCRUBBER | 13235 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-022 | MES01-C-022 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | ACID SCRUBBER | 13235 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-022 | MES01-C-022 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ACID SCRUBBER | 13235 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-022 | MES01-C-022 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ACID SCRUBBER | 13235 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-023 | MES01-C-023 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-C-9025590 |  | REFLUX | 13236 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-023 | MES01-C-023 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | REFLUX | 13236 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-023 | MES01-C-023 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REFLUX | 13236 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-023 | MES01-C-023 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REFLUX | 13236 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-024 | MES01-C-024 | FLD | 107-HF | BALL VALVE - ON/OFF - F.O. | 25-P-PT1A-C-9025591 |  | CONDENSATE TO RC1 | 13237 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-024 | MES01-C-024 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | CONDENSATE TO RC1 | 13237 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-024 | MES01-C-024 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CONDENSATE TO RC1 | 13237 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-024 | MES01-C-024 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CONDENSATE TO RC1 | 13237 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-025 | MES01-C-025 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9025594 |  | RC1 RECYCLE | 13238 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-025 | MES01-C-025 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | RC1 RECYCLE | 13238 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-025 | MES01-C-025 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RC1 RECYCLE | 13238 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-025 | MES01-C-025 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RC1 RECYCLE | 13238 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-026 | MES01-C-026 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021868 |  | PROCESS INLET 1 | 13239 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-026 | MES01-C-026 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | PROCESS INLET 1 | 13239 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-026 | MES01-C-026 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS INLET 1 | 13239 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-026 | MES01-C-026 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS INLET 1 | 13239 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-027 | MES01-C-027 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-902???? |  | SOLVENT INLET | 13240 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-027 | MES01-C-027 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | SOLVENT INLET | 13240 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-027 | MES01-C-027 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENT INLET | 13240 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-027 | MES01-C-027 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENT INLET | 13240 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-028 | MES01-C-028 | FLD | 107-HF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021828 |  | PROCESS INLET 2 | 13241 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES01 | MES01-CY-028 | MES01-C-028 | FLD | 107-HF | SOLENOID VALVE | RACK MOUNTED |  | PROCESS INLET 2 | 13241 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES01 | MES01-ZSC-028 | MES01-C-028 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS INLET 2 | 13241 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-ZSO-028 | MES01-C-028 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS INLET 2 | 13241 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-CV-031 | MES01-C-031 | PKG | 107-HG | V-BALL VALVE - CONTROL - F.C. |  |  | HEAT/COOL PACKAGE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-DIC-001 | MES01-D-001 | PCS | 107-HG | INDICATING CONTR. - MOTOR DRIVE | RETAGGED MES01-DIC-002 |  | RETAGGED MES01-DIC-002 | [11 empty] | 0 | [5 empty] | RETAGGED MES01-DIC-002 |  | 01
MES01 | MES01-DS-001 | MES01-D-001 | CPR | 107-HG | DRIVE - AVAILABLE | RETAGGED MES01-DS-002 |  | RETAGGED MES01-DS-002 | I.S: N.I.S; DI: DI |  |  | 35 | GP1 |  |  |  |  | RETAGGED MES01-DS-002 |  | 01
MES01 | MES01-DY-001 | MES01-D-001 | CPR | 107-HG | DRIVE - RUNNING | RETAGGED MES01-DY-002 |  | RETAGGED MES01-DY-002 | I.S: N.I.S; DI: DI |  |  | 35 | GP1 |  |  |  |  | RETAGGED MES01-DY-002 |  | 01
MES01 | MES01-DYC-001 | MES01-D-001 | CPR | 107-HG | DRIVE - START/STOP | RETAGGED MES01-DYC-002 | 072.0 | RETAGGED MES01-DYC-002 | 8689 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | RETAGGED MES01-DYC-002 |  | 01
MES01 | MES01-DIC-002 | MES01-D-002 | PCS | 107-HF | INDICATING CONTR. - MOTOR DRIVE |  |  | TP1 TRANSFER PUMP | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-DS-002 | MES01-D-002 | MCC | 107-HF | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13242 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | GP1 | [6 empty] | 01
MES01 | MES01-DY-002 | MES01-D-002 | MCC | 107-HF | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13242 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | GP1 | [6 empty] | 01
MES01 | MES01-DYC-002 | MES01-D-002 | MCC | 107-HF | DRIVE - START/STOP | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13242 | - | - | N/A | - | - | - | N.I.S | DO | 1 |  | 42 | GP1 | [6 empty] | 01
MES01 | MES01-DY-003 | MES01-D-003 | PKG | 107-HG | PACKAGE RUNNING |  |  | HEAT/COOL PACKAGE | 13243 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | [7 empty] | 01
MES01 | MES01-DYC-003 | MES01-D-003 | PCS | 107-HG | PACKAGE - START/STOP |  |  | HEAT/COOL PACKAGE | 13243 |  |  | N/A | - | - | - | N.I.S | DO | 1 |  | 42 | GP2 | [6 empty] | 01
MES01 | MES01-FI-003 | MES01-F-003 | FLD | 107-HF | INDICATOR - FLOW | 15-N-SS1U-0-9028664 | 043.4 | 0.8 BARG N2 SUPPLY | REQ: By request; F: C |  |  | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
MES01 | MES01-FS-011 | MES01-F-011 | PKG | 107-HG | FLOW SWITCH |  |  | HEAT/COOL PACKAGE | REQ: By request; F: C; Ref: Ops | [10 empty] | 01
MES01 | MES01-HV-001 | MES01-H-001 | FLD | 107-HF | HAND VALVE | REMOVED | 072.0 | REMOVED | 8126 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | REMOVED |  | 01
MES01 | MES01-HZSC-001 | MES01-H-001 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | RETAGGED MES01-ZSC-027 |  | RETAGGED MES01-ZSC-027 | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | RETAGGED MES01-ZSC-027 |  | 01
MES01 | MES01-HZSO-001 | MES01-H-001 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | RETAGGED MES01-ZSO-027 |  | RETAGGED MES01-ZSO-027 | [11 empty] | 0 | GP1 |  |  |  |  | RETAGGED MES01-ZSO-027 |  | 01
MES01 | MES01-HV-002 | MES01-H-002 | FLD | 107-HF | HAND VALVE | REMOVED | 109.0 | REMOVED | 7435 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES01 | MES01-HZSC-002 | MES01-H-002 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | RETAGGED MES01-HZSC-009 |  | RETAGGED MES01-HZSC-009 | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | RETAGGED MES01-HZSC-009 |  | 01
MES01 | MES01-HZSO-002 | MES01-H-002 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | RETAGGED MES01-HZSO-009 |  | RETAGGED MES01-HZSO-009 | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | RETAGGED MES01-HZSO-009 |  | 01
MES01 | MES01-HV-003 | MES01-H-003 | FLD | 107-HF | HAND VALVE | REPLACED | 109.0 | REPLACED | 7436 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REPLACED |  | 01
MES01 | MES01-HV-003 | MES01-H-003 | FLD | 107-HF | HAND VALVE | 50-P-PT1A-H-9025587 |  | TO VC1 | REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01
MES01 | MES01-HZSC-003 | MES01-H-003 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO VC1 | 7436 |  |  |  | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-HZSC-003 | MES01-H-003 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | REPLACED |  | REPLACED | REF: N/A; I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | REPLACED |  | 01
MES01 | MES01-HZSO-003 | MES01-H-003 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO VC1 | 7436 |  |  |  | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-HZSO-003 | MES01-H-003 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | REPLACED |  | REPLACED | REF: N/A; I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | REPLACED |  | 01
MES01 | MES01-HV-004 | MES01-H-004 | FLD | 107-HF | HAND VALVE | 15-N-SS1U-0-9028664 | 043.4 | 0.8 BAR N2 SUPPLY (G1) | 8122 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
MES01 | MES01-HZSC-004 | MES01-H-004 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY (G1) | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-HZSO-004 | MES01-H-004 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY (G1) | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
MES01 | MES01-HV-005 | MES01-H-005 | FLD | 107-HF | HAND VALVE | REPLACED | 109.0 | REPLACED | 7437 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REPLACED |  | 01
MES01 | MES01-HV-005 | MES01-H-005 | FLD | 107-HF | HAND VALVE | 50-P-PT1A-H-9025593 |  | RC10 INLET | REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01
MES01 | MES01-HZSC-005 | MES01-H-005 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RC10 INLET | 7437 |  |  |  | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-HZSC-005 | MES01-H-005 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | REPLACED |  | REPLACED | REF: N/A; I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | REPLACED |  | 01
MES01 | MES01-HZSO-005 | MES01-H-005 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RC10 INLET | 7437 |  |  |  | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-HZSO-005 | MES01-H-005 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | REPLACED |  | REPLACED | REF: N/A; I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | REPLACED |  | 01
MES01 | MES01-HV-006 | MES01-H-006 | FLD | 107-HF | HAND VALVE | REMOVED | 072.0 | REMOVED | 7467 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES01 | MES01-HZSC-006 | MES01-H-006 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | RETAGGED MES01-ZSC-026 |  | RETAGGED MES01-ZSC-026 | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | RETAGGED MES01-ZSC-026 |  | 01
MES01 | MES01-HZSO-006 | MES01-H-006 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | RETAGGED MES01-ZSO-026 |  | RETAGGED MES01-ZSO-026 | [11 empty] | 0 | GP1 |  |  |  |  | RETAGGED MES01-ZSO-026 |  | 01
MES01 | MES01-HV-007 | MES01-H-007 | FLD | 107-HF | HAND VALVE | REMOVED | 072.0 | REMOVED | 7468 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES01 | MES01-HZSC-007 | MES01-H-007 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | RETAGGED MES01-ZSC-028 |  | RETAGGED MES01-ZSC-028 | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | RETAGGED MES01-ZSC-028 |  | 01
MES01 | MES01-HZSO-007 | MES01-H-007 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | RETAGGED MES01-ZSO-028 |  | RETAGGED MES01-ZSO-028 | [11 empty] | 0 | GP1 |  |  |  |  | RETAGGED MES01-ZSO-028 |  | 01
MES01 | MES01-HV-008 | MES01-H-008 | FLD | 107-HF | HAND VALVE | REMOVED | 072.0 | REMOVED | 8130 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | REMOVED |  | 01
MES01 | MES01-HZSC-008 | MES01-H-008 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | REMOVED |  | REMOVED | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | REMOVED |  | 01
MES01 | MES01-HZSO-008 | MES01-H-008 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | REMOVED |  | REMOVED | [11 empty] | 0 | GP1 |  |  |  |  | REMOVED |  | 01
MES01 | MES01-HV-009 | MES01-H-009 | FLD | 107-HF | HAND VALVE | 25-P-PT1A-C-9025590 |  | REFLUX | REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01
MES01 | MES01-HZSC-009 | MES01-H-009 | FLD | 107-HF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REFLUX | 13244 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-HZSO-009 | MES01-H-009 | FLD | 107-HF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REFLUX | 13244 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES01 | MES01-LI-001A | MES01-L-001 | PCS | 107-HF | INDICATOR - LEVEL | RELOCATED TO RC10 |  | RELOCATED TO RC10 | [11 empty] | 0 | [5 empty] | RELOCATED TO RC10 |  | 01
MES01 | MES01-LI-001B | MES01-L-001 | FLD | 107-HF | INDICATOR - LEVEL | RELOCATED TO RC10 | 109.0 | RELOCATED TO RC10 | REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 |  | RELOCATED TO RC10 |  | 01
MES01 | MES01-LI-001B | MES01-L-001 | FLD | 107-HF | INDICATOR - LEVEL | GP1 | 169.0 | RC10 LEVEL |  | 0 to 300 l | +/- 1% | REF | 12 | C | Ops | I.S | [5 empty] | BEKA | BA324D | KX0017/P1 |  |  |  | 01
MES01 | MES01-LIC-001 | MES01-L-001 | PCS | 107-HF | INDICATING CONTROLLER - LEVEL |  | 169.0 | RC10 LEVEL | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-LT-001 | MES01-L-001 | FLD | 107-HF | TRANSMITTER - LEVEL | MES01-RC10/N4/100 | 169.0 | RC10 LEVEL | 6469 | 0 to 300 l | +/- 4% |  | 12 | C | Ops | I.S | AI | 1 |  | 11 | GP1 | ENDRESS + HAUSER | FMR245-24APKAA2A | KL0028/P2 | TI702-SP-5026 |  |  | 01
MES01 | MES01-LT-001 | MES01-L-001 | FLD | 107-HF | TRANSMITTER - LEVEL | RELOCATED TO RC10 | 109.0 | RELOCATED TO RC10 | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | GP1 | ENDRESS + HAUSER | FMR245 | KL0028/P1 |  | RELOCATED TO RC10 |  | 01
MES01 | MES01-LAH-002 | MES01-L-002 | PCS | 107-HF | ALARM - LEVEL - HIGH |  | 169.0 | RC10 HIGH LEVEL | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-LSH-002 | MES01-L-002 | FLD | 107-HF | SWITCH - LEVEL - HIGH | MES01-RC10/N7/80 | 169.0 | RC10 HIGH LEVEL | L13245 | Off/on | Off/on | REF | 24 | C | Ops | I.S | DI | 1 |  | 32 | GP1 | ENDRESS + HAUSER | FLT51 C 4ALKBK8G4AA | KL0014/P2 | TI702-SP-5036 |  |  | 01
MES01 | MES01-PI-001 | MES01-P-001 | FLD | 107-HF | PRESSURE GAUGE | 15-N-SS1U-0-9028664 | 043.4 | 0.8 BARG N2 SUPPLY | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
MES01 | MES01-PI-002 | MES01-P-002 | FLD | 107-HF | PRESSURE GAUGE | 15-N-SS1U-0-9028735 | 043.2 | 6 BARG N2 SUPPLY | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
MES01 | MES01-PI-004 | MES01-P-004 | FLD | 107-HF | PRESSURE GAUGE | 15-IA-SS1U-0-9028423 | 042.1 | INSTRUMENT AIR SUPPLY | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
MES01 | MES01-PI-005 | MES01-P-005 | FLD | 107-HF | PRESSURE GAUGE - DIAPHRAGM | REPLACED | 109.0 | REPLACED | -: -1 to 1.5 barg; -: +/- 1%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  | REPLACED |  | 01
MES01 | MES01-PI-005 | MES01-P-005 | FLD | 107-HF | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-H-9025587 |  | VC1 INLET PRESSURE |  | -1 to 3 barg | +/- 1% | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100/990.27 | KP0006/P6 |  |  |  | 01
MES01 | MES01-PIC-006 | MES01-P-006 | PCS | 107-HF | INDICATING CONTROLLER - PRESSURE | REPLACED |  | REPLACED | [11 empty] | 0 | [5 empty] | REPLACED |  | 01
MES01 | MES01-PIC-006 | MES01-P-006 | PCS | 107-HF | INDICATING CONTROLLER - PRESSURE |  |  | VC1 INLET PRESSURE | REQ: By request; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-PIT-006 | MES01-P-006 | FLD | 107-HF | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-H-9025589 |  | VC1 INLET PRESSURE | 6706 | -1 to 3 barg | +/- 0.25% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | GP1 | ROSEMOUNT | 3051S2 | KP0001/P | TI702-SP-5013 |  |  | 01
MES01 | MES01-PIT-006 | MES01-P-006 | FLD | 107-HF | TRANSMITTER - PRESSURE - DIAPHRAGM | REPLACED | 109.0 | REPLACED | 6706 | -1 to 1 barg | 0.25% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | FOXBORO | 141GP (Note 2) | KP0001 |  | REPLACED |  | 01
MES01 | MES01-PT-006 | MES01-P-006 | [6 empty] | REQ: By request
MES01 | MES01-PI-007 | MES01-P-007 | FLD | 107-HF | PRESSURE GAUGE - DIAPHRAGM | REPLACED | 109.0 | REPLACED | -: -1 to 1.5 barg; -: +/- 1%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  | REPLACED |  | 01
MES01 | MES01-PI-007 | MES01-P-007 | FLD | 107-HF | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-C-902???? |  | RC10 PRESSURE |  | -1 to 3 barg | +/- 1% | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100/990.27 | KP0006/P6 |  |  |  | 01
MES01 | MES01-PI-008 | MES01-P-008 | FLD | 107-HF | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-0-9025574 |  | TP1 DISCHARGE PRESSURE |  | 0 to 4 barg | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | 233.50.100/990.27 | KP0006/P6 |  |  |  | 01
MES01 | MES01-PSV-010 | MES01-P-010 | FLD | 107-HF | PRESSURE RELIEF VALVE | 25-HT-CS3A-0-9025578 | 109.0 | RC07-VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
MES01 | MES01-PRV-011 | MES01-P-011 | PKG | 107-HG | CONTROL VALVE SELF ACTUATING | 40-HWR-CS1B-H-902558 | 072.0 | HOT WATER BYPASS RELIEF | -: set @ 2.4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ROSEMOUNT | 98H(FS98H-75) | KV0006/1 |  |  |  | 01
MES01 | MES01-PI-012 | MES01-P-012 | PKG | 107-HG | PRESSURE GAUGE | MES01-HW1 | 072.0 | P1 DISCHARGE PRESSURE | -: 0 to 4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MES01 | MES01-PAH-027 | MES01-P-027 | PCS | 107-HF | ALARM - PRESSURE - HIGH |  |  |  | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-PSH-027 | MES01-P-027 | FLD | 107-HF | SWITCH - PRESSURE - HIGH | 50-RV-CS1A-0-9026734 |  | PROCESS ALARM | REQ: By request; F: C; Ref: Ops; I.S: I.S; DI: DI | 1 |  | 32 | GP1 | DELTA CONTROLS LTD | W28102G522C20 | KP0012/P | TI702-SP-5085 |  |  | 01
MES01 | MES01-PI-028 | MES01-P-028 | FLD | 107-HF | PRESSURE GAUGE | 20-N-SS1U-0-902560? |  | 6 BAR NITROGEN INLET |  | 0 to 10barg | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100 | KP0006/P6 |  |  |  | 01
MES01 | MES01-PSV-030 | MES01-P-030 | PKG | 107-HG | PRESSURE RELIEF VALVE |  |  | HEAT/COOL PACKAGE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-PS-031 | MES01-P-031 | PKG | 107-HG | SWITCH - PRESSURE - HIGH |  |  | HEAT/COOL PACKAGE | REF: REF; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
MES01 | MES01-PI-032 | MES01-P-032 | PKG | 107-HG | PRESSURE GAUGE |  |  | HEAT/COOL PACKAGE | REF: REF; REQ: REQ; F: C; Ref: Ref | [10 empty] | 01
MES01 | MES01-RO-001 | MES01-R-001 | FLD | 107-HF | RESTRICTION ORIFICE PLATE | 15-N-SS1U-0-9028735 | 043.2 | 2 BARG N2 SUPPLY | -: 100 Nm3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
MES01 | MES01-RO-002 | MES01-R-002 | PKG | 107-HG | RESTRICTION ORIFICE PLATE | REPLACED | 072.0 | REPLACED | [11 empty] | 0 |  | SITE FABRICATED | N/A | SITE FAB/2 |  | REPLACED |  | 01 | bar: - to -
MES01 | MES01-RO-002 | MES01-R-002 | FLD | 107-HF | RESTRICTION ORIFICE | 25-P-PT1A-0-9025574 |  | TP1 DISCHARGE | -: 5mm; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-TC-001 | MES01-T-001 | CPR | 107-HG | CONTROLLER - TEMPERATURE | RETAGGED MES01-TCI-015 | 072.0 | HOT WATER TEMPERATURE | 8689 | 0 to 100 degC | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP1 | [6 empty] | 01
MES01 | MES01-TE-001 | MES01-T-001 | FLD | 107-HG | ELEMENT - TEMPERATURE - RTD | RETAGGED MES01-TE-015 |  | RETAGGED MES01-TE-015 | [11 empty] | 0 | [5 empty] | RETAGGED MES01-TE-015 |  | 01
MES01 | MES01-TI-001 | MES01-T-001 | FLD | 107-HG | INDICATOR - TEMPERATURE | RETAGGED MES01-TI-015 | 072.0 | RETAGGED MES01-TI-015 |  | 0 to 100 degC | +/- 1% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 |  | RETAGGED MES01-TI-015 |  | 01
MES01 | MES01-TIC-001 | MES01-T-001 | PCS | 107-HG | INDICATING CONTROLLER - TEMPERATURE | RETAGGED MES01-TIC-015 |  | RETAGGED MES01-TIC-015 | [11 empty] | 0 | [5 empty] | RETAGGED MES01-TIC-015 |  | 01
MES01 | MES01-TT-001 | MES01-T-001 | FLD | 107-HG | TRANSMITTER - TEMPERATURE | RETAGGED MES01-TT-015 | 072.0 | RETAGGED MES01-TT-015 | 6591 | 0 to 100 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG | KT0004 |  | RETAGGED MES01-TT-015 |  | 01
MES01 | MES01-TAH-002 | MES01-T-002 | PCS | 107-HG | ALARM - TEMPERATURE - HIGH | REMOVED |  | REMOVED | [11 empty] | 0 | [5 empty] | REMOVED |  | 01
MES01 | MES01-TSH-002 | MES01-T-002 | FLD | 107-HG | SWITCH - TEMPERATURE - HIGH | REMOVED | 072.0 | REMOVED | 8690 | 95 deg C | +/- 2% | REF | 12 | C |  | I.S | DI |  |  | 32 | GP1 |  |  | KT0014 |  | REMOVED |  | 01
MES01 | MES01-TI-003 | MES01-T-003 | FLD | 107-HF | INDICATOR - TEMPERATURE | RELOCATED TO 9028901 | 072.0 | RELOCATED TO 9028901 | -: 0 to 100 degC; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 | N/A | WIKA | S5550/4 | KT0003 |  | RELOCATED TO 9028901 |  | 01
MES01 | MES01-TI-003 | MES01-T-003 | FLD | 107-HF | INDICATOR - TEMPERATURE | 40-HWF-CS1B-0-9028901 |  | JACKET HEATING SUPPLY |  | 0 to 100 degC | +/- 5% | REF | 12 | C | Ops | [6 empty] | WIKA | S5550/4 | KT0003/P1 |  |  |  | 01
MES01 | MES01-TT-003 | MES01-T-003 | [6 empty] | REQ: By request
MES01 | MES01-TE-004 | MES01-T-004 | FLD | 107-HF | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9025562 |  | RC07-VC1 HTF RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
MES01 | MES01-TI-004 | MES01-T-004 | PCS | 107-HF | INDICATOR - TEMPERATURE |  |  | RC07-VC1 HTF RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
MES01 | MES01-TT-004 | MES01-T-004 | FLD | 107-HF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 109.0 | RC07-VC1 HTF RTN TEMP. | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
MES01 | MES01-TE-005 | MES01-T-005 | FLD | 107-HF | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9025559 |  | RC07-VC1 VENT TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
MES01 | MES01-TI-005 | MES01-T-005 | PCS | 107-HF | INDICATOR - TEMPERATURE |  |  | RC07-VC1 VENT TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
MES01 | MES01-TT-005 | MES01-T-005 | FLD | 107-HF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 109.0 | RC07-VC1 VENT TEMP. | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
MES01 | MES01-TC-011 | MES01-T-011 | PCS | 107-HG | REMOTE SETPOINT - TEMPERATURE |  |  | HEAT/COOL PACKAGE | 13248 | 0 to 100 C |  | N/A | - | - | - | N.I.S | AO | 1 |  | 22 | GP1 | [6 empty] | 01
MES01 | MES01-TIC-011 | MES01-T-011 | PKG | 107-HG | INDICATING CONTROLLER - TEMPERATURE |  |  | HEAT/COOL PACKAGE | L15683 | 0 to 100 C | +/-2degC | GxP/SHE | 12 | C | Ops | N.I.S | AI | 1 |  | 13 | GP1 | [6 empty] | 01
MES01 | MES01-TSH-012 | MES01-T-012 | PKG | 107-HG | SWITCH - TEMPERATURE - HI |  |  | HEAT/COOL PACKAGE | REQ: By request; F: C; Ref: Ops | [10 empty] | 01
MES01 | MES01-TI-013 | MES01-T-013 | PCS | 107-HG | INDICATOR - TEMPERATURE |  |  | HEAT/COOL PACKAGE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-TT-013 | MES01-T-013 | PKG | 107-HG | TRANSMITTER - TEMPERATURE | HEAD MOUNTED |  | HEAT/COOL PACKAGE | REQ: By request; F: C; Ref: Ops; I.S: N.I.S; DI: AI | 1 |  | 13 | GP1 | [6 empty] | 01
MES01 | MES01-TSL-014 | MES01-T-014 | PKG | 107-HG | SWITCH - TEMPERATURE - LOW |  |  | HEAT/COOL PACKAGE | REQ: By request; F: C; Ref: Ops | [10 empty] | 01
MES01 | MES01-TE-015 | MES01-T-015 | FLD | 107-HF | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-H-9025589 |  | VC1 INLET TEMPERATURE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-TI-015 | MES01-T-015 | PCS | 107-HF | INDICATOR - TEMPERATURE |  |  | VC1 INLET TEMPERATURE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-TT-015 | MES01-T-015 | FLD | 107-HF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED |  | VC1 INLET TEMPERATURE | REQ: By request; F: C; Ref: Ops; I.S: I.S; DI: AI | 1 |  | 11 | GP1 | ROSEMOUNT | 644H | KT0004/P2 | TI702-SP-5012 |  |  | 01
MES01 | MES01-UI-001 | MES01-U-001 | PKG | 107-HF | MOBILE EQUIPMENT ANALOGUE 1 | MES01 | 072.0 | MOBILE EQUIPMENT STATION | 8691 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | GP1 |  |  |  | NOT REQUIRED | FIELD POWERED LOOP |  | 01
MES01 | MES01-UI-002 | MES01-U-002 | PKG | 107-HF | MOBILE EQUIPMENT ANALOGUE 2 | MES01 | 072.0 | EQUIP. ANALOGUE SIGNAL #2 | 8691 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | GP1 |  |  |  | NOT REQUIRED | FIELD POWERED LOOP |  | 01
MES01 | MES01-UA-003 | MES01-U-003 | PKG | 107-HF | MOBILE EQUIPMENT DISCRETE INPUT 1 | MES01 | 072.0 | EQUIP. DIGITAL SIGNAL | 8691 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | GP1 |  |  |  | NOT REQUIRED |  |  | 01
MES01 | MES01-UI-004 | MES01-U-004 | PKG | 107-HF | SPARE I/O | MES01 | 072.0 | SPARE | 8691 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | GP1 |  |  |  | NOT REQUIRED |  |  | 01
MES01 | MES01-UI-005 | MES01-U-005 | PKG | 107-HF | SPARE I/O | MES01 | 072.0 | SPARE | 8691 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | GP1 |  |  |  | NOT REQUIRED |  |  | 01
MES01 | MES01-YA-021 | MES01-Y-021 | PCS | 107-HG | ALARM - FAULT |  |  | HEAT/COOL PACKAGE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES01 | MES01-YS-021 | MES01-Y-021 | PKG | 107-HG | SWITCH - FAULT |  |  | HEAT/COOL PACKAGE | 13250 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | GP1 | [6 empty] | 01
MES01 | MES01-YS-022 | MES01-Y-022 | ?? | 107-HG | SWITCH - CRASH COOL |  |  | HEAT/COOL PACKAGE | REF: SHE; REQ: 12; F: F; Ref: GMP | [10 empty] | 01
MES02 | MES02-BD-001 | MES02-B-001 | FLD | 107-HC | RUPTURE DISC | RETAGGED FD04-BD-001 | 110.0 | RETAGGED FD04-BD-001 | 6732 | 1.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | FRS | KS0003 |  | RETAGGED FD04-BD-001 |  | 01
MES02 | MES02-YI-001 | MES02-B-001 | PCS | 107-HC | ALARM - RUPTURE DISC FAIL | RETAGGED FD04-YI-001 |  | RETAGGED FD04-YI-001 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-YI-001 |  | 01
MES02 | MES02-BD-002 | MES02-B-002 | FLD | 107-HC | RUPTURE DISC | RETAGGED FD04-BD-002 | 009.0 | RETAGGED FD04-BD-002 | 6762 | 1.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | FRS | KS0003 |  | RETAGGED FD04-BD-002 |  | 01
MES02 | MES02-YI-002 | MES02-B-002 | PCS | 107-HC | ALARM - RUPTURE DISC FAIL | RETAGGED FD04-YI-002 |  | RETAGGED FD04-YI-002 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-YI-002 |  | 01
MES02 | MES02-CV-001 | MES02-C-001 | FLD | 107-HC | BALL VALVE - ON/OFF - F.C. | RETAGGED FD04-CV-014 | 043.3 | RETAGGED FD04-CV-014 | 7088 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | RETAGGED FD04-CV-014 |  | 01
MES02 | MES02-CY-001 | MES02-C-001 | FLD | 107-HC | SOLENOID VALVE | RETAGGED FD04-CY-014 |  | RETAGGED FD04-CY-014 | I.S: I.S; DI: DO |  |  | 41 | GP2 |  |  |  |  | RETAGGED FD04-CY-014 |  | 01
MES02 | MES02-ZSC-001 | MES02-C-001 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | RETAGGED FD04-ZSC-014 |  | RETAGGED FD04-ZSC-014 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSC-014 |  | 01
MES02 | MES02-ZSO-001 | MES02-C-001 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | RETAGGED FD04-ZSO-014 |  | RETAGGED FD04-ZSO-014 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSO-014 |  | 01
MES02 | MES02-CV-012 | MES02-C-012 | FLD | 107-HC | BALL VALVE - ON/OFF - F.C. | RETAGGED FD04-CV-009 | 036.2 | RETAGGED FD04-CV-009 | 7282 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | RETAGGED FD04-CV-009 |  | 01
MES02 | MES02-CY-012 | MES02-C-012 | FLD | 107-HC | SOLENOID VALVE | RETAGGED FD04-CY-009 |  | RETAGGED FD04-CY-009 | I.S: I.S; DI: DO |  |  | 41 | GP2 |  |  |  |  | RETAGGED FD04-CY-009 |  | 01
MES02 | MES02-ZSC-012 | MES02-C-012 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | RETAGGED FD04-ZSC-009 |  | RETAGGED FD04-ZSC-009 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSC-009 |  | 01
MES02 | MES02-ZSO-012 | MES02-C-012 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | RETAGGED FD04-ZSO-009 |  | RETAGGED FD04-ZSO-009 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSO-009 |  | 01
MES02 | MES02-CV-013 | MES02-C-013 | FLD | 107-HC | BALL VALVE - ON/OFF - F.C. | RETAGGED FD04-CV-011 | 008.2 | RETAGGED FD04-CV-011 | 7255 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | RETAGGED FD04-CV-011 |  | 01
MES02 | MES02-CY-013 | MES02-C-013 | FLD | 107-HC | SOLENOID VALVE | RETAGGED FD04-CY-011 |  | RETAGGED FD04-CY-011 | I.S: I.S; DI: DO |  |  | 41 | GP2 |  |  |  |  | RETAGGED FD04-CY-011 |  | 01
MES02 | MES02-ZSC-013 | MES02-C-013 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | RETAGGED FD04-ZSC-011 |  | RETAGGED FD04-ZSC-011 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSC-011 |  | 01
MES02 | MES02-ZSO-013 | MES02-C-013 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | RETAGGED FD04-ZSO-011 |  | RETAGGED FD04-ZSO-011 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSO-011 |  | 01
MES02 | MES02-CV-015 | MES02-C-015 | FLD | 107-HC | V-BALL VALVE - CONTROL - F.C. | RETAGGED FD04-CV-008 | 110.0 | RETAGGED FD04-CV-008 | 6854 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC | AKH-3 | KV0004 |  | RETAGGED FD04-CV-008 |  | 01
MES02 | MES02-CV-016 | MES02-C-016 | FLD | 107-HC | V-BALL VALVE - CONTROL - F.C. | RETAGGED FD04-CV-010 | 110.0 | RETAGGED FD04-CV-010 | 6820 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC | AKH-3 | KV0004 |  | RETAGGED FD04-CV-010 |  | 01
MES02 | MES02-CV-018 | MES02-C-018 | FLD | 107-HC | V-BALL VALVE - CONTROL - F.C. | RETAGGED FD04-CV-017 | 110.0 | RETAGGED FD04-CV-017 | 6841 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC | AKH-3 | KV0004 |  | RETAGGED FD04-CV-017 |  | 01
MES02 | MES02-DIC-001 | MES02-D-001 | PCS | 107-HG | INDICATING CONTR. - MOTOR DRIVE | RETAGGED FD04-DIC-002 |  | RETAGGED FD04-DIC-002 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-DIC-002 |  | 01
MES02 | MES02-DS-001 | MES02-D-001 | CPR | 107-HG | DRIVE - AVAILABLE | RETAGGED FD04-DS-002 |  | RETAGGED FD04-DS-002 | I.S: N.I.S; DI: DI |  |  | 35 | GP2 |  |  |  |  | RETAGGED FD04-DS-002 |  | 01
MES02 | MES02-DY-001 | MES02-D-001 | CPR | 107-HG | DRIVE - RUNNING | RETAGGED FD04-DY-002 |  | RETAGGED FD04-DY-002 | I.S: N.I.S; DI: DI |  |  | 35 | GP2 |  |  |  |  | RETAGGED FD04-DY-002 |  | 01
MES02 | MES02-DYC-001 | MES02-D-001 | CPR | 107-HG | DRIVE - START/STOP | RETAGGED FD04-DYC-002 | 073.0 | RETAGGED FD04-DYC-002 | 8694 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 |  |  |  |  | RETAGGED FD04-DYC-002 |  | 01
MES02 | MES02-FI-003 | MES02-F-003 | FLD | 107-HC | INDICATOR - FLOW | REMOVED | 043.4 | REMOVED | -: 5 to 50L/min; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | KROHNE | DK32 | KF0027 |  | REMOVED |  | 01
MES02 | MES02-HV-001 | MES02-H-001 | FLD | 107-HC | HAND VALVE | REMOVED | 073.0 | REMOVED | 8123 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | REMOVED |  | 01
MES02 | MES02-HZSC-001 | MES02-H-001 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | REMOVED |  | REMOVED | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HZSO-001 | MES02-H-001 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | REMOVED |  | REMOVED | [11 empty] | 0 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HV-002 | MES02-H-002 | FLD | 107-HC | HAND VALVE | REMOVED | 110.0 | REMOVED | 7426 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES02 | MES02-HZSC-002 | MES02-H-002 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | RETAGGED FD04-ZSC-026 |  | RETAGGED FD04-ZSC-026 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSC-026 |  | 01
MES02 | MES02-HZSO-002 | MES02-H-002 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | RETAGGED FD04-ZSO-026 |  | RETAGGED FD04-ZSO-026 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSO-026 |  | 01
MES02 | MES02-HV-003 | MES02-H-003 | FLD | 107-HC | HAND VALVE | REMOVED | 110.0 | REMOVED | 7427 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES02 | MES02-HZSC-003 | MES02-H-003 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | RETAGGED FD04-ZSC-027 |  | RETAGGED FD04-ZSC-027 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSC-027 |  | 01
MES02 | MES02-HZSO-003 | MES02-H-003 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | RETAGGED FD04-ZSO-027 |  | RETAGGED FD04-ZSO-027 | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | RETAGGED FD04-ZSO-027 |  | 01
MES02 | MES02-HV-004 | MES02-H-004 | FLD | 107-HC | HAND VALVE | REMOVED | 043.4 | REMOVED | 7547 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | REMOVED |  | 01
MES02 | MES02-HZSC-004 | MES02-H-004 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | REMOVED |  | REMOVED | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HZSO-004 | MES02-H-004 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | REMOVED |  | REMOVED | [11 empty] | 0 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HV-005 | MES02-H-005 | FLD | 107-HC | HAND VALVE | REMOVED | 110.0 | REMOVED | 7428 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES02 | MES02-HZSC-005 | MES02-H-005 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | REMOVED |  | REMOVED | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HZSO-005 | MES02-H-005 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | REMOVED |  | REMOVED | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HV-006 | MES02-H-006 | FLD | 107-HC | HAND VALVE | REMOVED | 073.0 | REMOVED | 7462 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES02 | MES02-HZSC-006 | MES02-H-006 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | REMOVED |  | REMOVED | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HZSO-006 | MES02-H-006 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | REMOVED |  | REMOVED | [11 empty] | 0 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HV-007 | MES02-H-007 | FLD | 107-HC | HAND VALVE | REMOVED | 073.0 | REMOVED | 7463 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES02 | MES02-HZSC-007 | MES02-H-007 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | REMOVED |  | REMOVED | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HZSO-007 | MES02-H-007 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | REMOVED |  | REMOVED | [11 empty] | 0 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HV-008 | MES02-H-008 | FLD | 107-HC | HAND VALVE | REMOVED | 073.0 | REMOVED | 8127 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | REMOVED |  | 01
MES02 | MES02-HZSC-008 | MES02-H-008 | FLD | 107-HC | PROXIMITY SENSOR - CLOSED | REMOVED |  | REMOVED | I.S: I.S; DI: DI |  |  | 31 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-HZSO-008 | MES02-H-008 | FLD | 107-HC | PROXIMITY SENSOR - OPEN | REMOVED |  | REMOVED | [11 empty] | 0 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-LI-001A | MES02-L-001 | PCS | 107-HC | INDICATOR - LEVEL | RETAGGED FD04-LI-001A |  | RETAGGED FD04-LI-001A | [11 empty] | 0 | [5 empty] | RETAGGED FD04-LI-001A |  | 01
MES02 | MES02-LI-001B | MES02-L-001 | FLD | 107-HC | INDICATOR - LEVEL | RETAGGED FD04-LI-001B | 110.0 | RETAGGED FD04-LI-001B |  | 0 to 200L | +/- 2% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 |  | RETAGGED FD04-LI-001B |  | 01
MES02 | MES02-LT-001 | MES02-L-001 | FLD | 107-HC | TRANSMITTER - LEVEL | RETAGGED FD04-LT-001 | 110.0 | RETAGGED FD04-LT-001 | 6470 | 0 to 200 l | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ENDRESS + HAUSER | FMR245 note2 | KL0028/P2 |  | RETAGGED FD04-LT-001 |  | 01
MES02 | MES02-PI-001 | MES02-P-001 | FLD | 107-HC | PRESSURE GAUGE | REMOVED | 043.4 | REMOVED | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  | REMOVED |  | 01
MES02 | MES02-PI-002 | MES02-P-002 | FLD | 107-HC | PRESSURE GAUGE | REMOVED | 043.3 | REMOVED | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  | REMOVED |  | 01
MES02 | MES02-PI-004 | MES02-P-004 | FLD | 107-HC | PRESSURE GAUGE | REMOVED | 042.1 | REMOVED | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  | REMOVED |  | 01
MES02 | MES02-PI-005 | MES02-P-005 | FLD | 107-HC | PRESSURE GAUGE - DIAPHRAGM | REMOVED | 110.0 | REMOVED | -: -1 to 1.5 barg; -: +/- 1%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  | REMOVED |  | 01
MES02 | MES02-PIC-006 | MES02-P-006 | PCS | 107-HC | INDICATING CONTROLLER - PRESSURE | RETAGGED FD04-PIC-004 |  | RETAGGED FD04-PIC-004 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-PIC-004 |  | 01
MES02 | MES02-PIT-006 | MES02-P-006 | FLD | 107-HC | TRANSMITTER - PRESSURE - DIAPHRAGM | RETAGGED FD04-PT-004 | 110.0 | RETAGGED FD04-PT-004 | 6705 | -1 to 1 barg | 0.25% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | FOXBORO | 141GP (Note 2) | KP0001 |  | RETAGGED FD04-PT-004 |  | 01
MES02 | MES02-PI-007 | MES02-P-007 | FLD | 107-HC | PRESSURE GAUGE - DIAPHRAGM | REMOVED | 110.0 | REMOVED | -: -1 to 1.5 barg; -: +/- 1%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  | REMOVED |  | 01
MES02 | MES02-PSV-010 | MES02-P-010 | FLD | 107-HC | PRESSURE RELIEF VALVE | RETAGGED FD04-PSV010 | 110.0 | RETAGGED FD04-PSV010 | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  | RETAGGED FD04-PSV010 |  | 01
MES02 | MES02-PRV-011 | MES02-P-011 | PKG | 107-HG | CONTROL VALVE SELF ACTUATING | REMOVED | 073.0 | REMOVED | -: set @ 2.4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ROSEMOUNT | 98H(FS98H-75) | KV0006/1 |  | REMOVED |  | 01
MES02 | MES02-PI-012 | MES02-P-012 | PKG | 107-HG | PRESSURE GAUGE | REMOVED | 073.0 | REMOVED | -: 0 to 4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | REMOVED |  | 01
MES02 | MES02-RO-001 | MES02-R-001 | FLD | 107-HC | RESTRICTION ORIFICE PLATE | REMOVED | 043.3 | REMOVED | -: 100 Nm3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  | REMOVED |  | 01
MES02 | MES02-RO-002 | MES02-R-002 | PKG | 107-HG | RESTRICTION ORIFICE PLATE | REMOVED | 073.0 | REMOVED | [11 empty] | 0 |  | SITE FAB |  | SITE FAB/2 |  | REMOVED |  | 01 | bar: - to -
MES02 | MES02-TC-001 | MES02-T-001 | CPR | 107-HG | CONTROLLER - TEMPERATURE | RETAGGED FD04-TC-015 | 073.0 | RETAGGED FD04-TC-015 | 8694 | 0 to 100 degC | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP2 |  |  |  |  | RETAGGED FD04-TC-015 |  | 01
MES02 | MES02-TE-001 | MES02-T-001 | FLD | 107-HG | ELEMENT - TEMPERATURE - RTD | RETAGGED FD04-TE-015 |  | RETAGGED FD04-TE-015 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-TE-015 |  | 01
MES02 | MES02-TI-001 | MES02-T-001 | FLD | 107-HG | INDICATOR - TEMPERATURE | RETAGGED FD04-TI-015 | 073.0 | RETAGGED FD04-TI-015 |  | 0 to 100 degC | +/- 1% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 |  | RETAGGED FD04-TI-015 |  | 01
MES02 | MES02-TIC-001 | MES02-T-001 | PCS | 107-HG | INDICATING CONTROLLER - TEMPERATURE | RETAGGED FD04-TIC-015 |  | RETAGGED FD04-TIC-015 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-TIC-015 |  | 01
MES02 | MES02-TT-001 | MES02-T-001 | FLD | 107-HG | TRANSMITTER - TEMPERATURE | RETAGGED FD04-TT-015 | 073.0 | RETAGGED FD04-TT-015 | 8104 | 0 to 100 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG | KT0004 |  | RETAGGED FD04-TT-015 |  | 01
MES02 | MES02-TAH-002 | MES02-T-002 | PCS | 107-HG | ALARM - TEMPERATURE - HIGH | REMOVED |  | REMOVED | [11 empty] | 0 | [5 empty] | REMOVED |  | 01
MES02 | MES02-TSH-002 | MES02-T-002 | FLD | 107-HG | SWITCH - TEMPERATURE - HIGH | REMOVED | 073.0 | REMOVED | 8695 | 95 deg C | +/- 2% | REF | 12 | C |  | I.S | DI |  |  | 32 | GP2 |  |  | KT0014 |  | REMOVED |  | 01
MES02 | MES02-TI-003 | MES02-T-003 | FLD | 107-HC | INDICATOR - TEMPERATURE | RETAGGED FD04-TI-006 | 073.0 | RETAGGED FD04-TI-006 | -: 0 to 100 degC; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 | N/A | WIKA | S5550/4 | KT0003 |  | RETAGGED FD04-TI-006 |  | 01
MES02 | MES02-TE-004 | MES02-T-004 | FLD | 107-HC | ELEMENT - TEMPERATURE - RTD | RETAGGED FD04-TE-003 |  | RETAGGED FD04-TE-003 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-TE-003 |  | 01
MES02 | MES02-TI-004 | MES02-T-004 | PCS | 107-HC | INDICATOR - TEMPERATURE | RETAGGED FD04-TI-003 |  | RETAGGED FD04-TI-003 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-TI-003 |  | 01
MES02 | MES02-TT-004 | MES02-T-004 | FLD | 107-HC | TRANSMITTER - TEMPERATURE | RETAGGED FD04-TT-003 | 110.0 | RETAGGED FD04-TT-003 | 6624 | -30 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG | KT0004 |  | RETAGGED FD04-TT-003 |  | 01
MES02 | MES02-TE-005 | MES02-T-005 | FLD | 107-HC | ELEMENT - TEMPERATURE - RTD | RETAGGED FD04-TE-002 |  | RETAGGED FD04-TE-002 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-TE-002 |  | 01
MES02 | MES02-TI-005 | MES02-T-005 | PCS | 107-HC | INDICATOR - TEMPERATURE | RETAGGED FD04-TI-002 |  | RETAGGED FD04-TI-002 | [11 empty] | 0 | [5 empty] | RETAGGED FD04-TI-002 |  | 01
MES02 | MES02-TT-005 | MES02-T-005 | FLD | 107-HC | TRANSMITTER - TEMPERATURE | RETAGGED FD04-TT-002 | 110.0 | RETAGGED FD04-TT-002 | 6625 | -20 to 80 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG | KT0004 |  | RETAGGED FD04-TT-002 |  | 01
MES02 | MES02-UI-001 | MES02-U-001 | PKG | 107-HC | MOBILE EQUIPMENT ANALOGUE 1 | REMOVED | 073.0 | REMOVED | 8696 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-UI-002 | MES02-U-002 | PKG | 107-HC | MOBILE EQUIPMENT ANALOGUE 2 | REMOVED | 073.0 | REMOVED | 8696 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-UA-003 | MES02-U-003 | PKG | 107-HC | MOBILE EQUIPMENT DISCRETE INPUT 1 | REMOVED | 073.0 | REMOVED | 8696 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-UI-004 | MES02-U-004 | PKG | 107-HC | SPARE I/O | REMOVED | 073.0 | REMOVED | 8696 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | GP2 |  |  |  |  | REMOVED |  | 01
MES02 | MES02-UI-005 | MES02-U-005 | PKG | 107-HC | SPARE I/O | REMOVED | 073.0 | REMOVED | 8696 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | GP2 |  |  |  |  | REMOVED |  | 01
MES03 | MES03-BD-001 | MES03-B-001 | FLD | 107-HE | RUPTURE DISC | 40-P-PT1A-C-9025744 |  | RC11 BURSTING DISC | Deleted | 6.0 barg | - | N/A | - | - | - | I.S | DI | 1 |  | 32 | FG1 | BS&B | SPR-7 | KS0003/P4 |  |  |  | 01
MES03 | MES03-YI-001 | MES03-B-001 | PCS | 107-HE | ALARM - RUPTURE DISC FAIL | PCS |  | RC11 BURSTING DISC | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-BD-002 | MES03-B-002 | FLD | 107-HE | RUPTURE DISC | REPLACED | 009.0 | REPLACED | Deleted | 1.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | FG1 | BS&B | FRS | KS0003 |  | REPLACED | D2 | 01
MES03 | MES03-BD-002 | MES03-B-002 | FLD | 107-HE | RUPTURE DISC | 50-RV-CS1A-0-9028892 |  | PROCESS RELIEF | Deleted | 1.0 barg | - | N/A | - | - | - | I.S | DI | 1 |  | 32 | FG1 | BS&B | SPR-7 | KS0003/P4 |  |  |  | 01
MES03 | MES03-YI-002 | MES03-B-002 | PCS | 107-HE | ALARM - RUPTURE DISC FAIL | REPLACED |  | REPLACED | PKG: Deleted |  |  | 0 | [5 empty] | REPLACED |  | 01
MES03 | MES03-YI-002 | MES03-B-002 | PCS | 107-HE | ALARM - RUPTURE DISC FAIL | PCS |  | BURSTING DISC | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-CV-001 | MES03-C-001 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 15-N-SS1U-0-9028863 | 043.2 | 6 BAR N2 SUPPLY | Deleted | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
MES03 | MES03-CY-001 | MES03-C-001 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | 6 BAR N2 SUPPLY | PKG: Deleted; I.S: I.S; DI: DO |  |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-001 | MES03-C-001 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 | [6 empty] | 01
MES03 | MES03-ZSO-001 | MES03-C-001 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 | [6 empty] | 01
MES03 | MES03-CV-006 | MES03-C-006 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-H-9025751 |  | TO VC1 | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-006 | MES03-C-006 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | TO VC1 | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-006 | MES03-C-006 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO VC1 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-006 | MES03-C-006 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO VC1 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-012 | MES03-C-012 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9025948 |  | CONT. VACUUM | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-012 | MES03-C-012 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | CONT. VACUUM | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-012 | MES03-C-012 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CONT. VACUUM | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-012 | MES03-C-012 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CONT. VACUUM | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-013 | MES03-C-013 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9025746 |  | ACID SCRUBBER | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-013 | MES03-C-013 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | ACID SCRUBBER | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-013 | MES03-C-013 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ACID SCRUBBER | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-013 | MES03-C-013 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ACID SCRUBBER | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-014 | MES03-C-014 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9025742 |  | RC11 INLET | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-014 | MES03-C-014 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | RC11 INLET | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-014 | MES03-C-014 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RC11 INLET | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-014 | MES03-C-014 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RC11 INLET | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-015 | MES03-C-015 | FLD | 107-HE | V-BALL VALVE - CONTROL - F.C. | 40-VP-PT1A-0-9025948 |  | DRYER VACUUM | Deleted | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC | AKH-3 | KV0004/P1 |  |  |  | 01
MES03 | MES03-CV-016 | MES03-C-016 | FLD | 107-HE | V-BALL VALVE - CONTROL - F.C. | 40-P-PT1A-0-9025746 |  | DRYER VACUUM | Deleted | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC | AKH-3 | KV0004/P1 |  |  |  | 01
MES03 | MES03-CV-017 | MES03-C-017 | FLD | 107-HE | V-BALL VALVE - CONTROL - F.C. | 25-N-SS1U-0-9028896 |  | NITROGEN TO RC1 | Deleted | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC | AKH-3 | KV0004/P1 |  |  |  | 01
MES03 | MES03-CV-018 | MES03-C-018 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-902???? |  | TP1 DISCHARGE | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-018 | MES03-C-018 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | TP1 DISCHARGE | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-018 | MES03-C-018 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TP1 DISCHARGE | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-018 | MES03-C-018 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TP1 DISCHARGE | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-021 | MES03-C-021 | FLD | 107-HE | V-BALL VALVE - CONTROL - F.C. | 50-SV-GR1A-0-9026304 |  | GLOVEBOX TO LEV | Deleted | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | FG1 | HABONIM | 31 SERIES V-FLOW | KV0004/P1 |  |  |  | 01
MES03 | MES03-CV-023 | MES03-C-022 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 50-SV-GR1A-0-9026305 |  | ACID SCRUBBER | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-023 | MES03-C-022 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | ACID SCRUBBER | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-023 | MES03-C-022 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ACID SCRUBBER | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-023 | MES03-C-022 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ACID SCRUBBER | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-023 | MES03-C-023 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-C-9025740 |  | REFLUX | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-023 | MES03-C-023 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | REFLUX | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-023 | MES03-C-023 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REFLUX | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-023 | MES03-C-023 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REFLUX | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-024 | MES03-C-024 | FLD | 107-HE | BALL VALVE - ON/OFF - F.O. | 25-P-PT1A-0-9025741 |  | CONDENSATE TO RC1 | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-024 | MES03-C-024 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | CONDENSATE TO RC1 | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-024 | MES03-C-024 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CONDENSATE TO RC1 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-024 | MES03-C-024 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CONDENSATE TO RC1 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-025 | MES03-C-025 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9025743 |  | RC1 RECYCLE | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-025 | MES03-C-025 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | RC1 RECYCLE | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-025 | MES03-C-025 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RC1 RECYCLE | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-025 | MES03-C-025 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RC1 RECYCLE | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-026 | MES03-C-026 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023868 |  | PROCESS INLET 1 | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-026 | MES03-C-026 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | PROCESS INLET 1 | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-026 | MES03-C-026 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS INLET 1 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-026 | MES03-C-026 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS INLET 1 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-027 | MES03-C-027 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-902???? |  | SOLVENT INLET | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-027 | MES03-C-027 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | SOLVENT INLET | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-027 | MES03-C-027 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENT INLET | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-027 | MES03-C-027 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENT INLET | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-028 | MES03-C-028 | FLD | 107-HE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023784 |  | PROCESS INLET 2 | Deleted | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
MES03 | MES03-CY-028 | MES03-C-028 | FLD | 107-HE | SOLENOID VALVE | RACK MOUNTED |  | PROCESS INLET 2 | Deleted |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | [6 empty] | 01
MES03 | MES03-ZSC-028 | MES03-C-028 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS INLET 2 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-ZSO-028 | MES03-C-028 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS INLET 2 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-CV-031 | MES03-C-031 | PKG | 107-HH | V-BALL VALVE - CONTROL - F.C. |  |  | HEAT/COOL PACKAGE | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-DIC-001 | MES03-D-001 | PCS | 107-HH | INDICATING CONTR. - MOTOR DRIVE | PCS |  | HOT WATER PUMP | PKG: Deleted |  |  | 0 | [7 empty] | 01
MES03 | MES03-DS-001 | MES03-D-001 | CPR | 107-HH | DRIVE - AVAILABLE | MES03-HW1 PANEL |  | HOT WATER PUMP | PKG: Deleted; I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
MES03 | MES03-DY-001 | MES03-D-001 | CPR | 107-HH | DRIVE - RUNNING | MES03-HW1 PANEL |  | HOT WATER PUMP | PKG: Deleted; I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
MES03 | MES03-DYC-001 | MES03-D-001 | CPR | 107-HH | DRIVE - START/STOP | MES03-HW1 PANEL | 074.0 | HOT WATER PUMP | Deleted | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
MES03 | MES03-DIC-002 | MES03-D-002 | PCS | 107-HE | INDICATING CONTR. - MOTOR DRIVE | PCS |  | TP1 TRANSFER PUMP | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-DS-002 | MES03-D-002 | MCC | 107-HE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | Deleted |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 01
MES03 | MES03-DY-002 | MES03-D-002 | MCC | 107-HE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | Deleted |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 01
MES03 | MES03-DYC-002 | MES03-D-002 | MCC | 107-HE | DRIVE - START/STOP | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | Deleted | - | - | N/A | - | - | - | N.I.S | DO | 1 |  | 42 | FG1 | [6 empty] | 01
MES03 | MES03-DY-003 | MES03-D-003 | PKG | 107-HH | PACKAGE RUNNING |  |  | HEAT/COOL PACKAGE | Deleted |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | [7 empty] | 01
MES03 | MES03-DYC-003 | MES03-D-003 | PCS | 107-HH | PACKAGE - START/STOP | PCS |  | HEAT/COOL PACKAGE | Deleted |  |  | N/A | - | - | - | N.I.S | DO | 1 |  | 42 | GP2 | [6 empty] | 01
MES03 | MES03-FI-003 | MES03-F-003 | FLD | 107-HE | INDICATOR - FLOW | 15-N-SS1U-0-9028805 | 043.4 | 0.8 BARG N2 SUPPLY | PKG: Deleted; REQ: By request; F: C |  |  | 0 |  | KHRONE | DK32 | KF0027 |  |  |  | 01
MES03 | MES03-FS-011 | MES03-F-011 | PKG | 107-HH | FLOW SWITCH |  |  | HEAT/COOL PACKAGE | PKG: Deleted; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
MES03 | MES03-HV-001 | MES03-H-001 | FLD | 107-HE | HAND VALVE | REMOVED | 074.0 | REMOVED | Deleted | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | REMOVED |  | 01
MES03 | MES03-HZSC-001 | MES03-H-001 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | RETAGGED MES03-ZSC-027 |  | RETAGGED MES03-ZSC-027 | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | RETAGGED MES03-ZSC-027 |  | 01
MES03 | MES03-HZSO-001 | MES03-H-001 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | RETAGGED MES03-ZSO-027 |  | RETAGGED MES03-ZSO-027 | PKG: Deleted |  |  | 0 | FG1 |  |  |  |  | RETAGGED MES03-ZSO-027 |  | 01
MES03 | MES03-HV-002 | MES03-H-002 | FLD | 107-HE | HAND VALVE | REMOVED | 102.0 | REMOVED | Deleted | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES03 | MES03-HZSC-002 | MES03-H-002 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | RETAGGED MES03-HZSC-009 |  | RETAGGED MES03-HZSC-009 | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | RETAGGED MES03-HZSC-009 |  | 01
MES03 | MES03-HZSO-002 | MES03-H-002 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | RETAGGED MES03-HZSO-009 |  | RETAGGED MES03-HZSO-009 | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | RETAGGED MES03-HZSO-009 |  | 01
MES03 | MES03-HV-003 | MES03-H-003 | FLD | 107-HE | HAND VALVE | REPLACED | 102.0 | REPLACED | Deleted | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REPLACED |  | 01
MES03 | MES03-HV-003 | MES03-H-003 | FLD | 107-HE | HAND VALVE | 50-P-PT1A-0-9025752 |  | TO VC1 | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01
MES03 | MES03-HZSC-003 | MES03-H-003 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | REPLACED |  | REPLACED | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | REPLACED |  | 01
MES03 | MES03-HZSC-003 | MES03-H-003 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO VC1 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-HZSO-003 | MES03-H-003 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | REPLACED |  | REPLACED | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | REPLACED |  | 01
MES03 | MES03-HZSO-003 | MES03-H-003 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO VC1 | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-HV-004 | MES03-H-004 | FLD | 107-HE | HAND VALVE | 15-N-SS1U-0-9028805 | 043.4 | 0.8 BAR N2 SUPPLY (G1) | Deleted | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
MES03 | MES03-HZSC-004 | MES03-H-004 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY (G1) | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 | [6 empty] | 01
MES03 | MES03-HZSO-004 | MES03-H-004 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY (G1) | PKG: Deleted |  |  | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01
MES03 | MES03-HV-005 | MES03-H-005 | FLD | 107-HE | HAND VALVE | REPLACED | 102.0 | REPLACED | Deleted | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  | REPLACED |  | 01
MES03 | MES03-HV-005 | MES03-H-005 | FLD | 107-HE | HAND VALVE | 50-P-PT1A-0-9025742 |  | RC11 INLET | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01
MES03 | MES03-HZSC-005 | MES03-H-005 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | REPLACED |  | REPLACED | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | REPLACED |  | 01
MES03 | MES03-HZSC-005 | MES03-H-005 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | RC11 INLET | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-HZSO-005 | MES03-H-005 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | REPLACED |  | REPLACED | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | REPLACED |  | 01
MES03 | MES03-HZSO-005 | MES03-H-005 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | RC11 INLET | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-HV-006 | MES03-H-006 | FLD | 107-HE | HAND VALVE | REMOVED | 102.0 | REMOVED | Deleted | - | - | REF | REQ | F | [5 empty] | 0 | FG1 |  |  | KV0007 |  | REMOVED |  | 01
MES03 | MES03-HZSC-006 | MES03-H-006 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | RETAGGED MES03-ZSC-026 |  | RETAGGED MES03-ZSC-026 | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | RETAGGED MES03-ZSC-026 |  | 01
MES03 | MES03-HZSO-006 | MES03-H-006 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | RETAGGED MES03-ZSO-026 |  | RETAGGED MES03-ZSO-026 | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | RETAGGED MES03-ZSO-026 |  | 01
MES03 | MES03-HV-007 | MES03-H-007 | FLD | 107-HE | HAND VALVE | REMOVED | 074.0 | REMOVED | Deleted | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | REMOVED |  | 01
MES03 | MES03-HZSC-007 | MES03-H-007 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | RETAGGED MES03-ZSC-028 |  | RETAGGED MES03-ZSC-028 | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | RETAGGED MES03-ZSC-028 |  | 01
MES03 | MES03-HZSO-007 | MES03-H-007 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | RETAGGED MES03-ZSO-028 |  | RETAGGED MES03-ZSO-028 | PKG: Deleted |  |  | 0 | FG1 |  |  |  |  | RETAGGED MES03-ZSO-028 |  | 01
MES03 | MES03-HV-008 | MES03-H-008 | FLD | 107-HE | HAND VALVE | REMOVED | 074.0 | REMOVED | PKG: Deleted; REQ: 24; F: F |  |  | 0 |  |  |  | KV0017 |  | REMOVED |  | 01
MES03 | MES03-HZSC-008 | MES03-H-008 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | REMOVED |  | REMOVED | PKG: Deleted; I.S: I.S; DI: DI |  |  | 31 | FG1 |  |  |  |  | REMOVED |  | 01
MES03 | MES03-HZSO-008 | MES03-H-008 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | REMOVED |  | REMOVED | PKG: Deleted |  |  | 0 | FG1 |  |  |  |  | REMOVED |  | 01
MES03 | MES03-HV-009 | MES03-H-009 | FLD | 107-HE | HAND VALVE | 25-P-PT1A-C-9025740 |  | REFLUX | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01
MES03 | MES03-HZSC-009 | MES03-H-009 | FLD | 107-HE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REFLUX | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-HZSO-009 | MES03-H-009 | FLD | 107-HE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REFLUX | Deleted |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MES03 | MES03-LI-001B | MES03-L-001 | FLD | 107-HE | INDICATOR - LEVEL | FG1 |  | RC11 LEVEL | Deleted | 0 to 300 l | +/- 1% | REF | 12 | C | Ops | I.S | [5 empty] | BEKA | BA324D | KX0017/P1 |  |  |  | 01
MES03 | MES03-LIC-001 | MES03-L-001 | PCS | 107-HE | INDICATING CONTROLLER - LEVEL | PCS |  | RC11 LEVEL | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-LT-001 | MES03-L-001 | FLD | 107-HE | TRANSMITTER - LEVEL | MES03-RC11/N4/100 |  | RC11 LEVEL | Deleted |  |  |  | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ENDRESS + HAUSER | FMR245-24APKAA2A | KL0028/P3 |  |  |  | 01
MES03 | MES03-LAH-002 | MES03-L-002 | PCS | 107-HE | ALARM - LEVEL - HIGH | PCS |  | RC11 HIGH LEVEL | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-LSH-002 | MES03-L-002 | FLD | 107-HE | SWITCH - LEVEL - HIGH | MES03-RC11/N7/80 |  | RC11 HIGH LEVEL | Deleted | Off/on | Off/on | SHE | 24 | C | Ops | I.S | DI | 1 |  | 32 | FG1 | ENDRESS + HAUSER | FLT51 C 4ALKBK8G4AA | KL0014/P2 |  |  |  | 01
MES03 | MES03-PI-001 | MES03-P-001 | FLD | 107-HE | PRESSURE GAUGE | 15-N-SS1U-0-9028805 | 043.4 | 0.8 BARG N2 SUPPLY | Deleted | -1 to 1.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
MES03 | MES03-PI-002 | MES03-P-002 | FLD | 107-HE | PRESSURE GAUGE | 15-N-SS1U-0-9028863 | 043.2 | 6 BARG N2 SUPPLY | Deleted | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
MES03 | MES03-PI-004 | MES03-P-004 | FLD | 107-HE | PRESSURE GAUGE | 15-IA-SS1U-0-9028511 | 042.1 | INSTRUMENT AIR SUPPLY | Deleted | 0 to 10 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
MES03 | MES03-PI-005 | MES03-P-005 | FLD | 107-HE | PRESSURE GAUGE - DIAPHRAGM | REPLACED | 102.0 | REPLACED | Deleted | -1 to 1.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  | REPLACED |  | 01
MES03 | MES03-PI-005 | MES03-P-005 | FLD | 107-HE | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-H-9025752 |  | VC1 INLET PRESSURE | Deleted | -1 to 3 barg | +/1% | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100/990.27 | KP0006/P6 SHT2 |  |  |  | 01
MES03 | MES03-PIC-006 | MES03-P-006 | PCS | 107-HE | INDICATING CONTROLLER - PRESSURE | PCS |  | VC1 INLET PRESSURE | PKG: Deleted; REQ: By request; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-PIT-006 | MES03-P-006 | FLD | 107-HE | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-H-9025751 |  | VC1 INLET PRESSURE | Deleted | -1 to 3 barg | +/- 0.25% | REF | 12 | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 3051 | KP0001/P |  |  |  | 01
MES03 | MES03-PT-006 | MES03-P-006 | [6 empty] | REQ: By request
MES03 | MES03-PI-007 | MES03-P-007 | FLD | 107-HE | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-C-902???? |  | RC11 PRESSURE | Deleted | -1 to 3 barg | +/- 1% | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100/990.27 | KP0006/P6 |  |  |  | 01
MES03 | MES03-PI-008 | MES03-P-008 | FLD | 107-HE | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-0-902???? |  | TP1 DISCHARGE PRESSURE |  | 0 to 4 barg | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | 233.50.100/990.27 | KP0006/P6 |  |  |  | 01
MES03 | MES03-PSV-010 | MES03-P-010 | FLD | 107-HE | PRESSURE RELIEF VALVE | 25-HT-CS3A-O-9025748 |  | VC1 HTF RELIEF |  | 10 barg | +/- 10% | N/A | - | - | - | [6 empty] | BROADY | 2531D-C-B000 | KS0001/P |  |  |  | 01
MES03 | MES03-PRV-011 | MES03-P-011 | PKG | 107-HH | CONTROL VALVE SELF ACTUATING | 40-HWF-CS1B-H-9025732 | 074.0 | HOT WATER BYPASS RELIEF | PKG | set @ 2.4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | ROSEMOUNT | 98H(FS98H-75) | KV0006/1 |  |  |  | 01
MES03 | MES03-PI-012 | MES03-P-012 | PKG | 107-HH | PRESSURE GAUGE | MES03-HW1 | 074.0 | P1 DISCHARGE PRESSURE | PKG | 0 to 4 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
MES03 | MES03-PAH-027 | MES03-P-027 | PCS | 107-HE | ALARM - PRESSURE - HIGH |  |  |  | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-PSH-027 | MES03-P-027 | FLD | 107-HE | SWITCH - PRESSURE - HIGH | 50-RV-CS1A-0-9028892 |  | PROCESS ALARM | REQ: By request; F: C; Ref: Ops; I.S: I.S; DI: DI | 1 |  | 32 | FG1 | DELTA CONTROLS LTD | W28102G522C20 | KP0012/P |  |  |  | 01
MES03 | MES03-PI-028 | MES03-P-028 | FLD | 107-HE | PRESSURE GAUGE | 20-N-SS1U-0-9028897 |  | 6 BAR NITROGEN INLET |  | 0 to 10 barg | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100 | KP0006/P6 |  |  |  | 01
MES03 | MES03-PSV-030 | MES03-P-030 | PKG | 107-HH | PRESSURE RELIEF VALVE |  |  | HEAT/COOL PACKAGE | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-PSH-031 | MES03-P-031 | PKG | 107-HH | SWITCH - PRESSURE - HIGH |  |  | HEAT/COOL PACKAGE | PKG: Deleted; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
MES03 | MES03-PI-032 | MES03-P-032 | PKG | 107-HH | PRESSURE GAUGE |  |  | HEAT/COOL PACKAGE | Deleted | ??? |  | REF | REQ | C | Ref | [12 empty] | 01
MES03 | MES03-RO-001 | MES03-R-001 | FLD | 107-HE | RESTRICTION ORIFICE PLATE | 15-N-SS1U-0-9028863 | 043.2 | 6 BARG N2 SUPPLY | -: 100 Nm3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
MES03 | MES03-RO-002 | MES03-R-002 | PKG | 107-HH | RESTRICTION ORIFICE PLATE | REPLACED | 074.0 | REPLACED | PKG: Deleted; -: -; -: - |  |  | 0 |  | SITE FAB |  | SITE FAB/2 |  | REPLACED |  | 01
MES03 | MES03-RO-002 | MES03-R-002 | FLD | 107-HE | RESTRICTION ORIFICE | 25-P-PT1A-0-902???? |  | TP1 DISCHARGE | -: 5mm; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-TC-001 | MES03-T-001 | CPR | 107-HH | CONTROLLER - TEMPERATURE | RELOCATED TO 902???? | 074.0 | RELOCATED TO 902???? | Deleted | 0 to 100 degC | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | FG1 |  |  |  |  | RELOCATED TO 902???? |  | 01
MES03 | MES03-TE-001 | MES03-T-001 | FLD | 107-HH | ELEMENT - TEMPERATURE - RTD | RELOCATED TO 902???? |  | RELOCATED TO 902???? | PKG: Deleted |  |  | 0 | [5 empty] | RELOCATED TO 902???? |  | 01
MES03 | MES03-TI-001 | MES03-T-001 | FLD | 107-HH | INDICATOR - TEMPERATURE | RELOCATED TO 902???? | 074.0 | RELOCATED TO 902???? | Deleted | 0 to 100 degC | +/- 1% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 | RELOCATED TO 902???? |  | 01
MES03 | MES03-TIC-001 | MES03-T-001 | PCS | 107-HH | INDICATING CONTROLLER - TEMPERATURE | RELOCATED TO 902???? |  | RELOCATED TO 902???? | PKG: Deleted |  |  | 0 | [5 empty] | RELOCATED TO 902???? |  | 01
MES03 | MES03-TT-001 | MES03-T-001 | FLD | 107-HH | TRANSMITTER - TEMPERATURE | RELOCATED TO 902???? | 074.0 | RELOCATED TO 902???? | Deleted | 0 to 100 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 | RELOCATED TO 902???? |  | 01
MES03 | MES03-TAH-002 | MES03-T-002 | PCS | 107-HH | ALARM - TEMPERATURE - HIGH | RELOCATED TO 902???? |  | RELOCATED TO 902???? | PKG: Deleted |  |  | 0 | [5 empty] | RELOCATED TO 902???? |  | 01
MES03 | MES03-TSH-002 | MES03-T-002 | FLD | 107-HH | SWITCH - TEMPERATURE - HIGH | RELOCATED TO 902???? | 074.0 | RELOCATED TO 902???? | Deleted | 95 deg C | +/- 2% | REF | 12 | C |  | I.S | DI |  |  | 32 | FG1 |  |  | KT0014 |  | RELOCATED TO 902???? |  | 01
MES03 | MES03-TI-003 | MES03-T-003 | FLD | 107-HE | INDICATOR - TEMPERATURE | RELOCATED TO 9028946 | 074.0 | RELOCATED TO 9028946 | Deleted | 0 to 100 degC | +/- 2% | REF | REQ | C | [5 empty] | 0 | N/A | WIKA | S5550/4 | KT0003 |  | RELOCATED TO 9028946 |  | 01
MES03 | MES03-TI-003 | MES03-T-003 | FLD | 107-HE | INDICATOR - TEMPERATURE | 40-HWF-CS1B-H-9028946 |  | TEMPERATURE |  | 0 to 100 degC | +/- 5% | REF | 12 | C | Ops | [6 empty] | WIKA | S5550/4 | KT0003/P1 |  |  |  | 01
MES03 | MES03-TT-003 | MES03-T-003 | [6 empty] | REQ: By request
MES03 | MES03-TE-004 | MES03-T-004 | FLD | 107-HE | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9023707 |  | VC1 HTF RTN TEMP | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-TI-004 | MES03-T-004 | PCS | 107-HE | INDICATOR - TEMPERATURE |  |  | VC1 HTF RTN TEMP | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-TT-004 | MES03-T-004 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED |  | VC1 HTF RTN TEMP | REQ: By request; F: C; Ref: Ref; I.S: I.S; DI: AI | 1 |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P2 |  |  |  | 01
MES03 | MES03-TE-005 | MES03-T-005 | FLD | 107-HE | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9025746 |  | VC1 VENT TEMPERATURE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-TI-005 | MES03-T-005 | PCS | 107-HE | INDICATOR - TEMPERATURE |  |  | VC1 VENT TEMPERATURE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-TT-005 | MES03-T-005 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED |  | VC1 VENT TEMPERATURE | REQ: By request; F: C; Ref: Ops; I.S: I.S; DI: AI | 1 |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P2 |  |  |  | 01
MES03 | MES03-TC-011 | MES03-T-011 | PCS | 107-HH | REMOTE SETPOINT - TEMPERATURE | PCS |  | HEAT/COOL PACKAGE | Deleted | 0 to 100 C |  | N/A | - | - | - | N.I.S | AO | 1 |  | 22 | FG1 | [6 empty] | 01
MES03 | MES03-TIC-011 | MES03-T-011 | PKG | 107-HH | INDICATING CONTROLLER - TEMPERATURE |  |  | HEAT/COOL PACKAGE | Deleted | 0 to 100 C |  | REF | REQ | C | Ops | N.I.S | AI | 1 |  | 13 | FG1 | [6 empty] | 01
MES03 | MES03-TSH-012 | MES03-T-012 | PKG | 107-HH | SWITCH - TEMPERATURE - HI |  |  | HEAT/COOL PACKAGE | PKG: Deleted; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
MES03 | MES03-TI-013 | MES03-T-013 | PCS | 107-HH | INDICATOR - TEMPERATURE | PCS |  | HEAT/COOL PACKAGE | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-TT-013 | MES03-T-013 | PKG | 107-HG | TRANSMITTER - TEMPERATURE | HEAD MOUNTED |  | HEAT/COOL PACKAGE | REQ: By request; F: C; Ref: Ops; I.S: N.I.S; DI: AI | 1 |  | 13 | FG1 | [6 empty] | 01
MES03 | MES03-TSL-014 | MES03-T-014 | PKG | 107-HG | SWITCH - TEMPERATURE - LOW |  |  | HEAT/COOL PACKAGE | REQ: By request; F: C; Ref: Ops | [10 empty] | 01
MES03 | MES03-TE-015 | MES03-T-015 | FLD | 107-HE | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-H-9025751 |  | VC1 INLET TEMPERATURE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-TI-015 | MES03-T-015 | PCS | 107-HE | INDICATOR - TEMPERATURE |  |  | VC1 INLET TEMPERATURE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-TT-015 | MES03-T-015 | FLD | 107-HE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED |  | VC1 INLET TEMPERATURE | REQ: By request; F: C; Ref: Ops; I.S: I.S; DI: AI | 1 |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P2 |  |  |  | 01
MES03 | MES03-UI-001 | MES03-U-001 | PKG | 107-HE | MOBILE EQUIPMENT ANALOGUE 1 | MES03 | 074.0 | MOBILE EQUIPMENT STATION | 8701 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | FG1 |  |  |  |  | FIELD POWERED LOOP |  | 01
MES03 | MES03-UI-002 | MES03-U-002 | PKG | 107-HE | MOBILE EQUIPMENT ANALOGUE 2 | MES03 | 074.0 | EQUIP. ANALOGUE SIGNAL #2 | 8701 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | FG1 |  |  |  |  | FIELD POWERED LOOP |  | 01
MES03 | MES03-UA-003 | MES03-U-003 | PKG | 107-HE | MOBILE EQUIPMENT DISCRETE INPUT 1 | MES03 | 074.0 | EQUIP. DIGITAL SIGNAL | 8701 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | FG1 | [6 empty] | 01
MES03 | MES03-UI-004 | MES03-U-004 | PKG | 107-HE | SPARE I/O | MES03 | 074.0 | SPARE | 8701 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | FG1 | [6 empty] | 01
MES03 | MES03-UI-005 | MES03-U-005 | PKG | 107-HE | SPARE I/O | MES03 | 074.0 | SPARE | 8701 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | FG1 | [6 empty] | 01
MES03 | MES03-YA-021 | MES03-Y-021 | PCS | 107-HH | ALARM - FAULT | PCS |  | HEAT/COOL PACKAGE | PKG: Deleted; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MES03 | MES03-YS-021 | MES03-Y-021 | PKG | 107-HF | SWITCH - FAULT |  |  | HEAT/COOL PACKAGE | 13280 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 01
MES03 | MES03-YS-022 | MES03-Y-022 | ?? | 107-HG | SWITCH - CRASH COOL |  |  | HEAT/COOL PACKAGE | REF: SHE; REQ: 12; F: F; Ref: GMP | [10 empty] | 01
MES04 | MES04-BD-002 | MES04-B-002 | FLD | 107-HD | RUPTURE DISC | 25-P-PT1A-E-9025631 | 009.0 | BURSTING DISC | 6764 | 1.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | C1 | BS&B | FRS / BAS+ | KS0003 | TI702-SP-5077 |  |  | 01
MES04 | MES04-YI-002 | MES04-B-002 | PCS | 107-HD | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
MES04 | MES04-CV-001 | MES04-C-001 | FLD | 107-HD | BALL VALVE - ON/OFF - F.C. | 15-N-SS1U-0-9028866 | 043.2 | 6 BAR N2 SUPPLY | 7081 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
MES04 | MES04-CY-001 | MES04-C-001 | FLD | 107-HD | SOLENOID VALVE | RACK MOUNTED |  | 6 BAR N2 SUPPLY | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
MES04 | MES04-ZSC-001 | MES04-C-001 | FLD | 107-HD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-ZSO-001 | MES04-C-001 | FLD | 107-HD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 6 BAR N2 SUPPLY | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-DIC-001 | MES04-D-001 | PCS | 107-HH | INDICATING CONTR. - MOTOR DRIVE |  |  | HOT WATER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
MES04 | MES04-DS-001 | MES04-D-001 | CPR | 107-HH | DRIVE - AVAILABLE | MES04-HW1 PANEL |  | HOT WATER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
MES04 | MES04-DY-001 | MES04-D-001 | CPR | 107-HH | DRIVE - RUNNING | MES04-HW1 PANEL |  | HOT WATER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
MES04 | MES04-DYC-001 | MES04-D-001 | CPR | 107-HH | DRIVE - START/STOP | MES04-HW1 PANEL | 075.0 | HOT WATER PUMP | 8704 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
MES04 | MES04-FI-003 | MES04-F-003 | FLD | 107-HD | INDICATOR - FLOW | 15-N-SS1U-0-9028843 | 043.4 | 0.8 BARG N2 SUPPLY | REF: REF; REQ: By request; F: C |  |  | 0 |  | KHRONE | DK32 | KF0027 |  |  |  | 01
MES04 | MES04-HV-001 | MES04-H-001 | FLD | 107-HD | HAND VALVE | 25-P-SS1C-0-9024879 | 075.0 | SOLVENT WASH (A3) | 8124 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
MES04 | MES04-HZSC-001 | MES04-H-001 | FLD | 107-HD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENT WASH (A3) | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HZSO-001 | MES04-H-001 | FLD | 107-HD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENT WASH (A3) | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
MES04 | MES04-HV-002 | MES04-H-002 | FLD | 107-HD | HAND VALVE | 25-P-PT1A-E-9025629 | 106.0 | (V1) TO FD02-VC1 INLET | 7429 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MES04 | MES04-HZSC-002 | MES04-H-002 | FLD | 107-HD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | (V1) TO FD02-VC1 INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HZSO-002 | MES04-H-002 | FLD | 107-HD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | (V1) TO FD02-VC1 INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HV-003 | MES04-H-003 | FLD | 107-HD | HAND VALVE | 25-P-PT1A-E-9025608 | 106.0 | (V2) TO FDO2-VC1 INLET | 7430 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MES04 | MES04-HZSC-003 | MES04-H-003 | FLD | 107-HD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | (V2) TO FDO2-VC1 INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HZSO-003 | MES04-H-003 | FLD | 107-HD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | (V2) TO FDO2-VC1 INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HV-004 | MES04-H-004 | FLD | 107-HD | HAND VALVE | 15-N-SS1U-0-9028843 | 043.4 | 0.8 BAR N2 SUPPLY (G1) | 7548 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
MES04 | MES04-HZSC-004 | MES04-H-004 | FLD | 107-HD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY (G1) | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HZSO-004 | MES04-H-004 | FLD | 107-HD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 0.8 BAR N2 SUPPLY (G1) | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
MES04 | MES04-HV-005 | MES04-H-005 | FLD | 107-HD | HAND VALVE | 25-P-PT1A-0-9025619 | 106.0 | (B) TO FD02-RC1 | 7431 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MES04 | MES04-HZSC-005 | MES04-H-005 | FLD | 107-HD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | (B) TO FD02-RC1 | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HZSO-005 | MES04-H-005 | FLD | 107-HD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | (B) TO FD02-RC1 | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HV-006 | MES04-H-006 | FLD | 107-HD | HAND VALVE | 40-P-PT1A-0-9024867 | 075.0 | TRANSFER INLET (A2) | 7464 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MES04 | MES04-HZSC-006 | MES04-H-006 | FLD | 107-HD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TRANSFER INLET (A2) | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HZSO-006 | MES04-H-006 | FLD | 107-HD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TRANSFER INLET (A2) | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
MES04 | MES04-HV-007 | MES04-H-007 | FLD | 107-HD | HAND VALVE | 40-P-PT1A-0-9024828 | 075.0 | TRANSFER INLET (A1) | 7465 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
MES04 | MES04-HZSC-007 | MES04-H-007 | FLD | 107-HD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TRANSFER INLET (A1) | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HZSO-007 | MES04-H-007 | FLD | 107-HD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TRANSFER INLET (A1) | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
MES04 | MES04-HV-008 | MES04-H-008 | FLD | 107-HD | HAND VALVE | 25-P-SS1C-0-9024879 | 075.0 | SOLVENT WASH (A4) | 8128 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
MES04 | MES04-HZSC-008 | MES04-H-008 | FLD | 107-HD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENT WASH (A4) | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
MES04 | MES04-HZSO-008 | MES04-H-008 | FLD | 107-HD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENT WASH (A4) | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
MES04 | MES04-PI-001 | MES04-P-001 | FLD | 107-HD | PRESSURE GAUGE | 15-N-SS1U-0-9028843 | 043.4 | 0.8 BARG N2 SUPPLY | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
MES04 | MES04-PI-002 | MES04-P-002 | FLD | 107-HD | PRESSURE GAUGE | 15-N-SS1U-0-9028866 | 043.2 | 6 BARG N2 SUPPLY | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
MES04 | MES04-PI-004 | MES04-P-004 | FLD | 107-HD | PRESSURE GAUGE | 15-IA-SS1U-0-9028518 | 042.1 | INSTRUMENT AIR SUPPLY | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
MES04 | MES04-PI-005 | MES04-P-005 | FLD | 107-HD | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-E-9025629 | 106.0 | VENT PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
MES04 | MES04-PRV-011 | MES04-P-011 | PKG | 107-HH | CONTROL VALVE SELF ACTUATING | 40-HWF-CS1B-H-9025632 | 075.0 | HOT WATER BYPASS RELIEF | -: set @ 2.4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ROSEMOUNT | 98H(FS98H-75) | KV0006/1 |  |  |  | 01
MES04 | MES04-PI-012 | MES04-P-012 | PKG | 107-HH | PRESSURE GAUGE | MES04-HW1 | 075.0 | P1 DISCHARGE PRESSURE | -: 0 to 4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MES04 | MES04-RO-001 | MES04-R-001 | FLD | 107-HD | RESTRICTION ORIFICE PLATE | 15-N-SS1U-0-9028866 | 043.2 | 6 BARG N2 SUPPLY | -: 100 Nm3/hr; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
MES04 | MES04-RO-002 | MES04-R-002 | PKG | 107-HH | RESTRICTION ORIFICE PLATE | MES04-HW1 | 075.0 | HOT WATER DRAIN | [11 empty] | 0 |  | SITE FAB |  | SITE FAB/2 |  |  |  | 01 | bar: PKG to -
MES04 | MES04-TC-001 | MES04-T-001 | CPR | 107-HH | CONTROLLER - TEMPERATURE | MES04-HW1 PANEL | 075.0 | HOT WATER TEMPERATURE | 8704 | 0 to 100 degC | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | C1 | [6 empty] | 01
MES04 | MES04-TE-001 | MES04-T-001 | FLD | 107-HH | ELEMENT - TEMPERATURE - RTD | 40-HWF-CS1B-H-9028939 |  | HOT WATER TEMPERATURE | PKG: L15862; -: 0 to 100 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
MES04 | MES04-TI-001 | MES04-T-001 | FLD | 107-HH | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 075.0 | HOT WATER TEMPERATURE |  | 0 to 100 degC | +/- 1% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 01
MES04 | MES04-TIC-001 | MES04-T-001 | PCS | 107-HH | INDICATING CONTROLLER - TEMPERATURE |  |  | HOT WATER TEMPERATURE | PKG: L15862; -: 0 to 100 degC; -: +/- 2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
MES04 | MES04-TT-001 | MES04-T-001 | FLD | 107-HH | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 075.0 | HOT WATER TEMPERATURE | L15862 | 0 to 100 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
MES04 | MES04-TI-001B | MES04-T-001B | [6 empty] | REQ: By request
MES04 | MES04-TAH-002 | MES04-T-002 | PCS | 107-HH | ALARM - TEMPERATURE - HIGH |  |  | HOT WATER HIGH TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
MES04 | MES04-TSH-002 | MES04-T-002 | FLD | 107-HH | SWITCH - TEMPERATURE - HIGH | 40-HWF-CS1B-H-9028939 | 075.0 | HOT WATER HIGH TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 32 | C1 | DELTA CONTROLS LTD | W721 | KT0014 | TI702-SP-5126 |  |  | 01
MES04 | MES04-TI-003 | MES04-T-003 | FLD | 107-HD | INDICATOR - TEMPERATURE | 40-HWF-CS1B-9028939 | 075.0 | JACKET HEATING SUPPLY | REF: REF; REQ: By request; F: C |  |  | 0 | N/A | WIKA | S5550/4 | KT0003 |  |  |  | 01
MES04 | MES04-UI-001 | MES04-U-001 | PKG | 107-HD | MOBILE EQUIPMENT ANALOGUE 1 | MES04 | 075.0 | MOBILE EQUIPMENT STATION | 8706 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | C1 |  |  |  | NOT REQUIRED | FIELD POWERED LOOP |  | 01
MES04 | MES04-UI-002 | MES04-U-002 | PKG | 107-HD | MOBILE EQUIPMENT ANALOGUE 2 | MES04 | 075.0 | EQUIP. ANALOGUE SIGNAL #2 | 8706 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | C1 |  |  |  | NOT REQUIRED | FIELD POWERED LOOP |  | 01
MES04 | MES04-UA-003 | MES04-U-003 | PKG | 107-HD | MOBILE EQUIPMENT DISCRETE INPUT 1 | MES04 | 075.0 | EQUIP. DIGITAL SIGNAL | 8706 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | C1 |  |  |  | NOT REQUIRED |  |  | 01
MES04 | MES04-UI-004 | MES04-U-004 | PKG | 107-HD | SPARE I/O | MES04 | 075.0 | SPARE | 8706 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | C1 |  |  |  | NOT REQUIRED |  |  | 01
MES04 | MES04-UI-005 | MES04-U-005 | PKG | 107-HD | SPARE I/O | MES04 | 075.0 | SPARE | 8706 | 0 to 100 % | - | REF | REQ | F |  | I.S | AI |  |  | 11 | C1 |  |  |  | NOT REQUIRED |  |  | 01
MFD01 | MFD01-BD-001 | MFD01-B-001 | PKG | 107-EU | RUPTURE DISC | SCRAPPED | 105.0 | SCRAPPED | -: 2.7 barg; REQ: 12; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-DIC-001 | MFD01-D-001 | LCP | 107-EU | INDICATING CONTR. - MOTOR DRIVE | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-HS-001A | MFD01-H-001 | LCP | 107-EU | SWITCH - HAND OP. | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-HS-001B | MFD01-H-001 | LCP | 107-EU | SWITCH - HAND OP. | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-HS-002 | MFD01-H-002 | LCP | 107-EU | SWITCH - HAND OP. | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-HC-003 | MFD01-H-003 | LCP | 107-EU | CONTROLLER - HAND | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-HS-003 | MFD01-H-003 | LCP | 107-EU | SWITCH - HAND OP. | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-HC-004A | MFD01-H-004 | LCP | 107-EU | CONTROLLER - HAND | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-HC-004B | MFD01-H-004 | LCP | 107-EU | CONTROLLER - HAND | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-HS-004 | MFD01-H-004 | LCP | 107-EU | SWITCH - HAND OP. | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-HS-005 | MFD01-H-005 | LCP | 107-EU | SWITCH - HAND OP. | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-PI-001 | MFD01-P-001 | PKG | 107-EU | PRESSURE GAUGE | SCRAPPED | 105.0 | SCRAPPED | -: -1 to 5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  |  |  | KP0006/P4 |  | SCRAPPED |  | 01
MFD01 | MFD01-TI-008 | MFD01-T-008 | PKG | 107-EU | INDICATOR - TEMPERATURE | SCRAPPED | 105.0 | SCRAPPED | -: +/- 1%; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-YS-002 | MFD01-Y-002 | PKG | 107-EU | SWITCH - AGITATOR POSITION | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-YI-006 | MFD01-Y-006 | LCP | 107-EU | INDICATOR - LAMP | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD01 | MFD01-ZI-001 | MFD01-Z-001 | PKG | 107-EU | INDICATOR - MECHANICAL | SCRAPPED | 105.0 | SCRAPPED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | SCRAPPED |  | 01
MFD02 | MFD02-BD-011 | MFD02-B-011 | PKG | 107-HP | RUPTURE DISC | MFD02 | 166.0 | BURSTING DISC |  | 5.5 barg | - | N/A | - | - | - | [6 empty] | BS&B | RLS | KS0003 |  |  |  | 01
MFD02 | MFD02-YI-011 | MFD02-B-011 | LCP | 107-HP | ALARM - RUPTURE DISC FAIL | LCP ADJ TO MFD02 | 166.0 | BURSTING DISC | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-CV-002 | MFD02-C-002 | PKG | 107-HP | BALL VALVE - ON/OFF - F.C. | ???? | 166.0 | 0.8 BAR N2 SUPPLY |  | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MFD02 | MFD02-CY-002 | MFD02-C-002 | PKG | 107-HP | SOLENOID VALVE | RACK MOUNTED | 166.0 | 0.8 BAR N2 SUPPLY | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-ZSC-002 | MFD02-C-002 | PKG | 107-HP | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 166.0 | 0.8 BAR N2 SUPPLY | REF: N/A; REQ: -; F: -; Ref: - |  |  |  |  | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | MFD02-ZSO-002 | MFD02-C-002 | PKG | 107-HP | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 166.0 | 0.8 BAR N2 SUPPLY | REF: N/A; REQ: -; F: -; Ref: - |  |  |  |  | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | MFD02-CV-003 | MFD02-C-003 | PKG | 107-HP | BALL VALVE - ON/OFF - F.C. | ???? | 166.0 | 2 BAR N2 SUPPLY |  | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MFD02 | MFD02-CY-003 | MFD02-C-003 | PKG | 107-HP | SOLENOID VALVE | RACK MOUNTED | 166.0 | 2 BAR N2 SUPPLY | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-ZSC-003 | MFD02-C-003 | PKG | 107-HP | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 166.0 | 2 BAR N2 SUPPLY | REF: N/A; REQ: -; F: -; Ref: - |  |  |  |  | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | MFD02-ZSO-003 | MFD02-C-003 | PKG | 107-HP | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 166.0 | 2 BAR N2 SUPPLY | REF: N/A; REQ: -; F: -; Ref: - |  |  |  |  | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | MFD02-CV-004 | MFD02-C-004 | PKG | 107-HP | SOLENOID VALVE | MFD02 | 166.0 | FILTER PULSE |  | - | - | N/A | - | - | - | [12 empty] | 01
MFD02 | MFD02-CV-005 | MFD02-C-005 | PKG | 107-HP | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-E-9025013 | 166.0 | RECIRC |  | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MFD02 | MFD02-CY-005 | MFD02-C-005 | PKG | 107-HP | SOLENOID VALVE | RACK MOUNTED | 166.0 | RECIRC | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-ZSC-005 | MFD02-C-005 | PKG | 107-HP | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 166.0 | RECIRC | REF: N/A; REQ: -; F: -; Ref: - |  |  |  |  | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | MFD02-ZSO-005 | MFD02-C-005 | PKG | 107-HP | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 166.0 | RECIRC | REF: N/A; REQ: -; F: -; Ref: - |  |  |  |  | PEPPERL + FUCHS | NJ2-V3-N |  |  |  |  | 01
MFD02 | MFD02-CV-028 | MFD02-C-028 | PKG | 107-HP | BALL VALVE - ON/OFF - F.C. | ???? | 166.0 |  |  | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
MFD02 | MFD02-CV-029 | MFD02-C-029 | PKG | 107-HP | SOLENOID VALVE | MFD02 | 166.0 | MECHANICAL SEAL PURGE |  | - | - | N/A | - | - | - | [12 empty] | 01
MFD02 | MFD02-FI-001 | MFD02-F-001 | PKG | 107-HP | INDICATOR - FLOW |  | 166.0 | N2 SUPPLY FLOW | REF: REF; REQ: REQ; F: C; Ref: Ref | [10 empty] | 01
MFD02 | MFD02-FI-002 | MFD02-F-002 | PKG | 107-HP | INDICATOR - FLOW |  | 166.0 | MECHANICAL SEAL PURGE | REF: REF; REQ: REQ; F: C; Ref: Ref | [10 empty] | 01
MFD02 | MFD02-FAH-003 | MFD02-F-003 | LCP | 107-HP | ALARM - HIGH FLOW | LCP ADJ TO MFD02 | 166.0 | MECHANICAL SEAL PURGE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-FSH-003 | MFD02-F-003 | PKG | 107-HP | SWITCH - FLOW - LOW |  | 166.0 | MECHANICAL SEAL PURGE | REF: REF; REQ: 12; F: C; Ref: Ops | [10 empty] | 01
MFD02 | MFD02-HS-001A | MFD02-H-001 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-TOP | 166.0 | AGITATOR START |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-001B | MFD02-H-001 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | AGITATOR START |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-002A | MFD02-H-002 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-TOP | 166.0 | AGITATOR STOP |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-002B | MFD02-H-002 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | AGITATOR STOP |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-007A | MFD02-H-007 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-TOP | 166.0 | AGITATOR RAISE/LOWER |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-007B | MFD02-H-007 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | AGITATOR RAISE/LOWER |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-011 | MFD02-H-011 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02 | 166.0 | FILTER PULSE JET ON/OFF |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-012A | MFD02-H-012 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-TOP | 166.0 | AGITATOR SPEED UP/DOWN |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-012B | MFD02-H-012 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02 | 166.0 | AGITATOR SPEED UP/DOWN |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-013A | MFD02-H-013 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-TOP | 166.0 | EMERGENCY STOP |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
MFD02 | MFD02-HS-013B | MFD02-H-013 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | EMERGENCY STOP |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
MFD02 | MFD02-HS-014 | MFD02-H-014 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02 | 166.0 | BASE RAISE/LOWER |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-015 | MFD02-H-015 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | GLOVEBOX LOCK/UNLOCK |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-016 | MFD02-H-016 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | NITROGEN |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-017A | MFD02-H-017A | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02 | 166.0 | LIGHT |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-017B | MFD02-H-017B | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | LIGHT |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-018 | MFD02-H-018 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | VESSEL TILT POSITION DOWN/OFF/UP |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-019 | MFD02-H-019 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02 | 166.0 | MECHANICAL SEAL PURGE | REF: REF; REQ: REQ; F: F; Ref: Ref | [10 empty] | 01
MFD02 | MFD02-HS-020 | MFD02-H-020 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | AGITATOR DIRECTION |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-021 | MFD02-H-021 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | SYSTEM RESET |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-HS-022 | MFD02-H-022 | LCP | 107-HP | SWITCH - HAND OP. | LCP ADJ TO MFD02-GB1 | 166.0 | AGITATOR AUTO RAISE/LOWE ON/OFF |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-PI-002B | MFD02-P-002 | LCP | 107-HP | INDICATOR - PRESSURE | LCP ADJ TO MFD02 | 166.0 | PRESSURE |  | -1 to 6 barg | +/- 1% | SHE | 12 | C | SHE | [12 empty] | 01
MFD02 | MFD02-PIC-002A | MFD02-P-002 | PCS | 107-HP | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-PSHL-002 | MFD02-P-002 | PKG | 107-HP | SWITCH - PRESSURE - HIGH/LOW | MFD02/P1/80 | 166.0 | HIGH / LOW PRESSURE |  | set @ +/-30 mbar | +/- 1% | SHE | 12 | C | SHE | [12 empty] | 01
MFD02 | MFD02-PT-002 | MFD02-P-002 | PKG | 107-HP | TRANSMITTER - PRESSURE - DIAPHRAGM | MFD02/P1/80 | 166.0 | PRESSURE |  | -1 to 6 barg | 0.3%@0barg | SHE | 12 | C | SHE | [12 empty] | 01
MFD02 | MFD02-PDI-003 | MFD02-P-003 | PCS | 107-HP | INDICATOR - PRESSURE - DIFF |  |  | FILTER DIFF PRESSURE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-PDT-003 | MFD02-P-003 | PKG | 107-HP | TRANSMITTER - PRESSURE - DIFF | ACROSS FILTER | 166.0 | FILTER DIFF PRESSURE |  | 0 to 1 bar | +/- 2% | REF | 12 | C | Ops | [12 empty] | 01
MFD02 | MFD02-PRV-016 | MFD02-P-016 | PKG | 107-HP | CONTROL VALVE SELF ACTUATING |  | 166.0 | N2 SUPPLY |  | set @ 2 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
MFD02 | MFD02-PRV-017 | MFD02-P-017 | PKG | 107-HP | CONTROL VALVE SELF ACTUATING |  | 166.0 | N2 SUPPLY |  | set @ 0.8 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
MFD02 | MFD02-PI-018 | MFD02-P-018 | LCP | 107-HP | PRESSURE GAUGE | LCP ADJ TO MFD02-GB1 | 166.0 | GLOVEBOX PRESSURE |  | 0.05 TO 0.5 kpA | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
MFD02 | MFD02-PI-019 | MFD02-P-019 | LCP | 107-HP | PRESSURE GAUGE | LCP ADJ TO MFD02-GB1 | 166.0 | EXTRACT FILTER CONDITION |  | 0 to 125 pA | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
MFD02 | MFD02-PI-020 | MFD02-P-020 | PKG | 107-HP | PRESSURE GAUGE | 15-N-SS1U-0-902???? | 166.0 | AGITATOR SEAL PRESSURE |  | 0 to 6 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
MFD02 | MFD02-PDI-021 | MFD02-P-021 | LCP | 107-HP | INDICATOR - PRESSURE - DIFF | LCP ADJ TO MFD02-GB1 | 166.0 | NITROGEN FLOW |  | 0 to 1.6 barg | +/- 5% | SHE | 12 | C | SHE | [12 empty] | 01
MFD02 | MFD02-PAL-022 | MFD02-P-022 | LCP | 107-HP | ALARM - PRESSURE - LOW | LCP ADJ TO MFD02 | 166.0 |  | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-PSL-022 | MFD02-P-022 | PKG | 107-HP | SWITCH - PRESSURE - LOW | SEAL | 166.0 | AGI SEAL PRESSURE |  | set @??? | +/- 5% | REF | REQ | C | Ops | [12 empty] | 01
MFD02 | MFD02-PSH-023 | MFD02-P-023 | PKG | 107-HP | SWITCH - PRESSURE - HIGH | LCP ADJ TO MFD02-GB1 | 166.0 | GLOVEBOX PRESSURE HIGH | -: set @ -50mbarg; REF: SHE; REQ: 12; F: C; Ref: SHE | [10 empty] | 01
MFD02 | MFD02-PRV-024 | MFD02-P-024 | PKG | 107-HP | CONTROL VALVE SELF ACTUATING |  | 166.0 | GLOVEBOX PURGE |  | set @ 0.9 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
MFD02 | MFD02-PRV-025 | MFD02-P-025 | PKG | 107-HP | CONTROL VALVE SELF ACTUATING |  | 166.0 | MECHANICAL SEAL PURGE |  | set @ 4.5 barg | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
MFD02 | MFD02-PDSL-026 | MFD02-P-026 | PKG | 107-HP | SWITCH -PRESSURE - DIFF LOW |  | 166.0 |  | -: set @???; REF: SHE; REQ: 12; F: C; Ref: SHE | [10 empty] | 01
MFD02 | MFD02-PIC-033 | MFD02-P-033 | PCS | 107-HP | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-PT-033 | MFD02-P-033 | PKG | 107-HP | TRANSMITTER - PRESSURE | MFD02 GLOVEBOX | 166.0 | PRESSURE | REF: SHE; REQ: 12; F: C; Ref: SHE | [10 empty] | 01
MFD02 | MFD02-RO-001 | MFD02-R-001 | PKG | 107-HP | RESTRICTION ORIFICE |  | 166.0 | GLOVEBOX PURGE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-SI-001A | MFD02-S-001 | PCS | 107-HP | INDICATOR - SPEED |  | 166.0 | AGITATOR | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-SI-001B | MFD02-S-001 | LCP | 107-HP | INDICATOR - SPEED | LCP ADJ TO MFD02 | 166.0 | AGITATOR | REF: REF; REQ: REQ; F: C; Ref: Ref | [10 empty] | 01
MFD02 | MFD02-SIC-001 | MFD02-S-001 | PKG | 107-HP | AC INVERTER DRIVE | SWITCHROOM | 166.0 | AGITATOR |  | 0-24 rpm | +/- 2.5% | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-TI-004 | MFD02-T-004 | PKG | 107-HP | INDICATOR - TEMPERATURE | 25-HWR-SS1C-H-9025001 | 166.0 | HOT WATER RTN TEMPERATURE | REF: SHE; REQ: REQ; F: C; Ref: Ref | [10 empty] | 01
MFD02 | MFD02-TE-005 | MFD02-T-005 | PKG | 107-HP | ELEMENT - TEMPERATURE - RTD | MFD02/T1/40 | 166.0 | TEMPERATURE | REF: SHE; REQ: 12; F: C; Ref: GMP | [10 empty] | 01
MFD02 | MFD02-TI-005A | MFD02-T-005 | PCS | 107-HP | INDICATOR - TEMPERATURE |  |  | TEMPERATURE | REF: SHE; REQ: 12; F: C; Ref: GMP | [10 empty] | 01
MFD02 | MFD02-TI-005B | MFD02-T-005 | LCP | 107-HP | INDICATOR - TEMPERATURE | LCP ADJ TO MFD02 | 166.0 | TEMPERATURE |  | -30 to 170 degC | +/- 0.5% | SHE | 12 | C | GMP | [12 empty] | 01
MFD02 | MFD02-TSH-005A | MFD02-T-005 | CPR | 107-HP | SWITCH - TEMPERATURE - HI |  | 166.0 | TEMPERATURE HIGH | REF: SHE; REQ: 12; F: C; Ref: GMP | [10 empty] | 01
MFD02 | MFD02-TSH-005B | MFD02-T-005 | CPR | 107-HP | SWITCH - TEMPERATURE - HI |  | 166.0 | TEMPERATURE HIGH | REF: SHE; REQ: 12; F: C; Ref: GMP | [10 empty] | 01
MFD02 | MFD02-TT-005 | MFD02-T-005 | PKG | 107-HP | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 166.0 | TEMPERATURE |  | -30 to 170 degC | +/- 0.5% | SHE | 12 | C | GMP | [12 empty] | 01
MFD02 | MFD02-YS-002A | MFD02-Y-002 | PKG | 107-HP | SWITCH - POSITION | MFD02-GB1 | 166.0 | GLOVEBOX OPEN |  | - | - | SIL | 12 | F | SHE | [12 empty] | 01
MFD02 | MFD02-YS-002B | MFD02-Y-002 | PKG | 107-HP | SWITCH - POSITION | MFD02-GB1 | 166.0 | GLOVEBOX OPEN |  | - | - | SIL | 12 | F | SHE | [12 empty] | 01
MFD02 | MFD02-YI-003 | MFD02-Y-003 | LCP | 107-HP | INDICATOR - LAMP | LCP ADJ TO MFD02 | 166.0 | BASE FULLY RAISED | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-YS-003A | MFD02-Y-003 | PKG | 107-HP | SWITCH - BASE OPEN | MFD02 | 166.0 | BASE OPEN |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
MFD02 | MFD02-YS-003B | MFD02-Y-003 | PKG | 107-HP | SWITCH - BASE OPEN | MFD02 | 166.0 | BASE OPEN |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
MFD02 | MFD02-YS-003C | MFD02-Y-003 | PKG | 107-HP | SWITCH - BASE OPEN | MFD02 | 166.0 | BASE OPEN |  | - | - | SHE | 12 | F | SHE | [12 empty] | 01
MFD02 | MFD02-YI-004A | MFD02-Y-004 | PCS | 107-HP | INDICATOR - PERMISSIVE |  | 166.0 | PERMISSIVE INTERLOCK | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-YI-004B | MFD02-Y-004 | LCP | 107-HP | INDICATOR - PERMISSIVE | LCP ADJ TO MFD02 | 166.0 | PERMISSIVE INTERLOCK | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
MFD02 | MFD02-YS-004 | MFD02-Y-004 | PKG | 107-HP | PERMISSIVE SIGNAL | SWITCHROOM | 166.0 | PERMISSIVE INTERLOCK |  | - | - | REF | REQ | F | Ops | [12 empty] | 01
MFD02 | MFD02-YS-005 | MFD02-Y-005 | PKG | 107-HP | IN PLACE - PLUGGED IN | SWITCHROOM | 166.0 | PERMISSIVE INTERLOCK |  | - | - | REF | REQ | F | Ref | [12 empty] | 01
MFD02 | MFD02-YI-006 | MFD02-Y-006 | LCP | 107-HP | INDICATOR - LAMP | LCP ADJ TO MFD02-GB1 | 166.0 | AGITATOR RUNNING |  | - | - | N/A | - | - | - | [12 empty] | 01
MFD02 | MFD02-YI-013 | MFD02-Y-013 | LCP | 107-HP | INDICATOR - LAMP | LCP ADJ TO MFD02-GB1 | 166.0 | PURGE COMPLETE |  | - | - | N/A | - | - | - | [12 empty] | 01
MFD02 | MFD02-YI-014 | MFD02-Y-014 | LCP | 107-HP | INDICATOR - LAMP | LCP ADJ TO MFD02 | 166.0 | EMERGENCY STOP HEALTHY |  | - | - | N/A | - | - | - | [12 empty] | 01
MFD02 | MFD02-YI-015 | MFD02-Y-015 | LCP | 107-HP | INDICATOR - LAMP | LCP ADJ TO MFD02 | 166.0 | GUARDS CIRCUIT HEALTHY |  | - | - | N/A | - | - | - | [12 empty] | 01
MFD02 | MFD02-YS-016 | MFD02-Y-016 | LCP | 107-HP | SWITCH | MFD02 | 166.0 | BASE UN-CLAMPED |  | - | - | N/A | - | - | - | [12 empty] | 01
MFD02 | MFD02-YS-017 | MFD02-Y-017 | LCP | 107-HP | SWITCH | MFD02 | 166.0 | BASE IN PLACE |  | - | - | N/A | - | - | - | [12 empty] | 01
MFM01 | MFM01 | MFM01 | FLD | N/A | MOBILE FLOW METER | MFM01 | 173.1 | FLOW METER | REF: REF; REQ: REQ |  |  |  |  | ROXSPUR | FGMT222L |  |  |  |  | 01
MFM02 | MFM02 | MFM02 | FLD | N/A | MOBILE FLOW METER | MFM02 | 173.2 | FLOW METER | REF: REF; REQ: REQ |  |  |  |  | ROXSPUR | FGMT222L |  |  |  |  | 01
MFM03 | MFM03 | MFM03 | FLD | N/A | MOBILE FLOW METER | MFM03 | 173.3 | FLOW METER | REF: REF; REQ: REQ |  |  |  |  | ROXSPUR | FGMT111L |  |  |  |  | 05
MHT01 | MHT01-PI-001 | MHT01-P-001 | PKG | 107-BA | PRESSURE GAUGE - DIAPHRAGM | MHT01 | 100.1 | MHT01 PRESSURE | REF: SHE; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
MHT02 | MHT02-PI-001 | MHT02-P-001 | [6 empty] | REF: SHE; REQ: By request
MHT03 | MHT03-PI-001 | MHT03-P-001 | PKG | 107-CA | PRESSURE GAUGE - DIAPHRAGM | MHT03 | 100.3 | PRESSURE | REF: SHE; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
MHT04 | MHT04-PI-001 | MHT04-P-001 | PKG | 107-CA | PRESSURE GAUGE - DIAPHRAGM | MHT04 | 100.4 | PRESSURE | REF: SHE; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
MHT05 | MHT05-PI-001 | MHT05-P-001 | PKG | 107-BA | PRESSURE GAUGE - DIAPHRAGM | MHT05 | 100.5 | MHT05 PRESSURE | REF: SHE; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
MHT06 | MHT06-PI-001 | MHT06-P-001 | PKG | 107-HL | INDICATOR - PRESSURE | MHT06 | 145.0 | MHT06 PRESSURE | REF: SHE; REQ: By request; F: C |  |  |  |  | WIKA | 232.50.100 |  |  |  |  | 29
MHT07 | MHT07-PI-001 | MHT07-P-001 | [6 empty] | REF: SHE; REQ: By request
MHT08 | MHT08-BD-001 | MHT08-B-001 | PKG | 107-HL | BURSTING DISC | MHT08 | 160.0 | VESSEL PRESSURE RELIEF | -: 0.9 barg; -: ±0.05 barg; REF: REF; REQ: REQ |  |  |  |  | ELFAB | [5 empty] | 43
MHT08 | MHT08-PI-001 | MHT08-P-001 | PKG | 107-HL | INDICATOR - PRESSURE | MHT08 | 160.0 | MHT08 PRESSURE | REF: SHE; REQ: By request | [10 empty] | 43
MHT09 | MHT09-BD-001 | MHT-09-B-001 | PKG | 107-HL | BURSTING DISC | MHT09 | 161.0 | VESSEL PRESSURE RELIEF | -: 0.9 barg; -: ±0.05 barg; REF: REF; REQ: REQ |  |  |  |  | ELFAB | [5 empty] | 43
MHT09 | MHT09-PI-001 | MHT09-P-001 | PKG | 107-HL | INDICATOR - PRESSURE | MHT09 | 161.0 | MHT09 PRESSURE | REF: SHE; REQ: By request | [10 empty] | 43
MHT10 | MHT10-PI-001 | MHT10-P-001 | PKG | 107-HL | INDICATOR - PRESSURE | MHT10 | 147.0 | MHT10 PRESSURE | REF: SHE; REQ: By request; F: C |  |  |  |  | WIKA | 232.50.063 + M990.22 |  |  |  |  | 01
MHT10 | MHT10-RV-001 | MHT10-R-001 | PKG | 107-HL | RELIEF VALVE | MHT10 | 147.0 | PRESSURE | -: 6 barg; -: +/- 10%; REQ: 24; F: C |  |  |  |  | HANDTMANN | DN50 33501 |  |  |  |  | 01
MHT11 | MHT11-BD-001 | MHT11-B-001 | PKG | 107-SC | BURSTING DISC | MOBILE HEAD TANK | 178.0 | VESSEL PRESSURE RELIEF |  | 6.0 barg | +/- 5% | N/A | N/A | N/A |  | N/A | [5 empty] | BS&B | SKr / SMR-7R | KS0003/P7 |  |  |  | 06
MHT11 | MHT11-LI-001 | MHT11-L-001 | PKG | 107-SC | LEVEL INDICATOR | MOBILE HEAD TANK | 178.0 | VESSEL LEVEL | -: N/A; REF: SHE; REQ: N/A; F: F; I.S: N/A | [6 empty] | N/A |  |  |  | 06
MHT11 | MHT11-PI-001 | MHT11-P-001 | PKG | 107-SC | PRESSURE GUAGE | MOBILE HEAD TANK | 178.0 | VESSEL PRESSURE | REF: SHE; REQ: By Req; F: C; I.S: N/A |  |  |  |  | WIKA | 232.30 | KP0006-P11 |  |  |  | 06
MHT11 | MHT11-PI-002 | MHT11-P-002 | PKG | 107-SC | PRESSURE INDICATOR | MOBILE HEAD TANK | 178.0 | AGITATOR AIR SUPPLY | REF: Ref; REQ: By Req; F: C; I.S: N/A | [6 empty] | N/A |  |  |  | 06
MHT11 | MHT11-PRV-003 | MHT11-P-003 | PKG | 107-SC | CONTROL VALVE SELF ACTUATING | MOBILE HEAD TANK | 178.0 | AGITATOR AIR SUPPLY | -: 0-6 barg; REF: N/A; REQ: N/A; F: N/A; I.S: N/A | [6 empty] | N/A |  |  |  | 06
MHT11 | MHT11-SI-001 | MHT11-S-001 | PKG | 107-SC | SPEED INDICATOR | MOBILE HEAD TANK | 178.0 | AGITATOR SPEED | REF: Ref; REQ: By Req; F: C | [6 empty] | N/A |  |  |  | 06
MHT12 | MHT12-BD-001 | MHT12-B-001 | PKG | 107-SC | BURSTING DISC | MOBILE HEAD TANK | 179.0 | VESSEL PRESSURE RELIEF |  | 6.0 barg | +/- 5% | N/A | N/A | N/A |  | N/A | [5 empty] | BS&B | SKr / SMR-7R | KS0003/P7 |  | Removed from Use |  | 50
MHT12 | MHT12-BD-002 | MHT12-B-002 | PKG | 107-SC | BURSTING DISC | RELIEF HEADER | 179.0 | VESSEL PRESSURE RELIEF |  | 1.0 barg | +/- 5% | N/A | N/A | N/A |  | I.S |  | DI |  |  | C1 | BS&B | SKR / SMR-7R / BAS+ | KS0003/P7 | TI702-SP-5077 | Removed from Use |  | 50
MHT12 | MHT12-LI-001 | MHT12-L-001 | PKG | 107-SC | LEVEL INDICATOR | MOBILE HEAD TANK | 179.0 | VESSEL LEVEL | -: N/A; REF: SHE; REQ: N/A; F: F; I.S: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MHT12 | MHT12-PI-001 | MHT12-P-001 | PKG | 107-SC | PRESSURE GUAGE | MOBILE HEAD TANK | 179.0 | VESSEL PRESSURE |  | -1-10 barg | +/- 5% | SHE | By Req | C |  | N/A | [5 empty] | WIKA | 232.30 | KP0006-P11 |  | Removed from Use |  | 50
MHT12 | MHT12-PSV-002 | MHT12-P-002 | PKG | 107-SC | PRESSURE RELIEF VALVE | MOBILE HEAD TANK | 179.0 | WASTE INLET VALVE BY-PASS | -: 9 barg; REF: N/A; REQ: N/A; F: F |  |  |  |  | BROADY | 2600 | KS0001/P2 |  | Removed from Use |  | 50
MHT13 | MHT13-BD-001 | MHT13-B-001 | PKG | 107-SC | BURSTING DISC | MOBILE HEAD TANK | 180.0 | VESSEL PRESSURE RELIEF |  | 6.0 barg | +/- 5% | N/A | N/A | N/A |  | N/A | [5 empty] | BS&B | SKr / SMR-7R | KS0003/P7 |  | Removed from Use |  | 50
MHT13 | MHT13-LI-001 | MHT13-L-001 | PKG | 107-SC | LEVEL INDICATOR | MOBILE HEAD TANK | 180.0 | VESSEL LEVEL | -: N/A; REF: SHE; REQ: N/A; F: F; I.S: N/A | [6 empty] | N/A |  | Removed from Use |  | 50
MHT13 | MHT13-PI-001 | MHT13-P-001 | PKG | 107-SC | PRESSURE GUAGE | MOBILE HEAD TANK | 180.0 | VESSEL PRESSURE |  | -1-10 barg | +/- 5% | SHE | By Req | C |  | N/A | [5 empty] | WIKA | 232.30 | KP0006-P11 |  | Removed from Use |  | 50
MHT14 | MHT14-BD-001 | MHT14-B-001 | PKG | 902-007-002-000-00157 | BURSTING DISC | MOBILE HEAD TANK | 181.0 | VESSEL PRESSURE RELIEF |  | 6.0 barg | +/- 5% | N/A | N/A | N/A |  | N/A | [5 empty] | BS&B | SKr / SMR-7R | KS0003/P7 |  |  |  | 50
MHT14 | MHT14-CV-001A | MHT14-C-001 | PKG | 902-007-002-000-00157 | CONTROL VALVE SELF ACTUATING | MOBILE HEAD TANK | 181.0 | VESSEL FLOW | I.S: I.S; DI: AO |  |  |  | GP1 | SAMSON | 3730-2 POSITIONER |  | TI702-SP-5008 |  |  | 50
MHT14 | MHT14-CV-001B | MHT14-C-001 | PKG | 902-007-002-000-00157 | CONTROL VALVE SELF ACTUATING | MOBILE HEAD TANK | 181.0 | VESSEL FLOW | I.S: I.S; DI: AO |  |  |  | GP1 | SAMSON | 3730-2 POSITIONER |  | TI702-SP-5008 |  |  | 50
MHT14 | MHT14-FIT-001A | MHT14-F-001 | PKG | 902-007-002-000-00157 | FLOW INDICATING TRANSMITTER | MOBILE HEAD TANK | 155.0 | VESSEL FLOW | I.S: I.S; DI: AO |  |  |  | GP1 | EMERSON | CMFS025HB69N2EZEK22 |  | TI702-SP-5168 | Changed to 001A 19-09-2018 |  | 50
MHT14 | MHT14-FIT-001B | MHT14-F-001 | PKG | 902-007-002-000-00157 | FLOW INDICATING TRANSMITTER | MOBILE HEAD TANK | 155.0 | VESSEL FLOW | I.S: I.S; DI: AO |  |  |  | GP1 | EMERSON | 1700R12DEFE222 |  | TI702-SP-5169 | Added 19-09-2018
MHT14 | MHT14-LI-001 | MHT14-L-001 | PKG | 902-007-002-000-00157 | LEVEL INDICATOR | MOBILE HEAD TANK | 181.0 | VESSEL LEVEL | -: N/A; REF: SHE; REQ: N/A; F: F; I.S: N/A | [6 empty] | N/A |  |  |  | 50
MHT14 | MHT14-PI-001 | MHT14-P-001 | PKG | 902-007-002-000-00157 | PRESSURE GUAGE | MOBILE HEAD TANK | 181.0 | VESSEL PRESSURE |  | -1-10 barg | +/- 5% | SHE | By Req | C |  | N/A | [5 empty] | WIKA | 232.30 | KP0006-P11 |  |  |  | 50
MHT14 | MHT14-YA-001 | MHT14-Y-001 | PKG | 902-007-002-000-00157 |  |  |  | IN GP1B POSITION | I.S: I.S; DI: DI |  |  |  | GP1 | N/A | N/A |  | TI702-SP-5097 | Added 19-09-2018
MHT14 | MHT14-YS-001 | MHT14-Y-001 | PKG | 902-007-002-000-00157 |  |  |  | IN GP1A POSITION | I.S: I.S; DI: DI |  |  |  | GP1 | N/A | N/A |  | TI702-SP-5097 | Added 19-09-2018
MHT15 | MHT15-BD-001 | MHT15-B-001 | PKG | 902-007-002-000-00218 | BURSTING DISC | MOBILE HEAD TANK | 187.0 | VESSEL PRESSURE RELIEF | -: 7.0 barg; -: +/- 5%; REF: SHE; I.S: N/A |  |  |  |  | Fike | [6 empty] | v19.0
MHT15 | MHT15-LI-001A | MHT15-L-001 | PKG | 902-007-002-000-00218 | LEVEL INDICATOR | MOBILE HEAD TANK | 187.0 | VESSEL LEVEL | -: N/A; REF: SHE; I.S: N/A | [11 empty] | v19.0
MHT15 | MHT15-LI-001B | MHT15-L-001 | PKG | 902-007-002-000-00218 | LEVEL INDICATOR | MOBILE HEAD TANK | 187.0 | VESSEL LEVEL | -: N/A; REF: SHE; I.S: N/A | [11 empty] | v19.0
MHT15 | MHT15-PI-001 | MHT15-P-001 | PKG | 902-007-002-000-00218 | PRESSURE GUAGE | MOBILE HEAD TANK | 187.0 | VESSEL PRESSURE | -: -1 to 5 barg; -: +/- 2%; REF: SHE; I.S: N/A |  |  |  |  | WIKA | 232.30.100 | [5 empty] | v19.0
MHT15 | MHT15-PI-002 | MHT15-P-002 | PKG | 902-007-002-000-00218 | PRESSURE INDICATOR | MOBILE HEAD TANK | 187.0 | AGITATOR AIR SUPPLY | -: 0-6 barg; REF: Ref; I.S: N/A | [11 empty] | v19.0
MHT15 | MHT15-PRV-003 | MHT15-P-003 | PKG | 902-007-002-000-00218 | CONTROL VALVE SELF ACTUATING | MOBILE HEAD TANK | 187.0 | AGITATOR AIR SUPPLY | -: 0-6 barg; REF: N/A; I.S: N/A | [11 empty] | v19.0
MHT15 | MHT15-PSV-004 | MHT15-P-004 | PKG | 902-007-002-000-00218 | PRESSURE SAFETY VALVE | MOBILE HEAD TANK | 187.0 | VESSEL PRESSURE RELIEF | -: 7.0 barg; -: +/- 5%; REF: SHE; I.S: N/A |  |  |  |  | Leser | 459 | [5 empty] | v20.0
MHT15 | MHT15-PI-005 | MHT15-P-005 | PKG | 902-007-002-000-00218 | PRESSURE GUAGE | MOBILE HEAD TANK | 187.0 | Pressure monitoring | -: -1 to 5 barg; -: +/- 2%; REF: SHE; I.S: N/A |  |  |  |  | WIKA | 232.30.63 | [5 empty] | v20.0
MI01 | MI01-AAH-001 | MI01-A-001 | PLC/HMI | 107-PC | Oxygen high level alarm | PLC/HMI | 155.0 | Mill vent oxygen level | PKG: 12460; -: 6% | [10 empty] | 01
MI01 | MI01-AAHH-001 | MI01-A-001 | PLC/HMI | 107-PC | Oxygen high high level alarm | PLC/HMI | 155.0 | Mill vent oxygen level | PKG: 12460; -: 8% | [10 empty] | 01
MI01 | MI01-AI-001 | MI01-A-001 | HMI | 107-PC | Oxygen level indication | MI01-OCP | 155.0 | Mill vent oxygen level | PKG: 12460; -: 0 to 25% | [10 empty] | 01
MI01 | MI01-AT-001 | MI01-A-001 | FLD | 107-PC | Oxygen level transmitter | Sensor panel - service area | 155.0 | Mill vent oxygen level | PKG: 12460; -: 0 to 25% |  |  |  |  | NTRON | Oxytron 2000 Cell: OC-2 |  |  |  |  | 01
MI01 | MI01-AY-001 | MI01-A-001 | MI01-MCP | 107-PC | IS Barrier (integral to analyser) | MI01 Main Control Panel | 155.0 | Mill vent oxygen level | PKG: 12460 |  |  |  |  | NTRON | Integral to Oxytron 2000 |  |  |  |  | 01
MI01 | MI01-A-002 | MI01-A-002 | PLC/HMI | 107-PC | E-stop alarm | PLC/HMI | 155.0 | Emergency stop alarm | [19 empty] | 01 | bar: PKG
MI01 | MI01-CV-001 | MI01-C-001 | FLD | 107-PC | Diaphragm valve | 25-CWF-CS1B-AC-9028130 | 155.0 | Cooling water to throat | PKG: 12441 |  |  |  |  | DYNAQUIP | Dynamatic PHS22AJS023 |  |  |  |  | 01
MI01 | MI01-XV-001 | MI01-C-001 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | Cooling water to throat | PKG: 12441 |  |  |  |  | HOERBIGER | PS13210-616A |  |  |  |  | 01
MI01 | MI01-XY-001 | MI01-C-001 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Cooling water to throat | PKG: 12441 |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-CV-002 | MI01-C-002 | FLD | 107-PC | Diaphragm valve | Mounted on mill assembly | 155.0 | Back purge unit drain | PKG: 12442 |  |  |  |  | GEMU | 2099461-650020D8040521-1D1-1507 |  |  |  |  | 01
MI01 | MI01-XV-002 | MI01-C-002 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | Back purge unit drain | PKG: 12442 |  |  |  |  | HOERBIGER | PS13210-616A |  |  |  |  | 01
MI01 | MI01-XY-002 | MI01-C-002 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Back purge unit drain | PKG: 12442 |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-CV-003 | MI01-C-003 | FLD | 107-PC | Diaphragm valve | Mounted on mill assembly | 155.0 | Mill chamber vacuum supply | PKG: 12443 |  |  |  |  | GEMU | 2099462-650025D80405E1-2D1-1507 |  |  |  |  | 01
MI01 | MI01-XV-003 | MI01-C-003 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | Mill chamber vacuum supply | PKG: 12443 |  |  |  |  | HOERBIGER | PS13210-616A |  |  |  |  | 01
MI01 | MI01-XY-003 | MI01-C-003 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Mill chamber vacuum supply | PKG: 12443 |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-CV-004 | MI01-C-004 | FLD | 107-PC | Diaphragm valve | Mounted on mill assembly | 155.0 | CIP supply primary filter spray | PKG: 12444 |  |  |  |  | GEMU | 2099461-650020D8040521-1D1-1507 |  |  |  |  | 01
MI01 | MI01-XV-004 | MI01-C-004 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | CIP supply primary filter spray | PKG: 12444 |  |  |  |  | HOERBIGER | PS13210-616A |  |  |  |  | 01
MI01 | MI01-XY-004 | MI01-C-004 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | CIP supply primary filter spray | PKG: 12444 |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-CV-005 | MI01-C-005 | FLD | 107-PC | Rotary valve speed control valve | Pneumatic panel | 155.0 | Feed rotary valve speed | PKG: 12455; -: 0 to 100% |  |  |  |  | BAUMANN FISHER | 16-512020SC-3661 |  |  |  |  | 01
MI01 | MI01-CY-005 | MI01-C-005 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Feed rotary valve speed | PKG: 12455 |  |  |  |  | PEPPERL + FUCHS | KFD2-CD-Ex1.32 |  |  |  |  | 01
MI01 | MI01-CV-006 | MI01-C-006 | FLD | 107-PC | Diaphragm valve | Pneumatic panel | 155.0 | Nitrogen inertion to mill | PKG: 12445 |  |  |  |  | SMC | LVA30-03N-A1 |  |  |  |  | 01
MI01 | MI01-XV-006 | MI01-C-006 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | Nitrogen inertion to mill | PKG: 12445 |  |  |  |  | HOERBIGER | PS13210-616A |  |  |  |  | 01
MI01 | MI01-XY-006 | MI01-C-006 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Nitrogen inertion to mill | PKG: 12445 |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-CV-007 | MI01-C-007 | FLD | 107-PC | Diaphragm valve | Pneumatic panel | 155.0 | Wall protusion seal air supply | PKG: 12446 |  |  |  |  | SMC | LVA30-03N-A |  |  |  |  | 01
MI01 | MI01-XV-007 | MI01-C-007 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | Wall protusion seal air supply | PKG: 12446 |  |  |  |  | HOERBIGER | PS13210-616A |  |  |  |  | 01
MI01 | MI01-XY-007 | MI01-C-007 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Wall protusion seal air supply | PKG: 12446 |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-CV-010 | MI01-C-010 | FLD | 107-PC | Diaphragm valve | Pneumatic panel | 155.0 | Venturi nitrogen supply | PKG: 12449 |  |  |  |  | SMC | LVA30-03N-A1 |  |  |  |  | 01
MI01 | MI01-XV-010 | MI01-C-010 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | Venturi nitrogen supply | PKG: 12449 |  |  |  |  | HOERBIGER | PS13210-616A |  |  |  |  | 01
MI01 | MI01-XY-010 | MI01-C-010 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Venturi nitrogen supply | PKG: 12449 |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-CY-020A | MI01-C-020 |  |  | Solenoid Valve |  |  | Scrubber Select | I.S: I.S; DI: DO |  |  |  | UTIL | RGS | EP000/ia |  | TI702-SP-5133 | Added 19-09-2018
MI01 | MI01-CY-020B | MI01-C-020 |  |  | Solenoid Valve |  |  | Scrubber Select | I.S: I.S; DI: DO |  |  |  | UTIL | RGS | EP000/ia |  | TI702-SP-5133 | Added 19-09-2018
MI01 | MI01-ZSC-020 | MI01-C-020 |  |  | Valve Limit |  |  | Scrubber Select | I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Added 19-09-2018
MI01 | MI01-ZSO-020 | MI01-C-020 |  |  | Valve Limit |  |  | Scrubber Select | I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | Added 19-09-2018
MI01 | MI01-FAL-001 | MI01-F-001 | PLC/HMI | 107-PC | Low flow alarm | PLC/HMI | 155.0 | Nitrogen inertion flow to seal | PKG: 12454; -: 1.70 Nm3/hr; REF: SHE | [10 empty] | 01
MI01 | MI01-FI-001 | MI01-F-001 | HMI | 107-PC | Flow indication | MI01-OCP | 155.0 | Nitrogen inertion flow to seal | PKG: 12454; -: 0.11 to 5.52 Nm3/hr; REF: SHE | [10 empty] | 01
MI01 | MI01-FT-001 | MI01-F-001 | FLD | 107-PC | Flow meter | Pneumatic panel | 155.0 | Nitrogen inertion flow to seal | PKG: 12454; -: 0.11 to 5.52 Nm3/hr; REF: SHE |  |  |  |  | BROOKS | MF51S/AD1BB1BA0LA1B2 |  |  |  |  | 01
MI01 | MI01-FAL-002 | MI01-F-002 | PLC/HMI | 107-PC | Low flow alarm | PLC/HMI | 155.0 | Air supply to wall protrusion seal | PKG: 12439; -: 0.3 Nm3/hr; REF: SHE | [10 empty] | 01
MI01 | MI01-FI-002 | MI01-F-002 | FLD | 107-PC | Flow indicator | Pneumatic panel | 155.0 | Air supply to wall protrusion seal | PKG: 12439; -: 0.3 to 3.3 Nm3/hr; REF: SHE |  |  |  |  | KROHNE | H 250 RR M9 K1-EEx |  |  |  |  | 01
MI01 | MI01-FS-002 | MI01-F-002 | FLD | 107-PC | Flow switch | Pneumatic panel | 155.0 | Air supply to wall protrusion seal | PKG: 12439; -: 0.3 Nm3/hr; REF: SHE | [10 empty] | 01
MI01 | MI01-FY-001 | MI01-F-002 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Nitrogen inertion flow to seal | PKG: 12454; REF: SHE |  |  |  |  | PEPPERL + FUCHS | KFD2-CR-Ex1.30.300 |  |  |  |  | 01
MI01 | MI01-FY-002 | MI01-F-002 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Air supply to wall protrusion seal | PKG: 12439; REF: SHE |  |  |  |  | PEPPERL + FUCHS | KFD2-SR2-Ex1.W |  |  |  |  | 01
MI01 | MI01-FI-003 | MI01-F-003 | FLD | 107-PC | Flow indicator | 25-CWR-CS1B-AC-9027260 | 155.0 | Cooling water flow to throat | -: 330 to 800 kg/hr |  |  |  |  | KROHNE | H250/M9 |  |  |  |  | 01
MI01 | MI01-FCV-001 | MI01-FCV-001 | FLD | 107-PC | Flow control valve | Pneumatic panel | 155.0 | Nitrogen inertion flow to seal | PKG: 12453; -: 0.11 to 5.52 Nm3/hr |  |  |  |  | BROOKS | MF51S/AD1BB1BA0LA1B3 |  |  |  |  | 01
MI01 | MI01-FCY-001 | MI01-FCV-001 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Nitrogen inertion flow to seal | PKG: 12453 |  |  |  |  | PEPPERL + FUCHS | KFD2-CD-Ex1.32 |  |  |  |  | 01
MI01 | MI01-HS-001 | MI01-H-001 | HMI | 107-PC | Emergency stop | MI01-OCP | 155.0 | Emergency stop | REF: SHE |  |  |  |  | BARTEC | [5 empty] | 01
MI01 | MI01-HS-002 | MI01-H-002 | FLD | 107-PC | Emergency stop | Field | 155.0 | Emergency stop | REF: SHE |  |  |  |  | CEAG | [5 empty] | 01
MI01 | MI01-HS-003 | MI01-H-003 | MCP | 107-PC | Emergency stop | MI01 Main Control Panel | 155.0 | Emergency stop | REF: SHE |  |  |  |  | BARTEC | [5 empty] | 01
MI01 | MI01-HS-004 | MI01-H-004 | FLD | 107-PC | Emergency stop | Field | 155.0 | Emergency stop | REF: SHE |  |  |  |  | CEAG | [5 empty] | 01
MI01 | MI01-OP-001 | MI01-OP-001 | PLC/PCS | 107-PC | Mill running signal from PLC to PCS | PLC/PCS |  | Mill running signal | PKG: 12436
MI01 | MI01-PAH-001A | MI01-P-001 | PLC/HMI | 107-PC | High pressure alarm | PLC/HMI | 155.0 | Mill pressure | PKG: 12435; -: 0.0 mbar g | [10 empty] | 01
MI01 | MI01-PAH-001B | MI01-P-001 | PCS | 107-PC | High pressure alarm | PCS |  | Mill pressure | PKG: 12435; -: 68.53 mbarg
MI01 | MI01-PAHH-001A | MI01-P-001 | PLC/HMI | 107-PC | High high pressure alarm | PLC/HMI | 155.0 | Mill pressure | PKG: 12435; -: 2.0 mbarg | [10 empty] | 01
MI01 | MI01-PAHH-001B | MI01-P-001 | PCS | 107-PC | High high pressure alarm | PCS |  | Mill pressure | PKG: 12435; -: 75.48 mbarg
MI01 | MI01-PAL-001A | MI01-P-001 | PLC/HMI | 107-PC | Low pressure alarm | PLC/HMI | 155.0 | Mill pressure | PKG: 12435; -: -50.0 mbarg | [10 empty] | 01
MI01 | MI01-PAL-001B | MI01-P-001 | PCS | 107-PC | Low pressure alarm | PCS |  | Mill pressure | PKG: 12435; -: -68.53 mbarg
MI01 | MI01-PALL-001 | MI01-P-001 | PCS | 107-PC | Low low pressure alarm | PCS |  | Mill pressure | PKG: 12435; -: -75.48 mbarg
MI01 | MI01-PI-001B | MI01-P-001 | PCS | 107-PC | PCS pressure indication | PCS |  | Mill pressure | PKG: 12435; -: -62.3 to +62.3 mbarg
MI01 | MI01-PIC-001A | MI01-P-001 | HMI | 107-PC | Operator interface panel pressure indication | MI01-OCP | 155.0 | Mill pressure | PKG: 12435; -: -62.3 to +62.3 mbarg | [10 empty] | 01
MI01 | MI01-PT-001 | MI01-P-001 | FLD | 107-PC | Pressure transmitter | Pneumatic panel | 155.0 | Mill pressure | PKG: 12435; -: -62.3 to +62.3 mbarg |  |  |  |  | ROSEMOUNT | Tx: 3051CD2A22A1AS1I1Q4 Seal: 1199WGA93SSCW70LA00 |  |  |  |  | 01
MI01 | MI01-PY-001 | MI01-P-001 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Mill pressure | PKG: 12435 |  |  |  |  | PEPPERL + FUCHS | STC-STC4-Ex1.20 |  |  |  |  | 01
MI01 | MI01-PAL-002 | MI01-P-002 | PLC/HMI | 107-PC | Low pressure alarm | PLC/HMI | 155.0 | Nitrogen supply pressure | PKG: 12458; -: 1.5 barg; REF: SHE | [10 empty] | 01
MI01 | MI01-PS-002A | MI01-P-002 | FLD | 107-PC | Pressure switch (contacts pair A) | Pneumatic panel | 155.0 | Nitrogen supply pressure | PKG: 12458; -: 1.5 barg; REF: SHE |  |  |  |  | WIKA | MA XXDN |  |  |  |  | 01
MI01 | MI01-PS-002B | MI01-P-002 | FLD | 107-PC | Pressure switch (contacts pair B) | Pneumatic panel | 155.0 | Nitrogen supply pressure | PKG: 12458; -: 1.5 barg; REF: SHE | [10 empty] | 01
MI01 | MI01-PAH-003 | MI01-P-003 | PLC/HMI | 107-PC | High pressure alarm | PLC/HMI | 155.0 | Mill pressure | PKG: 12459; -: 12 mbarg; REF: SHE | [10 empty] | 01
MI01 | MI01-PS-003A | MI01-P-003 | FLD | 107-PC | Pressure switch (contacts pair A) | Pneumatic panel | 155.0 | Mill pressure | PKG: 12459; -: 12 mbarg; REF: SHE |  |  |  |  | WIKA | MAB XX DN |  |  |  |  | 01
MI01 | MI01-PS-003B | MI01-P-003 | FLD | 107-PC | Pressure switch (contacts pair B) | Pneumatic panel | 155.0 | Mill pressure | PKG: 12459; -: 12 mbarg; REF: SHE | [10 empty] | 01
MI01 | MI01-PRV-005 | MI01-P-005 | FLD | 107-PC | Pressure control valve | Pneumatic panel | 155.0 | Venturi pressure control | PKG: 12456; -: 0.2 to 8.0 barg |  |  |  |  | WATSON-SMITH | Type 422 |  |  |  |  | 01
MI01 | MI01-PRY-005 | MI01-P-005 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Venturi pressure control | PKG: 12456 |  |  |  |  | PEPPERL + FUCHS | KFD2-CD-Ex1.32 |  |  |  |  | 01
MI01 | MI01-PAL-006 | MI01-P-006 | PLC/HMI | 107-PC | Low pressure alarm | PLC/HMI | 155.0 | Mill vent pressure | PKG: 12450; -: -100 mbarg; REF: SHE | [10 empty] | 01
MI01 | MI01-PI-006 | MI01-P-006 | FLD | 107-PC | Pressure indicator | Pneumatic panel | 155.0 | Mill vent pressure | PKG: 12450; -: 0 to -250 mbarg; REF: SHE |  |  |  |  | WIKA | 432.50, Inductive sensor 831.12 |  |  |  |  | 01
MI01 | MI01-PS-006A | MI01-P-006 | FLD | 107-PC | Pressure switch (contacts pair A) | Pneumatic panel | 155.0 | Mill vent pressure | PKG: 12450; -: -100 mbarg; REF: SHE |  |  |  |  | PEPPERL + FUCHS | Prox switches: SJ2-N |  |  |  |  | 01
MI01 | MI01-PS-006B | MI01-P-006 | FLD | 107-PC | Pressure switch (contacts pair B) | Pneumatic panel | 155.0 | Mill vent pressure | PKG: 12450; -: -100 mbarg; REF: SHE |  |  |  |  | PEPPERL + FUCHS | Prox switches: SJ2-N |  |  |  |  | 01
MI01 | MI01-PY-006 | MI01-P-006 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Mill vent pressure | PKG: 12450; REF: SHE |  |  |  |  | PEPPERL + FUCHS | KFD2-SR2-Ex2.W |  |  |  |  | 01
MI01 | MI01-PI-001 | MI01-PRV-001 | FLD | 107-PC | Pressure gauge mounted on regulator | Pneumatic panel | 155.0 | Instrument air supply pressure regulation | [19 empty] | 01 | bar: PKG
MI01 | MI01-PRV-001 | MI01-PRV-001 | FLD | 107-PC | Pressure regulator | Pneumatic panel | 155.0 | Instrument air supply pressure regulation | [19 empty] | 01 | bar: PKG
MI01 | MI01-PI-002 | MI01-PRV-002 | FLD | 107-PC | Pressure gauge mounted on regulator | Pneumatic panel | 155.0 | Air to rotary valve motor pressure reg. | [13 empty] | SMC | [5 empty] | 01 | bar: PKG
MI01 | MI01-PRV-002 | MI01-PRV-002 | FLD | 107-PC | Pressure regulator | Pneumatic panel | 155.0 | Air to rotary valve motor pressure reg. | [19 empty] | 01 | bar: PKG
MI01 | MI01-PI-003 | MI01-PRV-003 | FLD | 107-PC | Pressure gauge mounted on regulator | Pneumatic panel | 155.0 | Nitrogen inertion to mill pressure reg. | [13 empty] | SMC | [5 empty] | 01 | bar: PKG
MI01 | MI01-PRV-003 | MI01-PRV-003 | FLD | 107-PC | Pressure regulator | Pneumatic panel | 155.0 | Nitrogen inertion to mill pressure reg. | [19 empty] | 01 | bar: PKG
MI01 | MI01-PI-004 | MI01-PRV-004 | FLD | 107-PC | Pressure gauge mounted on regulator | Pneumatic panel | 155.0 | Air to wall seal pressure regulation | [13 empty] | SMC | [5 empty] | 01 | bar: PKG
MI01 | MI01-PRV-004 | MI01-PRV-004 | FLD | 107-PC | Pressure regulator | Pneumatic panel | 155.0 | Air to wall seal pressure regulation | [19 empty] | 01 | bar: PKG
MI01 | MI01-SA-003 | MI01-S-003 | PLC/HMI | 107-PC | Rotary valve speed deviation from set point high | PLC/HMI | 155.0 | Feed rotary valve speed | PKG: 12451; -: +/- 5 rpm | [10 empty] | 01
MI01 | MI01-SIC-003 | MI01-S-003 | HMI | 107-PC | Rotary valve speed indication | MI01-OCP | 155.0 | Feed rotary valve speed | PKG: 12451; -: 0 to 50 rpm | [10 empty] | 01
MI01 | MI01-ST-003 | MI01-S-003 | MCP | 107-PC | Pulses to speed frequency convertor/IS barrier | Main control panel | 155.0 | Feed rotary valve speed | PKG: 12451; -: 0 to 50 rpm |  |  |  |  | PEPPERL + FUCHS | KFU8-UFC-Ex1.D |  |  |  |  | 01
MI01 | MI01-ZS-003 | MI01-S-003 | FLD | 107-PC | Reflexion light scanner - rotary valve speed (pulses) | Mounted on mill | 155.0 | Feed rotary valve speed | PKG: 12451; -: 25 pulses/rev |  |  |  |  | PEPPERL + FUCHS | OCT 300-M1K-N2 |  |  |  |  | 01
MI01 | MI01-SAL-004 | MI01-S-004 | PLC/HMI | 107-PC | Mill speed deviation from set point high | PLC/HMI | 155.0 | Mill rotor speed | PKG: 12452; -: +/- 200 rpm | [10 empty] | 01
MI01 | MI01-SI-004 | MI01-S-004 | HMI | 107-PC | Mill speed indication | MI01-OCP | 155.0 | Mill rotor speed | PKG: 12452; -: 0 to 9200 rpm | [10 empty] | 01
MI01 | MI01-ST-004 | MI01-S-004 | MCP | 107-PC | Pulses to speed frequency convertor/IS barrier | Main control panel | 155.0 | Mill rotor speed | PKG: 12452; -: 0 to 9200 rpm |  |  |  |  | PEPPERL + FUCHS | KFU8-UFC-Ex1.D |  |  |  |  | 01
MI01 | MI01-ZS-004 | MI01-S-004 | FLD | 107-PC | Proximity sensor - mill rotor speed (pulses) | Mounted on mill | 155.0 | Mill rotor speed | PKG: 12452; -: 4 pulses/rev; REQ: REQ |  |  |  |  | PEPPERL + FUCHS | NCB2-12GM35-N0 |  |  |  |  | 28
MI01 | MI01-TAH-001A | MI01-T-001 | PLC/HMI | 107-PC | High temperature alarm | PLC/HMI | 155.0 | Mill product outlet temperature | PKG: 12434; -: 40oC; REF: SHE | [10 empty] | 01
MI01 | MI01-TAH-001B | MI01-T-001 | PCS | 107-PC | High temperature alarm | PCS |  | Mill product outlet temperature | PKG: 12434; -: 110oC; REF: SHE | [10 empty] | 01
MI01 | MI01-TAHH-001B | MI01-T-001 | PCS | 107-PC | High high temperature alarm | PCS |  | Mill product outlet temperature | PKG: 12434; -: 120oC; REF: SHE | [10 empty] | 01
MI01 | MI01-TAL-001 | MI01-T-001 | PCS | 107-PC | Low temperature alarm | PCS |  | Mill product outlet temperature | PKG: 12434; -: -10oC; REF: SHE | [10 empty] | 01
MI01 | MI01-TALL-001 | MI01-T-001 | PCS | 107-PC | Low low temperature alarm | PCS |  | Mill product outlet temperature | PKG: 12434; -: -20oC; REF: SHE | [10 empty] | 01
MI01 | MI01-TE-001 | MI01-T-001 | FLD | 107-PC | Temperature element - RTD | Mounted on mill chamber | 155.0 | Mill product outlet temperature | PKG: 12434; -: 0 to 100oC; REF: SHE |  |  |  |  | ROSEMOUNT | 0068N21N00N090XAX8Q4 |  |  |  |  | 01
MI01 | MI01-TI-001A | MI01-T-001 | HMI | 107-PC | Operator interface panel temperature indication | MI01-OCP | 155.0 | Mill product outlet temperature | PKG: 12434; -: 0 to 100oC; REF: SHE | [10 empty] | 01
MI01 | MI01-TI-001B | MI01-T-001 | PCS | 107-PC | PCS temperature indication | PCS |  | Mill product outlet temperature | PKG: 12434; -: 0 to 100oC; REF: SHE | [10 empty] | 01
MI01 | MI01-TT-001 | MI01-T-001 | FLD | 107-PC | Temperature transmitter | Mounted on mill chamber | 155.0 | Mill product outlet temperature | PKG: 12434; -: 0 to 100oC; REF: SHE |  |  |  |  | ROSEMOUNT | 644HAI1XAJ5C2Q4 |  |  |  |  | 01
MI01 | MI01-TY-001 | MI01-T-001 | MI01-MCP | 107-PC | IS Barrier/repeater | MI01 Main Control Panel | 155.0 | Mill product outlet temperature | PKG: 12434; -: 0 to 100oC; REF: SHE |  |  |  |  | PEPPERL + FUCHS | STC-STC4-Ex1.20 |  |  |  |  | 01
MI01 | MI01-TAH-002 | MI01-T-002 | PLC/HMI | 107-PC | Mill motor high temperature alarm | PLC/HMI | 155.0 | Mill motor temperature | [19 empty] | 01 | bar: PKG
MI01 | MI01-XL-001 | MI01-X-001 | FLD | 107-PC | Alarm beacon | Mill room | 155.0 | Mill alarm beacon | PKG: 12457 |  |  |  |  | YSEBAERT | TNFCDM |  |  |  |  | 01
MI01 | MI01-XV-008a | MI01-X-008 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | Rotary valve motor air supply - forward | PKG: 12447; REF: SHE |  |  |  |  | HOERBIGER | PS13213-616A |  |  |  |  | 01
MI01 | MI01-XV-008b | MI01-X-008 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | Rotary valve motor air supply - reverse | PKG: 12447; REF: SHE |  |  |  |  | HOERBIGER | PS13213-616A |  |  |  |  | 01
MI01 | MI01-XY-008a | MI01-X-008 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Rotary valve motor air supply - forward | PKG: 12447; REF: SHE |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-XY-008b | MI01-X-008 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Rotary valve motor air supply - reverse | PKG: 12447; REF: SHE |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-XV-009 | MI01-X-009 | FLD | 107-PC | Solenoid valve | Pneumatic panel | 155.0 | Back purge cylinder air supply | PKG: 12448 |  |  |  |  | HOERBIGER | PS13213-616A |  |  |  |  | 01
MI01 | MI01-XY-009 | MI01-X-009 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Back purge cylinder air supply | PKG: 12448 |  |  |  |  | PEPPERL + FUCHS | KFD2-SD-Ex1.17 |  |  |  |  | 01
MI01 | MI01-YA-001 | MI01-YA-001 | PLC/PCS | 107-PC | Mill common alarm from PLC to PCS | PLC/PCS |  | Mill common alarm | PKG: 12437
MI01 | MI01-ZA-001 | MI01-Z-001 | PLC/HMI | 107-PC | Feed butterfly valve not present alarm | PLC/HMI | 155.0 | Feed butterfly valve position | PKG: 12461; REF: SHE | [10 empty] | 01
MI01 | MI01-ZS-001 | MI01-Z-001 | FLD | 107-PC | Feed butterfly valve position sensor | Mounted on mill assembly | 155.0 | Feed butterfly valve position | PKG: 12461; REF: SHE |  |  |  |  | ELOBAU | 671.271.NU0 |  |  |  |  | 01
MI01 | MI01-ZA-002 | MI01-Z-002 | FLD | 107-PC | Throat not in position alarm | PLC/HMI | 155.0 | Throat position | PKG: 12462; REF: SHE | [10 empty] | 01
MI01 | MI01-ZS-002 | MI01-Z-002 | FLD | 107-PC | Throat position sensor | Mounted on mill assembly | 155.0 | Throat position | PKG: 12462; REF: SHE |  |  |  |  | ELOBAU | 671.271.NU0 |  |  |  |  | 01
MI01 | MI01-ZA-005 | MI01-Z-005 | PLC/HMI | 107-PC | Mill rotation direction incorrect alarm | PLC/HMI | 155.0 | Mill rotation direction | PKG: 12440 | [10 empty] | 01
MI01 | MI01-ZS-005 | MI01-Z-005 | FLD | 107-PC | Mill rotation direction sensor | Mounted on mill assembly | 155.0 | Mill rotation direction | PKG: 12440 |  |  |  |  | PEPPERL + FUCHS | NCB2-12GM35-N0 |  |  |  |  | 01
MI01 | MI01-ZY-005 | MI01-Z-005 | MI01-MCP | 107-PC | IS Barrier | MI01 Main Control Panel | 155.0 | Mill rotation direction | PKG: 12440 |  |  |  |  | PEPPERL + FUCHS | KFD2-SR2-Ex1.W |  |  |  |  | 01
MINST | MINST-AIC-001 | MINST-A-001 | PKG | 902-007-002-000-00211 | CONTROLLER | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION CONTROLLER | [13 empty] | AQUASANT | MIQ 8130 | [5 empty] | 16 | bar: PKG
MINST | MINST-AI-001A | MINST-A-001 | PKG | 902-007-002-000-00211 | PULSE INDICATOR | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | [13 empty] | AQUASANT | MIQ 8130 | [5 empty] | 15 | bar: PKG
MINST | MINST-AI-001B | MINST-A-001 | FLD | 902-007-002-000-00211 | PULSE INDICATOR | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | I.S: I.S. |  |  |  |  | BEKA | BA307E | [5 empty] | 15
MINST | MINST-AT-001 | MINST-A-001 | PKG | 902-007-002-000-00211 | MOBILE INTERFACE DETECTOR | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | I.S: I.S. |  |  |  |  | AQUASANT | TSS80 PIPE PROBE | [5 empty] | 15
MINST | MINST-HS-001 | MINST-H-001 | FLD | 902-007-002-000-00211 | SWITCH - START/STOP | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | [20 empty] | 16 | bar: PKG
MINST | MINST-HS-002 | MINST-H-002 | FLD | 902-007-002-000-00211 | PUSH BUTTON - LAMP TEST | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | bar: PKG
MINST | MINST-YI-001A | MINST-Y-001 | FLD | 902-007-002-000-00211 | INDICATOR LAMP | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | I.S: I.S. |  |  |  |  | BEKA | BA390G | [5 empty] | 15
MINST | MINST-YI-001B | MINST-Y-001 | FLD | 902-007-002-000-00211 | INDICATOR LAMP | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | I.S: I.S. |  |  |  |  | BEKA | BA390R | [5 empty] | 15
MINST | MINST-YS-001 | MINST-Y-001 | PKG | 902-007-002-000-00211 | SWITCH - INTERFACE STATUS | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | [20 empty] | 15 | bar: PKG
MINST | MINST-YS-002 | MINST-Y-002 | PKG | 902-007-002-000-00211 | SWITCH - SELECTOR | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | [17 empty] | Implemented as jumper cable in Exd enclosure |  |  | 18 | bar: PKG
MINST | MINST-YS-003 | MINST-Y-003 | PKG | 902-007-002-000-00211 | SWITCH - SELECTOR | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | [17 empty] | Implemented as jumper cable in Exd enclosure |  |  | 18 | bar: PKG
MINST | MINST-YS-004 | MINST-Y-004 | PKG | 902-007-002-000-00211 | SWITCH - SELECTOR | MOBILE INTERFACE DETECTOR SKID | 192.1 | INTERFACE DETECTION | [17 empty] | Implemented as jumper cable in Exd enclosure |  |  | 18 | bar: PKG
MIR01 | MIR01-CV-001 | MIR01-C-001 | PKG | 107-HM | CONTROL VALVE | MIR01 | 148.1 | MIR01 PURGE UNIT CONTROL VALVE | [19 empty] | 16 | bar: PKG
MIR01 | MIR01-FI-001 | MIR01-F-001 | PKG | 107-HM | FLOW METER | MIR01 | 148.1 | MIR01 FLOW | [19 empty] | 16 | bar: PKG
MIR01 | MIR01-FI-002 | MIR01-F-002 | PKG | 107-HM | FLOW METER | MIR01 | 148.1 | MIR01 FLOW | [19 empty] | 16 | bar: PKG
MIR01 | MIR01-PRV-001 | MIR01-P-001 | PKG | 107-HM | PRESSURE REDUCING VALVE | MIR01 | 148.1 | MIR01 PRESSURE | [19 empty] | 16 | bar: PKG
MIR01 | MIR01-PI-002 | MIR01-P-002 | PKG | 107-HM | PRESSURE GAUGE | MIR01 | 148.1 | MIR01 PRESSURE | [19 empty] | 16 | bar: PKG
MIR01 | MIR01-PSV-003 | MIR01-P-003 | PKG | 107-HM | RELIEF VALVE | MIR01 | 148.1 | MIR01 PRESSURE | [19 empty] | 16 | bar: PKG
MIR02 | MIR02-CV-001 | MIR02-C-001 | PKG | 107-HM | CONTROL VALVE | MIR02 | 148.2 | MIR02 PURGE UNIT CONTROL VALVE | [19 empty] | 16 | bar: PKG
MIR02 | MIR02-PRV-001 | MIR02-P-001 | PKG | 107-HM | PRESSURE REDUCING VALVE | MIR02 | 148.2 | MIR02 PRESSURE | [19 empty] | 16 | bar: PKG
MIR02 | MIR02-PI-002 | MIR02-P-002 | PKG | 107-HM | PRESSURE GAUGE | MIR02 | 148.2 | MIR02 PRESSURE | [19 empty] | 16 | bar: PKG
MIR02 | MIR02-PRV-003 | MIR02-P-003 | PKG | 107-HM | PRESSURE REDUCING VALVE | MIR02 | 148.2 | MIR02 PRESSURE | [19 empty] | 16 | bar: PKG
MIR02 | MIR02-PRV-004 | MIR02-P-004 | PKG | 107-HM | PRESSURE REDUCING VALVE | MIR02 | 148.2 | MIR02 PRESSURE | [19 empty] | 16 | bar: PKG
MIR02 | MIR02-PI-005 | MIR02-P-005 | PKG | 107-HM | PRESSURE GAUGE | MIR02 | 148.2 | MIR02 PRESSURE | [19 empty] | 16 | bar: PKG
MM01 | MM01-FI-001 | MM01-F-001 | FLD | 107-PE | INDICATOR - FLOW | MM01 | 086.1 | MM01 N2 FLOW | -: 0.5 to 5 L/min; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  |  |  | KROHNE | DK32 |  |  |  |  | 01
MM01 | MM01-PI-001 | MM01-P-001 | FLD | 107-PE | INDICATOR - PRESSURE | MM01 | 086.1 | MM01 N2 PRESSURE | -: -40 to 60 mbar; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  |  |  | BOURDON SEDEME | MCX5 D30 N65 |  |  |  |  | 01
MM01 | MM01-TI-001 | MM01-T-001 | FLD | 107-PE | INDICATOR - TEMPERATURE | MM01 | 086.1 | MM01 N2 TEMPERATURE | -: 0 to 160 deg C; -: +/- 5%; REF: SHE; REQ: REQ; F: C |  |  |  |  | BOURDON SEDEME | TB1 |  |  |  |  | 01
MM02 | MM02-DIC-001 | MM02-D-001 | PKG | 107-PE | INDICATING CONTROL - MOTOR DRIVE | MM02 | 086.2 |  | REF: SHE | [10 empty] | 01
MM02 | MM02-LSLH-001 | MM02-L-001 | PKG | 107-PE | LEVEL SWITCH | MM02 SEAL POT | 086.2 | MM02 SEAL POT LEVEL | REF: SHE |  |  |  |  | TAV | F71-211-203 |  |  |  |  | 01
MM02 | MM02-PI-001 | MM02-P-001 | PKG | 107-PE | PRESSURE GAUGE | MM02 PRESSURE | 086.2 | MM02 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  |  |  | WIKA | 232.50.100 / 990.26 C276 |  |  |  |  | 01
MM02 | MM02-PI-002 | MM02-P-002 | PKG | 107-PE | PRESSURE GAUGE | MM02 SEAL POT | 086.2 | MM02 SEAL POT PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  |  |  | WIKA | [5 empty] | 01
MM02 | MM02-PSLH-03 | MM02-P-003 | PKG | 107-PE | PRESSURE SWITCH | MM02 SEAL POT | 086.2 | MM02 SEAL POT PRESSURE | REF: SHE; REQ: REQ; F: C |  |  |  |  | DELTA CONTROLS LTD | H28102P622H |  |  |  |  | 01
MM03 | MM03-CV-001 | MM03-C-001 | PKG | 107-PE | CONTROL VALVE | 9024743 | 086.3 | CW SUPPLY ISOLATION | [13 empty] | END ARMATUREA | MEMG2Z326265015/Ax |  |  |  |  | 60 | 11 | bar: PKG
MM03 |  | MM03-C-002 |  |  |  |  | 086.3 | [20 empty] | 59 | bar: PKG
MM03 |  | MM03-C-003 |  |  |  |  | 086.3 | [20 empty] | 59 | bar: PKG
MM03 | MM03-CV-004 | MM03-C-004 | PKG | SAN-902-007-002-000-00161 | PROPORTIONAL CONTROL VALVE | MM03 CONTROL PANEL | 086.3 | PURGE PANEL PRESSURE CONTROL | REF: SHE |  |  |  |  | Gonnheimer | SVP.300-A00 |  |  |  |  | 59 | 11
MM03 | MM03-FIT-001 | MM03-F-001 | PKG | SAN-902-007-002-000-00161 | FLOW INDICATING TRANSMITTER | 9024741 | 086.3 | PROCESS FLOW | -: 0 to 3600 kg/hr; -: +/- 0.1% |  |  |  |  | Endres and Hauser | PROMASS 300 |  |  |  |  | 60 | 11
MM03 |  | MM03-F-002 | [25 empty] | 60 | bar: PKG
MM03 | MM03-FT-003 | MM03-F-003 | PKG | SAN-902-007-002-000-00161 | FLOW TRANSMITTER | MM03 CONTROL PANEL | 086.3 | PURGE PANEL FLOW | REF: SHE |  |  |  |  | Gonnheimer | F850S Purge System |  |  |  |  | 59 | 11
MM03 | MM03-LSH-001 | MM03-L-001 | PKG | SAN-902-007-002-000-00161 | LEVEL SWITCH HIGH | MM03 CONTROL PANEL | 086.3 | MM03 CONTROL PANEL LEVEL SWITCH | [13 empty] | Pepper and Fuchs | [5 empty] | 60 | 11 | bar: PKG
MM03 | MM03-PI-001 | MM03-P-001 | PKG | SAN-902-007-002-000-00161 | PRESSURE GAUGE | 9024741 | 086.3 | MM03 OUTLET PRESSURE | -: 0 to 6 barg; -: +/- 1.0% |  |  |  |  | WIKA | 233.30 CW Hastelloy C22 Chemical Seal |  |  |  |  | 60 | 11
MM03 | MM03-PI-002 | MM03-P-002 | PKG | SAN-902-007-002-000-00161 | PRESSURE GAUGE | MM03 SEAL POT | 086.3 | MM03 SEAL POT PRESSURE | -: 0 to 25 bar; -: +/- 1.6% |  |  |  |  | ARMANO | RSCh 63-2 0-25bar |  |  |  |  | 59 | 11
MM03 | MM03-PSL-002 | MM03-P-002 | PKG | SAN-902-007-002-000-00161 | PRESSURE SWITCH - LOW | MM03 SEAL POT | 086.3 | MM03 SEAL POT PRESSURE | REF: SHE |  |  |  |  | ARMANO | RSCh 63-2 0-25bar |  |  |  |  | 59 | 11
MM03-P-003 | bar: PKG
MM03 | MM03-PC-004 | MM03-P-004 | PKG | SAN-902-007-002-000-00161 | PRESSURE CONTROLLER | MM03 CONTROL PANEL | 086.3 | PURGE PANEL PRESSURE CONTROL | REF: SHE |  |  |  |  | Gonnheimer | F850S Purge System |  |  |  |  | 59 | 11
MM03 | MM03-PT-004 | MM03-P-004 | PKG | SAN-902-007-002-000-00161 | PRESSURE TRANSMITTER | MM03 CONTROL PANEL | 086.3 | PURGE PANEL PRESSURE | -: 0.8 to 15mbarg; REF: SHE |  |  |  |  | Gonnheimer | F850S Purge System |  |  |  |  | 59 | 11
MM03 | MM03-PRV-005 | MM03-P-005 | PKG | SAN-902-007-002-000-00161 | PRESSURE REDUCING VALVE | MM03 CONTROL PANEL | 086.3 | MM03 CONTROL PANEL PURGE PRESSURE | -: 2 to 4 barg; REF: SHE | [10 empty] | 59
MM03 | MM03-DYC-001 | MM03-S-001 | PKG | SAN-902-007-002-000-00161 | DRIVE - START/STOP | MM03 | 086.3 | MM03 | [19 empty] | 59 | bar: PKG
MM03 | MM03-SC-001 | MM03-S-001 | PKG | SAN-902-007-002-000-00161 | SPEED CONTROLLER | MM03 | 086.3 | MM03 SPEED CONTROL | -: 0 to 6000rpm |  |  |  |  | Danfoss | VLT Automation Drive FC301/302 |  |  |  |  | 59 | 11
MM03 | MM03-SI-001 | MM03-S-001 | PKG | SAN-902-007-002-000-00161 | SPEED INDICATOR | MM03 | 086.3 | MM03 | -: 0 to 6000rpm |  |  |  |  | Danfoss | VLT Automation Drive FC301/302 |  |  |  |  | 59 | 11
MM03 | MM03-TE-001 | MM03-T-001 | PKG | SAN-902-007-002-000-00161 | TEMPERATURE ELEMENT | MM03 | 086.3 | MM03 SEAL TEMPERATURE | REF: SHE | [10 empty] | 59 | 11
MM03 | MM03-TSH-001 | MM03-T-001 | PKG | SAN-902-007-002-000-00161 | TEMPERATURE SWITCH - HIGH | MM03 | 086.3 | MM03 SEAL TEMPERATURE | -: 90 deg C rising; REF: SHE | [10 empty] | 59 | 11
MM03 | MM03-TT-001 | MM03-T-001 | PKG | SAN-902-007-002-000-00161 | TEMPERATURE TRANSMITTER | MM03 | 086.3 | MM03 SEAL TEMPERATURE | REF: SHE | [10 empty] | 59 | 11
MM03 | MM03-TSH-002 | MM03-T-002 | PKG | SAN-902-007-002-000-00161 | TEMPERATURE SWITCH - HIGH | MM03 | 086.3 | MM03 CONTROL PANEL TEMPERATURE | -: 35 deg C rising | [11 empty] | 11
MM04 | MM04-AT-001 | MM04-A-001 | PKG | SAN-902-007-002-000-00212 | ANALYSER - OXYGEN | MM04 | 086.4 | MM04 OXYGEN LEVEL | -: 0 - 25%; REF: SIL 2 |  |  |  |  | NTRON | OC25 | [5 empty] | v16.0
MM04 | MM04-AI-001 | MM04-A-001 | PKG | SAN-902-007-002-000-00212 | INDICATOR - ANALYSIS | MM04 | 086.4 | MM04 OXYGEN LEVEL | -: 0 - 25% |  |  |  |  | Beka | BA307E | [5 empty] | v16.0
MM04 | MM04-ASH-001 | MM04-A-001 | PKG | SAN-902-007-002-000-00212 | SWITCH - LEVEL - HIGH | MM04 | 086.4 | MM04 OXYGEN LEVEL HIGH INDICATOR | -: 5% O2; -: +/- 0.25%; REF: SIL 2 | [11 empty] | v16.0
MM04 | MM04-AISH-001 | MM04-A-001 | PLC | SAN-902-007-002-000-00212 | INDICATOR - LAMP | MM04 | 086.4 | MM04 OXYGEN LEVEL HIGH INDICATOR | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-CV-001 | MM04-C-001 | PKG | SAN-902-007-002-000-00212 | BALL VALVE - ON/OFF | MM04 | 086.4 | NITROGEN SUPPLY | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-CV-002 | MM04-C-002 | PKG | SAN-902-007-002-000-00212 | BALL VALVE - ON/OFF | MM04 | 086.4 | MM04 NITROGEN PURGE - HIGH FLOW | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-CV-003 | MM04-C-003 | PKG | SAN-902-007-002-000-00212 | BALL VALVE - ON/OFF | MM04 | 086.4 | MM04 NITROGEN PURGE - LOW FLOW | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-CV-004 | MM04-C-004 | PKG | SAN-902-007-002-000-00212 | SOLENOID VALVE | MM04 | 086.4 | MM04 PANEL AIR SUPPLY | [20 empty] | v17.0 | bar: PKG
MM04 |  | MM04-C-005 |  | SAN-902-007-002-000-00212 | bar: PKG
MM04 | MM04-CV-006 | MM04-C-006 | PKG | SAN-902-007-002-000-00212 | SOLENOID VALVE | MM04 | 086.4 | MM04 FILTER BACK PULSE | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-CV-007 | MM04-C-007 | PKG | SAN-902-007-002-000-00212 | DIAPHRAGM VALVE - ON/OFF | MM04 | 086.4 | MM04 FILTER BACK PULSE | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-CV-008 | MM04-C-008 | PKG | SAN-902-007-002-000-00212 | CONTROL VALVE | MM04 | 086.4 | MM04 PURGE PANEL PRESSURE | [13 empty] | P&F 6000 Series | 6000 Series | [5 empty] | v16.0 | bar: PKG
MM04 | MM04-FI-001 | MM04-F-001 | PKG | SAN-902-007-002-000-00212 | FLOW INDICATOR | MM04 | 086.4 | NITROGEN PURGE FLOW | [13 empty] | PLATON | HG | [5 empty] | v16.0 | bar: PKG
MM04 | MM04-FT-002 | MM04-F-002 | PKG | SAN-902-007-002-000-00212 | FLOW TRANSMITTER | MM04 | 086.4 | PURGE PANEL FLOW | [13 empty] | P&F 6000 Series | 6000 Series | [5 empty] | v16.0 | bar: PKG
MM04 | MM04-HS-001 | MM04-H-001 | PKG | SAN-902-007-002-000-00212 | HAND SWITCH | MM04 | 086.4 | MM04 START PUSH BUTTON | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-HS-002 | MM04-H-002 | PKG | SAN-902-007-002-000-00212 | HAND SWITCH | MM04 | 086.4 | MM04 STOP PUSH BUTTON | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-HS-003 | MM04-H-003 | PKG | SAN-902-007-002-000-00212 | HAND SWITCH | MM04 | 086.4 | MM04 INERTION MODE SELECTOR SWITCH | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-HS-004 | MM04-H-004 | PKG | SAN-902-007-002-000-00212 | HAND SWITCH | MM04 | 086.4 | MM04 FAULT RESET | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-HS-005 | MM04-H-005 | PKG | SAN-902-007-002-000-00212 | HAND SWITCH | MM04 | 086.4 | FILTER CLEAN - MANUAL START | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-HS-006 | MM04-H-006 | PKG | SAN-902-007-002-000-00212 | HAND SWITCH | MM04 | 086.4 | PROCESS STOP | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-HS-007 | MM04-H-007 | PKG | SAN-902-007-002-000-00212 | HAND SWITCH | MM04 | 086.4 | LAMP TEST | [20 empty] | v17.0 | bar: PKG
MM04 | MM04-PIT-001 | MM04-P-001 | PKG | SAN-902-007-002-000-00212 | PRESSURE TRANSMITTER WITH INDICATOR | MM04 | 086.4 | MM04 MILL PRESSURE | -: -1 to 4 barg; -: +/- 0.5%; REF: SIL 2 |  |  |  |  | Rosemount | 3051T | [5 empty] | v16.0
MM04 | MM04-PI-001 | MM04-P-001 | PKG | SAN-902-007-002-000-00212 | INDICATOR/ALARM - PRESSURE | MM04 | 086.4 | MM04 MILL PRESSURE | [13 empty] | Beka | BA307E | [5 empty] | v16.0 | bar: PKG
MM04 | MM04-PSH-001 | MM04-P-001 | PKG | SAN-902-007-002-000-00212 | SWITCH PRESSURE HIGH | MM04 | 086.4 | MM04 MILL PRESSURE | -: 0.4 barg rising; -: +/- 0.05 barg; REF: SIL 2 | [11 empty] | v16.0
MM04 | MM04-PC-002 | MM04-P-002 | PKG | SAN-902-007-002-000-00212 | PRESSURE CONTROLLER | MM04 CONTROL PANEL | 086.4 | PURGE PANEL PRESSURE CONTROL | [13 empty] | P&F 6000 Series | 6000 Series | [5 empty] | v16.0 | bar: PKG
MM04 | MM04-PRV-003 | MM04-P-003 | PKG | SAN-902-007-002-000-00212 | PRESSURE REDUCING VALVE | MM04 PURGE PANEL | 086.4 | PURGE PANEL PRESSURE | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-PSL-004 | MM04-P-004 | PKG | SAN-902-007-002-000-00212 | SWITCH - PRESSURE - LOW | MM04 PURGE PANEL | 086.4 | PURGE PANEL AIR PRESSURE LOW | -: 1.0 barg falling; -: +/- 0.05 barg | [11 empty] | v17.0
MM04 | MM04-PRV-005 | MM04-P-005 | PKG | SAN-902-007-002-000-00212 | PRESSURE REDUCING VALVE | MM04 PURGE PANEL | 086.4 | PURGE PANEL AIR PRESSURE | [20 empty] | v17.0 | bar: PKG
MM04 | MM04-PRV-006 | MM04-P-006 | PKG | SAN-902-007-002-000-00212 | PRESSURE REDUCING VALVE | MM04 PURGE PANEL | 086.4 | NITROGEN SWEEP PRESSURE | [20 empty] | v17.0 | bar: PKG
MM04 | MM04-PRV-007 | MM04-P-007 | PKG | SAN-902-007-002-000-00212 | PRESSURE REDUCING VALVE | MM04 PURGE PANEL | 086.4 | NITROGEN FILTER BACK PULSE PRESSURE | [20 empty] | v17.0 | bar: PKG
MM04 | MM04-PS-008 | MM04-P-008 | PKG | SAN-902-007-002-000-00212 | SWITCH - PRESSURE | MM04 PURGE PANEL | 086.4 | PURGE PANEL AIR PRESSURE | -: 5.0 barg rising; -: +/- 0.05 barg | [11 empty] | v17.0
MM04 | MM04-RO-001 | MM04-R-001 | PKG | SAN-902-007-002-000-00212 | RESTRICTION ORIFICE | MM04 | 086.4 | RESTRICT N2 FLOW TO MM04 | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-SIC-001 | MM04-S-001 | PKG | SAN-902-007-002-000-00212 | SPEED CONTROLLER | MM04 | 086.4 | MM04 SPEED CONTROL | [13 empty] | Control Techniques | Commander C300 | [5 empty] | v16.0 | bar: PKG
MM04 | MM04-SI-001 | MM04-S-001 | PKG | SAN-902-007-002-000-00212 | INDICATOR - SPEED | MM04 | 086.4 | MM04 SPEED INDICATION | [13 empty] | Beka | BA307E | [5 empty] | v16.0 | bar: PKG
MM04 | MM04-SC-001 | MM04-S-001 | PKG | SAN-902-007-002-000-00212 | SPEED CONTROLLER | MM04 | 086.4 | MM04 SPEED CONTROL | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-TT-001 | MM04-T-001 | PKG | SAN-902-007-002-000-00212 | TEMPERATURE TRANSMITTER | MM04 | 086.4 | MM04 SCREEN TEMPERATURE | -: -20-100°C; -: +/- 0.5%; REF: SIL 1 |  |  |  |  | ITS | PT100-3W-SA | [5 empty] | v16.0
MM04 | MM04-TI-001 | MM04-T-001 | PKG | SAN-902-007-002-000-00212 | INDICATOR - TEMPERATURE | MM04 | 086.4 | MM04 SCREEN TEMPERATURE | [13 empty] | Beka | BA307E | [5 empty] | v16.0 | bar: PKG
MM04 | MM04-TSH-001 | MM04-T-001 | PKG | SAN-902-007-002-000-00212 | SWITCH - TEMPERATURE - HIGH | MM04 | 086.4 | MM04 SCREEN TEMPERATURE | -: 55°C Rising; -: +/- 5°C; REF: SIL 1 | [11 empty] | v16.0
MM04 | MM04-TT-002 | MM04-T-002 | PKG | SAN-902-007-002-000-00212 | TEMPERATURE TRANSMITTER | MM04 | 086.4 | MM04 GEARBOX TEMPERATURE | -: -20-100°C; -: +/- 0.5%; REF: SIL 1 |  |  |  |  | ITS | PT100-3W-SA | [5 empty] | v16.0
MM04 | MM04-TI-002 | MM04-T-002 | PKG | SAN-902-007-002-000-00212 | INDICATOR - TEMPERATURE | MM04 | 086.4 | MM04 GEARBOX TEMPERATURE | [13 empty] | Beka | BA307E | [5 empty] | v16.0 | bar: PKG
MM04 | MM04-TSH-002 | MM04-T-002 | PKG | SAN-902-007-002-000-00212 | SWITCH - TEMPERATURE - HIGH | MM04 | 086.4 | MM04 GEARBOX TEMPERATURE | -: 60°C Rising; -: +/- 5°C; REF: SIL 1 | [11 empty] | v16.0
MM04 | MM04-TSAH-002 | MM04-T-002 | PKG | SAN-902-007-002-000-00212 | SWITCH - TEMPERATURE - HIGH | MM04 | 086.4 | MM04 SCREEN/GEARBOX TEMPERATURE TRIP | REF: SIL 1 | [11 empty] | v17.0
MM04 | MM04-TSH-003 | MM04-T-003 | PKG | SAN-902-007-002-000-00212 | SWITCH - TEMPERATURE - HIGH | MM04 | 086.4 | CONTROL PANEL SHUTDOWN STAT 1 | -: 55°C Rising; -: +/- 5°C | [11 empty] | v17.0
MM04 | MM04-TSH-004 | MM04-T-004 | PKG | SAN-902-007-002-000-00212 | SWITCH - TEMPERATURE - HIGH | MM04 | 086.4 | CONTROL PANEL SHUTDOWN STAT 2 | -: 35°C Rising; -: +/- 5°C | [11 empty] | v17.0
MM04 | MM04-YS-001 | MM04-Y-001 | PKG | SAN-902-007-002-000-00212 | INDICATOR LAMP | MM04 | 086.4 | MILL RUNNING | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-YS-002 | MM04-Y-002 | PKG | SAN-902-007-002-000-00212 | INDICATOR LAMP | MM04 | 086.4 | NITROGEN PURGING | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-YS-003 | MM04-Y-003 | PKG | SAN-902-007-002-000-00212 | INDICATOR LAMP | MM04 | 086.4 | NITROGEN MODE | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-YS-004 | MM04-Y-004 | PKG | SAN-902-007-002-000-00212 | INDICATOR LAMP | MM04 | 086.4 | COMMON FAULT | [20 empty] | v16.0 | bar: PKG
MM04 | MM04-ZS-003 | MM04-Z-003 | PKG | SAN-902-007-002-000-00212 | SAFETY SWITCH - STATUS | MM04 | 086.4 | MM04 MILL COVER POSITION SWITCH | REF: SIL 2 |  |  |  |  | Elobau | 671271MU0-5 | [5 empty] | v16.0
MNF01 | MNF01-BD-001 | MNF01-B-001 | PKG | 107-HK | RUPTURE DISC | MNF01 VENT |  | BURSTING DISC | -: 2.7 barg; -: +/- 5%; REQ: 12; F: F |  |  | 0 | [7 empty] | 01
MNF01 | MNF01-PI-001 | MNF01-P-001 | PKG | 107-HK | PRESSURE GAUGE - DIAPHRAGM | MNF01 VENT |  | PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
MNF02 | MNF02-BD-001 | MNF02-B-001 | PKG | 107-HK | RUPTURE DISC | MNF02 VENT |  | BURSTING DISC | -: 2.7 barg; -: +/- 5%; REQ: 12; F: F |  |  | 0 | [7 empty] | 01
MNF02 | MNF02-PI-001 | MNF02-P-001 | PKG | 107-HK | PRESSURE GAUGE - DIAPHRAGM | MNF02 VENT |  | PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 |  | Wika | 232.50.100 | KP0006/P2 |  |  |  | 29
MNF03 | MNF03-BD-001 | MNF03-B-001 | PKG | 107-HK | RUPTURE DISC | MNF03 VENT |  | BURSTING DISC | -: 2.7 barg; -: +/- 5%; REQ: 12; F: F |  |  | 0 | [7 empty] | 01
MNF03 | MNF03-PI-001 | MNF03-P-001 | PKG | 107-HK | PRESSURE GAUGE - DIAPHRAGM | MNF03 VENT |  | PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 |  | Wika | 232.50.100 | KP0006/P2 |  |  |  | 29
MNF04 | MNF04-BD-001 | MNF04-B-001 | PKG | 107-HK | RUPTURE DISC | MNF04 VENT |  | BURSTING DISC | -: 2.7 barg; -: +/- 5%; REQ: 12; F: F |  |  | 0 | [5 empty] | REMOVED FROM SERVICE eCC15028 |  | 22
MNF04 | MNF04-PI-001 | MNF04-P-001 | PKG | 107-HK | PRESSURE GAUGE - DIAPHRAGM | MNF04 VENT |  | PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | Bourdon-Sedeme | MEX 5 D30 B76 | KP0006/P2 |  | REMOVED FROM SERVICE eCC15028 |  | 22
MNF05 | MNF05-PI-001 | MNF05-P-001 | PKG | 107-HK | PRESSURE GAUGE - DIAPHRAGM | MNF05 VENT | 089.5 | PRESSURE | REF: REF; REQ: By request; F: C |  |  |  |  | Wika | 232.50.100 | KP0006/P2 |  |  |  | 29
MNF05 | MNF05-PSV-001 | MNF05-P-001 | PKG | 107-HK | RELIEF VALVE | MNF05 VENT | 089.5 | PRESSURE | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  |  |  | Nabic | Fig 540 |  |  |  |  | 01
MNF06 | MNF06-BD-001 | MNF06-B-001 | PKG | 107-HR | RUPTURE DISC | MNF06 VENT | 089.6 | BURSTING DISC | -: 2.7 barg; -: +/- 5%; REQ: 24; F: F |  |  |  |  | Elfab | SC25NH39EA |  |  |  |  | 01
MNF06 | MNF06-PI-001 | MNF06-P-001 | PKG | 107-HR | PRESSURE GAUGE - DIAPHRAGM | MNF06 VENT | 089.6 | PRESSURE | REF: REF; REQ: By request; F: C |  |  |  |  | Wika | 232.50.100 / 990.26 C276 |  |  |  |  | 01
MPF01 | MPF01-BD-001 | MPF01-B-001 | PKG | 107-HL | RUPTURE DISC | DELETED |  | DELETED | -: 2.7 barg; -: +/- 5%; REQ: 12; F: F |  |  | 0 | [5 empty] | DELETED |  | 01
MPF01 | MPF01-PI-001 | MPF01-P-001 | PKG | 107-HL | PRESSURE GAUGE - DIAPHRAGM | MPF01 | 088.1 | MPF01 PRESSURE | REQ: By request; F: C |  |  | 0 |  | Wika | 232.50 + 990.10 |  |  |  |  | 01
MPF01 | MPF01-PSV-001 | MPF01-P-001 | PKG | 107-HL | RELIEF VALVE | MPF01 | 088.1 | MPF01 PRESSURE | -: 3.6 barg; -: +/- 10%; REQ: 24; F: C |  |  |  |  | Nabic | Fig 500FN |  |  |  |  | 01
MPF02 | MPF02-BD-001 | MPF02-B-001 | PKG | 107-HL | RUPTURE DISC | DELETED | 088.2 | DELETED | -: 2.7 barg; -: +/- 5%; REQ: 12; F: F |  |  | 0 | [5 empty] | DELETED |  | 01
MPF02 | MPF02-PI-001 | MPF02-P-001 | PKG | 107-HL | PRESSURE GAUGE - DIAPHRAGM | MPF02 | 088.2 | MPF02 PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 |  | Eurofiltec | [5 empty] | 01
MPF02 | MPF02-PSV-001 | MPF02-P-001 | PKG | 107-HL | RELIEF VALVE | MPF02 | 088.2 | MPF02 PRESSURE | -: 3.6 barg; -: +/- 10%; REF: GxP; REQ: 24; F: C |  |  |  |  | Nabic | Fig 500FN |  |  |  |  | 01
MPH01 | MPH01-PSV-001 | MPH01-P-001 | PKG | 107-HR | RELIEF VALVE | MPH01-P2 | 176.1 | MPH01-P2 RELIEF | -: 3.0 barg; F: F | [11 empty] | 15
MPH02 | MPH02-AIT-001 | MPH02-A-001 | PKG | 107-HR | TEMPERATURE PROBE | MPH02 | 176.0 | MPH02 TEMPERATURE | PKG: L15245; -: pH 0-14 (-5-135oC); -: +/- 0.25 pH units; REF: GxP; REQ: By request |  |  |  |  | Mettler Toledo | InPRo 4800SG/120/Pt1000 |  |  |  |  | 15
MPH03 | MPH02-DIC-001 | MPH02-D-001 | PKG | 107-HR | DIGITAL INDICATOR CONTROLLER | MPH02 | 176.0 |  | PKG: L15248; REF: GxP; REQ: By request | [10 empty] | 15
MPH02 | MPH02-DIC-002 | MPH02-D-002 | PKG | 107-HR | DIGITAL INDICATOR CONTROLLER | MPH02 | 176.0 |  | PKG: L15249; REF: GxP; REQ: By request | [10 empty] | 15
MPH02 | MPH02-FIT-001 | MPH02-F-001 | PKG | 107-HR | FLOW METER | MPH02 | 176.0 | MPH02 FLOW | PKG: L15246; -: 0-2180kg/h; -: 0.1%; REF: GxP; REQ: By request |  |  |  |  | EMERSON | CMF025 |  |  |  |  | 15
MPH02 | MPH02-FIT-002 | MPH02-F-002 | PKG | 107-HR | FLOW METER | MPH02 | 176.0 | MPH02 FLOW | PKG: L15247; -: 0-2180kg/h; -: 0.1%; REF: GxP; REQ: By request |  |  |  |  | EMERSON | CMF025 |  |  |  |  | 15
MPH02 | MPH02-PS-001 | MPH02-P-001 | PKG | 107-HR | PRESSURE SWITCH | MPH02 | 176.0 | MPH02 PRESSURE | -: -1 to 10 barg; -: +/- 1%; REF: SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 3051T |  |  |  |  | 18
MPH02 | MPH02-PT-001 | MPH02-P-001 | PKG | 107-HR | PRESSURE TRANSMITTER | MPH02 | 176.0 | MPH02 PRESSURE | PKG: L15250; -: -1 to 10 barg; -: +/- 1%; REF: SHE; REQ: 12
MPH02 | MPH02-PS-002 | MPH02-P-002 | PKG | 107-HR | PRESSURE SWITCH | MPH02 | 176.0 | MPH02 PRESSURE | -: -1 to 10 barg; -: +/- 1%; REF: SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 3051T |  |  |  |  | 18
MPH02 | MPH02-PT-002 | MPH02-P-002 | PKG | 107-HR | PRESSURE TRANSMITTER | MPH02 | 176.0 | MPH02 PRESSURE | PKG: L15251; -: -1 to 10 barg; -: +/- 1%; REF: SHE; REQ: 12
MS01 | MS01-PI-001 | MS01-P-001 | PKG | 107-BA | PRESSURE GAUGE - DIAPHRAGM | MS01 | 092.0 | MS01 PRESSURE | -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
MTP03 | MTP03-PRV-001 | MTP03-P-001 | PKG | 107-BP | CONTROL VALVE SELF ACTUATING | MTP03 | 089.1 | AIR TO MTP03 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
MTP04 | MTP04-PRV-001 | MTP04-P-001 | PKG | 107-CP | CONTROL VALVE SELF ACTUATING | MTP04 | 089.1 | AIR TO MTP04 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
MTP05 | MTP05-PRV-001 | MTP05-P-001 | PKG | 107-DP | CONTROL VALVE SELF ACTUATING | MTP05 | 089.1 | AIR TO MTP05 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
MTP06 | MTP06-PRV-001 | MTP06-P-001 | PKG | 107-EP | CONTROL VALVE SELF ACTUATING | MTP06 | 089.1 | AIR TO MTP06 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
MW | MW-FQI-002 | MW-F-002 | CPR | 108-EA | INDICATOR - FLOW | BEMS SYSTEM |  | MAINS WATER FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
MW | MW-FT-002 | MW-F-002 | FLD | 108-EA | TRANSMITTER - FLOW | 80-MW-CS1B-E-902804 | 044.1 | MAINS WATER FLOW |  | 12 - 833 l/min | +/- 5% | REF | REQ | C |  | N.I.S |  |  |  | 36 |  | MEINECKE | MEIN50WPD | KF0018 |  | INPUT TO BEMS SYSTEM | DI | 01
MIR | MIR-CV-001A-P01 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 3x2 Intergrated Probe | Intergrated in valve | 148.3 | N/A | PKG: N/A; -: N/A |  |  |  |  | METTLER TOLEDO | AgX DiComp |  |  |  |  | 17
MIR | MIR-CV-001A-TE-001 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 3x2 Temp Element | Intergrated in valve | 148.3 | N/A | PKG: L15596; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MIR | MIR-CV-001A-TE-002 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 3x2 Temp Element | Intergrated in valve | 148.3 | N/A | PKG: L15596; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MIR | MIR-CV-001A-TT-001 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 3x2 Temp Transmitter | Intergrated in valve | 148.3 | N/A | PKG: L15596; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 17
MIR | MIR-CV-001A-TT-002 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 3x2 Temp Transmitter | Intergrated in valve | 148.3 | N/A | PKG: L15596; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MIR | MIR-CV-001B-P01 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Intergrated Probe | Intergrated in valve | 148.4 | N/A | PKG: N/A; -: N/A |  |  |  |  | METTLER TOLEDO | AgX DiComp |  |  |  |  | 17
MIR | MIR-CV-001B-TE-001 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Temp Element | Intergrated in valve | 148.4 | N/A | PKG: L15598; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MIR | MIR-CV-001B-TE-002 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Temp Element | Intergrated in valve | 148.4 | N/A | PKG: L15598; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MIR | MIR-CV-001B-TT-001 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Temp Transmitter | Intergrated in valve | 148.4 | N/A | PKG: L15598; -: -30/+170oC; -: +/-1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 17
MIR | MIR-CV-001B-TT-002 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Temp Transmitter | Intergrated in valve | 148.4 | N/A | PKG: L15598; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MIR | MIR-CV-001C-P01 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Intergrated Probe | Intergrated in valve | 148.6 | N/A | PKG: N/A |  |  |  |  | METTLER TOLEDO | AgX DiComp |  |  |  |  | 25
MIR | MIR-CV-001C-TE-001 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Temp Element | Intergrated in valve | 148.6 | N/A | PKG: L15751; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MIR | MIR-CV-001C-TE-002 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Temp Element | Intergrated in valve | 148.6 | N/A | PKG: L15751; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MIR | MIR-CV-001C-TT-001 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Temp Transmitter | Intergrated in valve | 148.6 | N/A | PKG: L15751; -: -30/+170oC; -: +/- 1degC; REF: GxP/SHE; REQ: 12 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MIR | MIR-CV-001C-TT-002 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Temp Transmitter | Intergrated in valve | 148.6 | N/A | PKG: L15751; -: -30 to 170degC; -: +/- 1degC; REF: GxP/SHE; REQ: 12
MIR | MIR-CV-001-TT-002 | N/A | N/A | N/A | Mid IR Units Reactor Base Valve 4x3 Temp Transmitter | Intergrated in valve | 148.6 | N/A | PKG: TBC; -: -30/+170oC; REQ: 24 |  |  |  |  | ROSEMOUNT | 644HAI1Q4 |  |  |  |  | 25
MS01 |  | MS01-C-001 | [26 empty] | v20.0 | bar: PKG
MS01 |  | MS01-C-002 | [26 empty] | v20.0 | bar: PKG
MS01 |  | MS01-C-003 | [26 empty] | v20.0 | bar: PKG
MS01 | MS01-CV-004 | MS01-C-004 | PKG | SAN-902-007-002-000-00217 | SOLENOID VALVE | MS01 | 086.9 | MS01 PANEL AIR SUPPLY | [20 empty] | v20.0 | bar: PKG
MS01 |  | MS01-C-005 |  | SAN-902-007-002-000-00217 | [24 empty] | v20.0 | bar: PKG
MS01 | MS01-CV-006 | MS01-C-006 | PKG | SAN-902-007-002-000-00217 | SOLENOID VALVE | MS01 | 086.9 | MS01 FILTER BACK PULSE | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-CV-007 | MS01-C-007 | PKG | SAN-902-007-002-000-00217 | DIAPHRAGM VALVE - ON/OFF | MS01 | 086.9 | MS01 FILTER BACK PULSE | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-CV-008 | MS01-C-008 | PKG | SAN-902-007-002-000-00217 | CONTROL VALVE | MS01 | 086.9 | MS01 PURGE PANEL PRESSURE | [13 empty] | P&F 6000 Series | 6000 Series | [5 empty] | v20.0 | bar: PKG
MS01 | MS01-HS-001 | MS01-H-001 | PKG | SAN-902-007-002-000-00217 | HAND SWITCH | MS01 | 086.9 | MS01 START PUSH BUTTON | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-HS-002 | MS01-H-002 | PKG | SAN-902-007-002-000-00217 | HAND SWITCH | MS01 | 086.9 | MS01 STOP PUSH BUTTON | [20 empty] | v20.0 | bar: PKG
MS01 |  | MS01-H-003 |  | SAN-902-007-002-000-00217 | [24 empty] | v20.0 | bar: PKG
MS01 | MS01-HS-004 | MS01-H-004 | PKG | SAN-902-007-002-000-00217 | HAND SWITCH | MS01 | 086.9 | MS01 FAULT RESET | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-HS-005 | MS01-H-005 | PKG | SAN-902-007-002-000-00217 | HAND SWITCH | MS01 | 086.9 | FILTER CLEAN - MANUAL START | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-HS-006 | MS01-H-006 | PKG | SAN-902-007-002-000-00217 | HAND SWITCH | MS01 | 086.9 | PROCESS STOP | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-HS-007 | MS01-H-007 | PKG | SAN-902-007-002-000-00217 | HAND SWITCH | MS01 | 086.9 | LAMP TEST | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-PIT-001 | MS01-P-001 | PKG | SAN-902-007-002-000-00217 | PRESSURE TRANSMITTER WITH INDICATOR | MS01 | 086.9 | MS01 MILL PRESSURE | -: -1 to 4 barg; -: +/- 0.5%; REF: SIL 2 |  |  |  |  | Rosemount | 3051T | [5 empty] | v20.0
MS01 | MS01-PI-001 | MS01-P-001 | PKG | SAN-902-007-002-000-00217 | INDICATOR/ALARM - PRESSURE | MS01 | 086.9 | MS01 MILL PRESSURE | [13 empty] | Beka | BA307E | [5 empty] | v20.0 | bar: PKG
MS01 | MS01-PSH-001 | MS01-P-001 | PKG | SAN-902-007-002-000-00217 | SWITCH PRESSURE HIGH | MS01 | 086.9 | MS01 MILL PRESSURE | -: 0.4 barg rising; -: +/- 0.05 barg; REF: SIL 2 | [11 empty] | v20.0
MS01 | MS01-PC-002 | MS01-P-002 | PKG | SAN-902-007-002-000-00217 | PRESSURE CONTROLLER | MS01 CONTROL PANEL | 086.9 | PURGE PANEL PRESSURE CONTROL | [13 empty] | P&F 6000 Series | 6000 Series | [5 empty] | v20.0 | bar: PKG
MS01 | MS01-PRV-003 | MS01-P-003 | PKG | SAN-902-007-002-000-00217 | PRESSURE REDUCING VALVE | MS01 PURGE PANEL | 086.9 | PURGE PANEL PRESSURE | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-PSL-004 | MS01-P-004 | PKG | SAN-902-007-002-000-00217 | SWITCH - PRESSURE - LOW | MS01 PURGE PANEL | 086.9 | PURGE PANEL AIR PRESSURE LOW | -: 1.0 barg falling; -: +/- 0.05 barg | [11 empty] | v20.0
MS01 | MS01-PRV-005 | MS01-P-005 | PKG | SAN-902-007-002-000-00217 | PRESSURE REDUCING VALVE | MS01 PURGE PANEL | 086.9 | PURGE PANEL AIR PRESSURE | [20 empty] | v20.0 | bar: PKG
MS01 |  | MS01-P-006 |  | SAN-902-007-002-000-00217 | [24 empty] | v20.0 | bar: PKG
MS01 | MS01-PRV-007 | MS01-P-007 | PKG | SAN-902-007-002-000-00217 | PRESSURE REDUCING VALVE | MS01 PURGE PANEL | 086.9 | FILTER BACK PULSE PRESSURE | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-PS-008 | MS01-P-008 | PKG | SAN-902-007-002-000-00217 | SWITCH - PRESSURE | MS01 PURGE PANEL | 086.9 | PURGE PANEL AIR PRESSURE | -: 5.0 barg rising; -: +/- 0.05 barg | [11 empty] | v20.0
MS01 | MS01-SIC-001 | MS01-S-001 | PKG | SAN-902-007-002-000-00217 | SPEED CONTROLLER | MS01 | 086.9 | MS01 SPEED CONTROL | [13 empty] | Control Techniques | Commander C300 | [5 empty] | v20.0 | bar: PKG
MS01 | MS01-SI-001 | MS01-S-001 | PKG | SAN-902-007-002-000-00217 | INDICATOR - SPEED | MS01 | 086.9 | MS01 SPEED INDICATION | [13 empty] | Beka | BA307E | [5 empty] | v20.0 | bar: PKG
MS01 | MS01-SC-001 | MS01-S-001 | PKG | SAN-902-007-002-000-00217 | SPEED CONTROLLER | MS01 | 086.9 | MS01 SPEED CONTROL | [20 empty] | v20.0 | bar: PKG
MS01 |  | MS01-T-001 | PKG | SAN-902-007-002-000-00217 | [24 empty] | v20.0 | bar: PKG
MS01 | MS01-TT-002 | MS01-T-002 | PKG | SAN-902-007-002-000-00217 | TEMPERATURE TRANSMITTER | MS01 | 086.9 | MS01 GEARBOX TEMPERATURE | -: -20-100°C; -: +/- 0.5%; REF: SIL 1 |  |  |  |  | ITS | PT100-3W-SA | [5 empty] | v20.0
MS01 | MS01-TI-002 | MS01-T-002 | PKG | SAN-902-007-002-000-00217 | INDICATOR - TEMPERATURE | MS01 | 086.9 | MS01 GEARBOX TEMPERATURE | [13 empty] | Beka | BA307E | [5 empty] | v20.0 | bar: PKG
MS01 | MS01-TSH-002 | MS01-T-002 | PKG | SAN-902-007-002-000-00217 | SWITCH - TEMPERATURE - HIGH | MS01 | 086.9 | MS01 GEARBOX TEMPERATURE | -: 60°C Rising; -: +/- 5°C; REF: SIL 1 | [11 empty] | v20.0
MS01 | MS01-TSAH-002 | MS01-T-002 | PKG | SAN-902-007-002-000-00217 | SWITCH - TEMPERATURE - HIGH | MS01 | 086.9 | MS01 SCREEN/GEARBOX TEMPERATURE TRIP | REF: SIL 1 | [11 empty] | v20.0
MS01 | MS01-TSH-003 | MS01-T-003 | PKG | SAN-902-007-002-000-00217 | SWITCH - TEMPERATURE - HIGH | MS01 | 086.9 | CONTROL PANEL SHUTDOWN STAT 1 | -: 55°C Rising; -: +/- 5°C | [11 empty] | v20.0
MS01 | MS01-TSH-004 | MS01-T-004 | PKG | SAN-902-007-002-000-00217 | SWITCH - TEMPERATURE - HIGH | MS01 | 086.9 | CONTROL PANEL SHUTDOWN STAT 2 | -: 35°C Rising; -: +/- 5°C | [11 empty] | v20.0
MS01 | MS01-YS-001 | MS01-Y-001 | PKG | SAN-902-007-002-000-00217 | INDICATOR LAMP | MS01 | 086.9 | MILL RUNNING | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-YS-002 | MS01-Y-002 | PKG | SAN-902-007-002-000-00217 | INDICATOR LAMP | MS01 | 086.9 | NITROGEN PURGING | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-YS-003 | MS01-Y-003 | PKG | SAN-902-007-002-000-00217 | INDICATOR LAMP | MS01 | 086.9 | NITROGEN MODE | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-YS-004 | MS01-Y-004 | PKG | SAN-902-007-002-000-00217 | INDICATOR LAMP | MS01 | 086.9 | COMMON FAULT | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-YS-005 | MS01-Y-005 | PKG | SAN-902-007-002-000-00217 | INDICATOR LAMP | MS01 | 086.9 | POWER | [20 empty] | v20.0 | bar: PKG
MS01 | MS01-ZS-003 | MS01-Z-003 | PKG | SAN-902-007-002-000-00217 | SAFETY SWITCH - STATUS | MS01 | 086.9 | MS01 MILL COVER POSITION SWITCH | REF: SIL 2 |  |  |  |  | Elobau | 671271MU0-5 | [5 empty] | v20.0
N2NTH | N2NTH-PRV-001 | N2NTH-P-001 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028761 | 043.2 | FG1 N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PRV-002 | N2NTH-P-002 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028884 | 043.2 | FG1 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PRV-003 | N2NTH-P-003 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028764 | 043.2 | FG1 N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PRV-004 | N2NTH-P-004 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028766 | 043.4 | FG1 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PRV-005 | N2NTH-P-005 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028768 | 043.2 | C1 N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PRV-006 | N2NTH-P-006 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028770 | 043.4 | C1 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PRV-007 | N2NTH-P-007 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028772 | 043.2 | C1 N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PRV-008 | N2NTH-P-008 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028774 | 043.4 | C1 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PSV-009 | N2NTH-P-009 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028761 | 043.2 | PRV-001 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511E-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PSV-010 | N2NTH-P-010 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028884 | 043.2 | PRV-002 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511F-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PSV-011 | N2NTH-P-011 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028764 | 043.2 | PRV-003 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511E-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PSV-012 | N2NTH-P-012 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028766 | 043.4 | PRV-004 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511F-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PSV-013 | N2NTH-P-013 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028768 | 043.2 | PRV-005 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511E-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PSV-014 | N2NTH-P-014 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028770 | 043.4 | PRV-006 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511F-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PSV-015 | N2NTH-P-015 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028772 | 043.2 | PRV-007 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511E-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PSV-016 | N2NTH-P-016 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028774 | 043.4 | PRV-008 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511F-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PRV-017 | N2NTH-P-017 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028806 | 043.4 | TD01 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PSV-018 | N2NTH-P-018 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028765 | 043.4 | PRV-017 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511D-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PRV-019 | N2NTH-P-019 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 40-N-SS1U-0-9028750 | 043.2 | PIPE RACK UTILITIES N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PSV-020 | N2NTH-P-020 | FLD | 108-DB | PRESSURE RELIEF VALVE | 40-N-SS1U-0-9028750 | 043.2 | PRV-019 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511D-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PRV-021 | N2NTH-P-021 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 50-N-SS1U-0-9028772 | 043.4 | FD02 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PSV-022 | N2NTH-P-022 | FLD | 108-DB | PRESSURE RELIEF VALVE | 50-N-SS1U-0-9028838 | 043.4 | PRV-021 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511D-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PRV-023 | N2NTH-P-023 | FLD | 108-DB | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028784 | 043.4 | DVP03 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2NTH | N2NTH-PSV-024 | N2NTH-P-024 | FLD | 108-DB | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028784 | 043.4 | PRV-023 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511D-S-N000 | KS0001 |  |  |  | 01
N2NTH | N2NTH-PRV-025 | N2NTH-P-025 | FLD | 108-DB | PRESSURE REDUCING VALVE | 25-N-SS1U-O-9028890 | 043.4 | TD02 PURGING NITROGEN | -: 35 mbarg; REF: REF; REQ: REQ; F: C; Ref: Ref |  |  |  |  | ESME | R1440/40 | KV0006/P |  |  |  | 01
N2NTH | N2NTH-PSV-026 | N2NTH-P-026 | FLD | 108-DB | PRESSURE SAFETY VALVE | 25-N-SS1U-O-9028890 | 043.4 | TD02 PURGING NITROGEN | -: 1 barg; REF: N/A; REQ: -; F: -; Ref: - |  |  |  |  | BROADY | 2511D | KS0001/P |  |  |  | 01
N2NTH | N2NTH-PRV-029 | N2NTH-P-029 | FLD | 108-DB | PRESSURE REDUCING VALVE | 25-N-SS1U-O-9028906 | 043 | CARBON DRUM PURGING NITROGEN | -: 300 mbarg; REF: REF; REQ: REQ; F: C; Ref: Ref |  |  |  |  | ESME | R1440/40 | KV0006/P2 |  |  |  | 23
N2NTH | N2NTH-PSV-030 | N2NTH-P-030 | FLD | 108-DB | PRESSURE SAFETY VALVE | 25-N-SS1U-O-9028906 | 043 | CARBON DRUM PURGING NITROGEN | -: 400 mbarg; REF: N/A; REQ: -; F: -; Ref: - |  |  |  |  | DONKIN | 226 VR | KS0001/P3 |  |  |  | 23
N2STH | N2STH-PRV-001 | N2STH-P-001 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028600 | 043.3 | GP1 N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2STH | N2STH-PRV-002 | N2STH-P-002 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028602 | 043.4 | GP1 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2STH | N2STH-PRV-003 | N2STH-P-003 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028604 | 043.3 | GP1 N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2STH | N2STH-PRV-004 | N2STH-P-004 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028606 | 043.4 | GP1 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2STH | N2STH-PRV-005 | N2STH-P-005 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028608 | 043.3 | GP2 N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2STH | N2STH-PRV-006 | N2STH-P-006 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028610 | 043.4 | GP2 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2STH | N2STH-PRV-007 | N2STH-P-007 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028612 | 043.3 | GP2 N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2STH | N2STH-PRV-008 | N2STH-P-008 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028614 | 043.4 | GP2 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2STH | N2STH-PSV-009 | N2STH-P-009 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028600 | 043.3 | PRV-001 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511E-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PSV-010 | N2STH-P-010 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028602 | 043.4 | PRV-002 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511F-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PSV-011 | N2STH-P-011 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028604 | 043.3 | PRV-003 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511E-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PSV-012 | N2STH-P-012 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028606 | 043.4 | PRV-004 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511F-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PSV-013 | N2STH-P-013 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028608 | 043.3 | PRV-005 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511E-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PSV-014 | N2STH-P-014 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028610 | 043.4 | PRV-006 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511F-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PSV-015 | N2STH-P-015 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028612 | 043.3 | PRV-007 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511E-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PSV-016 | N2STH-P-016 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028614 | 043.4 | PRV-008 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511F-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PRV-017 | N2STH-P-017 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028638 | 043.4 | TP07 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2STH | N2STH-PSV-018 | N2STH-P-018 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028638 | 043.4 | PRV-017 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511D-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PRV-019 | N2STH-P-019 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028601 | 043.4 | PD01/DVP02 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2STH | N2STH-PSV-020 | N2STH-P-020 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028601 | 043.4 | PRV-018 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511D-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PRV-021 | N2STH-P-021 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 50-N-SS1U-0-9028612 | 043.4 | FD03/DVP04 N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2STH | N2STH-PSV-022 | N2STH-P-022 | FLD | 108-DA | PRESSURE RELIEF VALVE | 50-N-SS1U-0-9028706 | 043.4 | PRV-021 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511E-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PRV-025 | N2STH-P-025 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028724 | 043.3 | HYDROG N2 SUPPLY | -: set @ 2.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
N2STH | N2STH-PSV-026 | N2STH-P-026 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028724 | 043.3 | PRV-025 RELIEF | -: 2.7 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511D-S-N000 | KS0001 |  |  |  | 01
N2STH | N2STH-PRV-027 | N2STH-P-027 | FLD | 108-DA | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028721 | 043.4 | HYDROG N2 SUPPLY | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440 | KV0006 |  |  |  | 01
N2STH | N2STH-PSV-028 | N2STH-P-028 | FLD | 108-DA | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028721 | 043.4 | PRV-027 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511D-S-N000 | KS0001 |  |  |  | 01
NS01 | NS01-BD-001 | NS01-B-001 | PKG | 107-QC | RUPTURE DISC | NS01 | 043.1 | BURSTING DISC | -: 20 barg; -: -; REQ: 12; F: F; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-BD-002 | NS01-B-002 | PKG | 107-QC | RUPTURE DISC | NS01 | 043.1 | BURSTING DISC | -: 20 barg; -: -; REQ: 12; F: F; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-FI-001 | NS01-F-001 | PCS | 107-QC | INDICATOR - FLOW |  |  | NITROGEN FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
NS01 | NS01-FT-001 | NS01-F-001 | PKG | 107-QC | TRANSMITTER - FLOW | NS01 | 043.1 | NITROGEN FLOW | 8709 | 25-600 Nm3/hr | +/- 2% | REF | REQ | C | SER | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | 77FS25-GA011C03 | KF0008 | TI702-SP-5111 |  |  | 47
NS01 | NS01-LI-001 | NS01-L-001 | PCS | 107-QC | INDICATOR - LEVEL |  |  | LIQUID NITROGEN LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
NS01 | NS01-LIT-001 | NS01-L-001 | PKG | 107-QC | TRANSMITTER - LEVEL | NS01 | 043.1 | LIQUID NITROGEN LEVEL | 8710 | 0-9500 litres | +/- 2% | REF | REQ | C | SER | I.S | AI |  |  | 11 | UTIL | WIKA | 712.15.160 + 892.44 |  | TI702-SP-5173 |  |  | 01
NS01 | NS01-PI-001 | NS01-P-001 | PCS | 107-QC | INDICATOR - PRESSURE |  |  | NITROGEN PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
NS01 | NS01-PIT-001 | NS01-P-001 | FLD | 107-QC | TRANSMITTER - PRESSURE | 40-N-SS1U-0-9027980 | 043.2 | NITROGEN PRESSURE | 8110 | 0 to 10 barg | +/- 2% | SHE | REQ | C |  | I.S | AI |  |  | 11 | UTIL | FOXBORO | 141GP (Note 2) | KP0001 | TI702-SP-5006 |  |  | 01
NS01 | NS01-PSV-002 | NS01-P-002 | PKG | 107-QC | PRESSURE RELIEF VALVE | NS01 | 043.1 | LIQ N2 RELIEF | -: set @ 7 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-PSV-003 | NS01-P-003 | PKG | 107-QC | PRESSURE RELIEF VALVE | NS01 | 043.1 | LIQ N2 RELIEF | -: set @ 16.9 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-PSV-004 | NS01-P-004 | PKG | 107-QC | PRESSURE RELIEF VALVE | NS01 | 043.1 | LIQ N2 RELIEF | -: set @ 16.9 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-PSV-005 | NS01-P-005 | PKG | 107-QC | PRESSURE RELIEF VALVE | NS01 | 043.1 | LIQ N2 RELIEF | -: set @ 23.5 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-PSV-006 | NS01-P-006 | PKG | 107-QC | PRESSURE RELIEF VALVE | NS01 | 043.1 | LIQ N2 RELIEF | -: set @ 23.5 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-PRV-007 | NS01-P-007 | PKG | 107-QC | CONTROL VALVE SELF ACTUATING | NS01 | 043.1 | LIQ N2 DIVERTER |  | set @ 10.5 barg | +/- 5% | REF | REQ | C | SER |  |  |  |  | 0 | [7 empty] | 01
NS01 | NS01-PSV-008 | NS01-P-008 | PKG | 107-QC | PRESSURE RELIEF VALVE | NS01 | 043.1 | DIVERTER RELIEF | -: set @ 23.5 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-PSV-009 | NS01-P-009 | PKG | 107-QC | PRESSURE RELIEF VALVE | NS01 | 043.1 | SUPPLY TO LETDOWN RELIEF | -: set @ 19 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-PI-010 | NS01-P-010 | PKG | 107-QC | PRESSURE GAUGE | NS01 | 043.1 | 6 BARG N2 SUPPLY |  | 0 to 100 barg | +/- 5% | REF | REQ | C | SER |  |  |  |  | 0 | [7 empty] | 01
NS01 | NS01-PRV-011 | NS01-P-011 | PKG | 107-QC | CONTROL VALVE SELF ACTUATING | NS01 | 043.1 | 6 BARG N2 SUPPLY |  | set @ 6 barg | +/- 5% | REF | REQ | C | SER |  |  |  |  | 0 | [7 empty] | 01
NS01 | NS01-PRV-012 | NS01-P-012 | PKG | 107-QC | CONTROL VALVE SELF ACTUATING | NS01 | 043.1 | 6.5 BARG N2 SUPPLY |  | set @ 6.2 barg | +/- 5% | REF | REQ | C | SER |  |  |  |  | 0 | [7 empty] | 01
NS01 | NS01-PI-013 | NS01-P-013 | PKG | 107-QC | PRESSURE GAUGE | NS01 | 043.1 | 6.5 BARG N2 SUPPLY |  | 0 to 100 barg | +/- 5% | REF | REQ | C | SER |  |  |  |  | 0 | [7 empty] | 01
NS01 | NS01-PSV-014 | NS01-P-014 | PKG | 107-QC | PRESSURE RELIEF VALVE | NS01 | 043.1 | N2 SUPPLY RELIEF | -: set @ 7 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
NS01 | NS01-PSV-015 | NS01-P-015 | PKG | 107-QC | PRESSURE RELIEF VALVE | LIQ N2 SUPPLY HEADER | 043.5 | LIQ N2 SUPPLY RELIEF | -: set @ 16.9 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
NS01 | NS01-PSV-016 | NS01-P-016 | FLD | 107-QC | PRESSURE RELIEF VALVE | NS01 | 043.1 | N2 PRESSURE | -: set @ 23.5 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  |  |  | BOC | [5 empty] | 01
NS01 | NS01-TI-001 | NS01-T-001 | PCS | 107-QC | INDICATOR - TEMPERATURE |  |  | NITROGEN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
NS01 | NS01-TT-001 | NS01-T-001 | PKG | 107-QC | TRANSMITTER - TEMPERATURE | NS01 | 043.1 | NITROGEN TEMPERATURE | 8711 | -100to100deg C | +/- 2% | REF | REQ | C | SER | I.S | AI |  |  | 11 | UTIL | [6 empty] | 01
PCS | PCS-XA-001 | PCS-X-001 | SGS | C&E/693 | ALARM - PCS GENERAL |  |  | PCS GENERAL ALARM | PKG: 8712; I.S: N.I.S | DI |  | 35 | SGS | [6 empty] | 01
PCS | PCS-XS-001 | PCS-X-001 | PCS | C&E/693 | SWITCH - MISC. ALARM |  | 083.1 | PCS GENERAL ALARM |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 43 | UTIL | [6 empty] | 01
PCS | PCS-XA-002 | PCS-X-002 | SGS | C&E/693 | ALARM - AUDIBLE |  |  | PCS FAULT | PKG: 8713; I.S: N.I.S | DI |  | 35 | SGS | [6 empty] | 01
PCS | PCS-XS-002 | PCS-X-002 | PCS | C&E/693 | SWITCH - MISC. ALARM |  | 083.1 | PCS FAULT |  | - | - | REF | 12 | F | SIL | N.I.S | DO |  |  | 43 | UTIL | [6 empty] | 01
PD01 | PD01-BD-001 | PD01-B-001 | FLD | 107-DU | RUPTURE DISC | 40-P-PT1A-E-9023945 | 104.0 | BURSTING DISC | 6726 | 1.50 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP1 | ELFAB | BURST-TEL | KS0003/P1 | TI702-SP-5084 |  |  | 01
PD01 | PD01-YI-001 | PD01-B-001 | PCS | 107-DU | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-CV-002 | PD01-C-002 | FLD | 107-DU | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-H-9023901 | 104.0 | NITROGEN SUPPLY | 7135 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
PD01 | PD01-CY-002 | PD01-C-002 | FLD | 107-DU | SOLENOID VALVE | RACK MOUNTED |  | NITROGEN SUPPLY | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
PD01 | PD01-ZSC-002 | PD01-C-002 | FLD | 107-DU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | NITROGEN SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-ZSO-002 | PD01-C-002 | FLD | 107-DU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | NITROGEN SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-CV-005 | PD01-C-005 | PKG | 107-DU | SOLENOID VALVE | REVERSE JET FILTER | 104.0 | FILTER PULSE | 6352 | - | - | REF | REQ | F |  | I.S | DO |  |  | 41 | GP1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 | TBC - TI702-SP-5090 |  | 01
PD01 | PD01-CV-008 | PD01-C-008 | FLD | 107-DU | V-BALL VALVE - CONTROL - F.C. | 40-VP-PT1A-0-9023922 | 104.0 | DRYER VACUUM | 6851 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
PD01 | PD01-CV-009 | PD01-C-009 | FLD | 107-DU | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9023922 | 008.2 | DRYER VACUUM | 7277 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
PD01 | PD01-CY-009 | PD01-C-009 | FLD | 107-DU | SOLENOID VALVE | RACK MOUNTED |  | DRYER VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
PD01 | PD01-ZSC-009 | PD01-C-009 | FLD | 107-DU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DRYER VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-ZSO-009 | PD01-C-009 | FLD | 107-DU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DRYER VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-CV-010 | PD01-C-010 | FLD | 107-DU | V-BALL VALVE - CONTROL - F.C. | 40-P-PT1A-0-9023920 | 104.0 | SCRUBBER 01 | 6817 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
PD01 | PD01-CV-011 | PD01-C-011 | FLD | 107-DU | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023920 | 008.2 | SCRUBBER 02 | 7253 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
PD01 | PD01-CY-011 | PD01-C-011 | FLD | 107-DU | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
PD01 | PD01-ZSC-011 | PD01-C-011 | FLD | 107-DU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-ZSO-011 | PD01-C-011 | FLD | 107-DU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-CV-012 | PD01-C-012 | FLD | 107-DU | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-D-9023905 | 104.0 | COLD HTF RTN | 6773 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
PD01 | PD01-CV-017 | PD01-C-017 | FLD | 107-DU | V-BALL VALVE - CONTROL - F.C. | 25-P-PT1A-C-9023933 | 104.0 | NITROGEN TO RC1 | 6838 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 |  |  | 01
PD01 | PD01-CV-019 | PD01-C-019 | FLD | 107-DU | BALL VALVE - ON/OFF - F.C. | 40-HT-CS3A-D-9029108 | 104.0 | HOT HTF SUPPLY | 7127 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
PD01 | PD01-CY-019 | PD01-C-019 | FLD | 107-DU | SOLENOID VALVE | RACK MOUNTED |  | HOT HTF SUPPLY | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
PD01 | PD01-ZSC-019 | PD01-C-019 | FLD | 107-DU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-ZSO-019 | PD01-C-019 | FLD | 107-DU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-CV-020 | PD01-C-020 | FLD | 107-DU | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-D-9029316 | 104.0 | COLD HTF SUPPLY | 7492 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
PD01 | PD01-ZSC-020 | PD01-C-020 | FLD | 107-DU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-ZSO-020 | PD01-C-020 | FLD | 107-DU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-CV-021 | PD01-C-021 | FLD | 107-DU | SOLENOID VALVE | ADJ TO PT-021 | 104.0 | INTERLOCK | REF: SHE |  |  |  |  | RSG | [5 empty] | 01
PD01 | PD01-DIC-001 | PD01-D-001 | PCS | 107-DU | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-DS-001 | PD01-D-001 | MCC | 107-DU | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
PD01 | PD01-DY-001 | PD01-D-001 | MCC | 107-DU | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
PD01 | PD01-DYC-001 | PD01-D-001 | MCC | 107-DU | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 104.0 | JACKET PUMP | 8714 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
PD01 | PD01-FI-001 | PD01-F-001 | FLD | 107-DU | INDICATOR - FLOW | 25-N-SS1U-0-9028708 | 043.4 | N2 SUPPLY FLOW | -: 5 to 50 l/min; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
PD01 | PD01-HS-001 | PD01-H-001 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01 TOP | 104.0 | AGITATOR START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-HS-002 | PD01-H-002 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01 TOP | 104.0 | AGITATOR STOP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-HIC-003 | PD01-H-003 | LCP | 107-DU | INDICATING/CONTROLLER - HAND | LCP ADJ TO PD01 TOP | 104.0 | AGITATOR SPEED | -: -; -: -; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PD01 | PD01-HS-004 | PD01-H-004 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01 TOP | 104.0 | FILTER PULSE JET ENABLE | 8715 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | GP1 | [6 empty] | 01
PD01 | PD01-HV-005 | PD01-H-005 | FLD | 107-DU | HAND VALVE | 25-SO-PT1A-0-9023940 | 104.0 | WASH SOLVENT INLET | 8120 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN |  | KV0007 |  |  |  | 01
PD01 | PD01-HZSC-005 | PD01-H-005 | FLD | 107-DU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | WASH SOLVENT INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-HZSO-005 | PD01-H-005 | FLD | 107-DU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | WASH SOLVENT INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
PD01 | PD01-HC-007 | PD01-H-007 | LCP | 107-DU | CONTROLLER - HAND | LCP ADJ TO PD01-GB1 | 104.0 | AGITATOR RAIS/LOWER SPEED | -: -; -: -; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PD01 | PD01-HS-008 | PD01-H-008 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01 TOP | 104.0 | AGITATOR RECIPROCATION | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-HS-009A | PD01-H-009 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01 TOP | 104.0 | EMERGENCY STOP | -: -; -: -; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-HS-009B | PD01-H-009 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01-GB1 | 104.0 | EMERGENCY STOP | -: -; -: -; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-HV-010 | PD01-H-010 | FLD | 107-DU | HAND VALVE | 25-P-PT1A-C-9023916 | 104.0 | CLEANING INLET TO RC1 | 7411 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
PD01 | PD01-HZSC-010 | PD01-H-010 | FLD | 107-DU | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CLEANING INLET TO RC1 | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
PD01 | PD01-HZSO-010 | PD01-H-010 | FLD | 107-DU | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CLEANING INLET TO RC1 | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
PD01 | PD01-HS-011 | PD01-H-011 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01-GB1 | 104.0 | GLOVEBOX LOCK/UNLOCK | -: -; -: -; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-HS-012 | PD01-H-012 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01-GB1 | 104.0 | NITROGEN | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-HS-013 | PD01-H-013 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01-GB1 | 104.0 | GLOVEBOX LIGHT | -: -; -: -; REF: SHE; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-HS-014 | PD01-H-014 | FLD | 107-DU | SWITCH - HAND OP. | ADJ TO PD01-GB1 | 104.0 | GLOVEBOX LIGHT | REF: REF; REQ: REQ; F: F | [10 empty] | 01
PD01 | PD01-HS-019 | PD01-H-019 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01 TOP | 104.0 | AGITATOR RAISE/LOWER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-HS-020 | PD01-H-020 | LCP | 107-DU | SWITCH - HAND OP. | LCP ADJ TO PD01 TOP | 104.0 | AGITATOR FORWARD/REVERSE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-LI-002A | PD01-L-002 | PCS | 107-DU | INDICATOR - LEVEL |  |  | RC1 LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-LI-002B | PD01-L-002 | FLD | 107-DU | INDICATOR - LEVEL | ADJ TO PD01 | 104.0 | RC1 LEVEL |  | 0 to 100L | +/- 1% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 |  |  |  | 01
PD01 | PD01-LT-002 | PD01-L-002 | FLD | 107-DU | TRANSMITTER - LEVEL | PD01-RC1/L1/50 | 104.0 | RC1 LEVEL | 6920 | 0 to 100 l | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ENDRESS + HAUSER | FMR245 note2 | KL0028/P2 | TI702-SP-5026 |  |  | 01
PD01 | PD01-PI-001 | PD01-P-001 | FLD | 107-DU | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-0-9023901 | 104.0 | N2 SUPPLY PRESSURE | -: -1 to 3 barg; -: +/- 1%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
PD01 | PD01-PDI-003 | PD01-P-003 | PCS | 107-DU | INDICATOR - PRESSURE - DIFF |  |  | FILTER DIFF PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-PDT-003 | PD01-P-003 | PKG | 107-DU | TRANSMITTER - PRESSURE - DIFF | 50-P-PT1A-E-9023918 | 104.0 | FILTER DIFF PRESSURE | 8716 | 0 to 1 bar | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | [6 empty] | 01
PD01 | PD01-PIC-004 | PD01-P-004 | PCS | 107-DU | INDICATING CONTROLLER - PRESSURE |  |  | VC1 INLET PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-PT-004 | PD01-P-004 | FLD | 107-DU | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-E-9023918 | 104.0 | VC1 INLET PRESSURE | 8114 | -1 to 1.5 barg | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
PD01 | PD01-PI-005 | PD01-P-005 | FLD | 107-DU | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-C-9029316 | 104.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
PD01 | PD01-PI-006 | PD01-P-006 | FLD | 107-DU | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-D-9023939 | 104.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
PD01 | PD01-PI-007 | PD01-P-007 | FLD | 107-DU | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-C-9023933 | 104.0 | RC1 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
PD01 | PD01-PSV-009 | PD01-P-009 | FLD | 107-DU | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9023903 | 104.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
PD01 | PD01-PSV-010 | PD01-P-010 | FLD | 107-DU | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023949 | 104.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
PD01 | PD01-PSV-011 | PD01-P-011 | PKG | 107-DU | PRESSURE RELIEF VALVE | 50-P-PT1A-C-9023927 | 104.0 | RC1 RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
PD01 | PD01-PSL-012 | PD01-P-012 | PKG | 107-DU | SWITCH - PRESSURE - LOW | DELETED | 104.0 | DELETED | -: set @ -30 mbar; -: +/- 1%; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
PD01 | PD01-PSH-013 | PD01-P-013 | PKG | 107-DU | SWITCH - PRESSURE - HIGH | DELETED | 104.0 | DELETED | -: set @ 30 mbar; -: +/- 1%; REQ: 12; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
PD01 | PD01-PI-014 | PD01-P-014 | PKG | 107-DU | PRESSURE GAUGE | DELETED | 104.0 | DELETED | -: -1 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | DELETED |  | 01
PD01 | PD01-PRV-015 | PD01-P-015 | PKG | 107-DU | CONTROL VALVE SELF ACTUATING | WITH MTP02 | 089.2 | AIR TO MTP02 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PD01 | PD01-PI-016 | PD01-P-016 | LCP | 107-DU | PRESSURE GAUGE | LCP ADJ TO PD01-GB1 | 104.0 | GLOVEBOX PRESSURE | -: 0.05 to 0.5 kpA; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PD01 | PD01-PDI-017 | PD01-P-017 | LCP | 107-DU | INDICATOR - DIFF PRESSURE | LCP ADJ TO PD01-GB1 | 104.0 | EXTRACT FILTER CONDITION | -: 0 to 1 kpA; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PD01 | PD01-PI-018 | PD01-P-018 | PKG | 107-DU | PRESSURE GAUGE | 15-N-SS1U-0-9023948 | 104.0 | AGITATOR SEAL PRESSURE | -: 0 to 4 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PD01 | PD01-PI-019 | PD01-P-019 | LCP | 107-DU | PRESSURE GAUGE | LCP ADJ TO PD01-GB1 | 104.0 | NITROGEN PRESSURE | -: 0 to 1.6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PD01 | PD01-PI-020 | PD01-P-020 | PKG | 107-DU | PRESSURE GAUGE | SEAL LUBRICATOR | 104.0 | AGI SEAL LUBRICATOR PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PD01 | PD01-PI-021 | PD01-P-021 | FLD | 107-DU | INDICATOR - PRESSURE | CONTROL PANEL | 104.0 | PRESSURE | -: -1 to 3 barg; REF: GxP/SHE; REQ: 12 |  |  |  |  | PSL | [5 empty] | 01
PD01 | PD01-PT-021 | PD01-P-021 | FLD | 107-DU | TRANSMITTER - PRESSURE | CONTROL PANEL | 104.0 | PRESSURE | -: -1 to 3 barg; REF: GxP/SHE; REQ: 12; I.S: I.S; DI: AI |  |  |  | GP1 | ROSEMOUNT | 3051S ULTRA | KP0001/P2 | TI702-SP-5141 |  |  | 01
PD01 | PD01-SI-001 | PD01-S-001 | PCS | 107-DU | INDICATOR - SPEED |  |  | AGITATOR SPEED | REF: SHE |  |  | 0 | [7 empty] | 01
PD01 | PD01-SIC-001 | PD01-S-001 | PKG | 107-DU | AC INVERTER DRIVE | SWITCHROOM | 104.0 | AGITATOR | 8717 | 0-40 rpm | +/- 2.5% | SHE | REQ | F |  | N.I.S | AI |  |  | 13 | GP1 |  |  |  |  | MIN SPEED 8 rpm |  | 01
PD01 | PD01-TE-002 | PD01-T-002 | FLD | 107-DU | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023920 |  | VC1 VENT TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-TI-002 | PD01-T-002 | PCS | 107-DU | INDICATOR - PRESSURE |  |  | VC1 VENT TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-TT-002 | PD01-T-002 | FLD | 107-DU | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 104.0 | VC1 VENT TEMPERATURE | 6626 | -30 to 70 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
PD01 | PD01-TE-003 | PD01-T-003 | FLD | 107-DU | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9023923 |  | VC1 HTF RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-TI-003 | PD01-T-003 | PCS | 107-DU | INDICATOR - TEMPERATURE |  |  | VC1 HTF RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-TT-003 | PD01-T-003 | FLD | 107-DU | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 104.0 | VC1 HTF RTN TEMP. | 8106 | -30 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
PD01 | PD01-TI-004 | PD01-T-004 | FLD | 107-DU | INDICATOR - TEMPERATURE | 50-HT-CS3A-D-9023947 | 104.0 | JACKET RETURN FROM PD01 | -: -20 to 120 degC; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | S5550/4 | KT0003 |  |  |  | 01
PD01 | PD01-TE-005 | PD01-T-005 | PKG | 107-DU | ELEMENT - TEMPERATURE - RTD | PD01/T1/20 |  | TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
PD01 | PD01-TI-005A | PD01-T-005 | PCS | 107-DU | INDICATOR - PRESSURE |  |  | TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
PD01 | PD01-TI-005B | PD01-T-005 | LCP | 107-DU | INDICATOR - TEMPERATURE | LCP ADJ TO PD01-GB1 | 104.0 | TEMPERATURE |  | -30 to 170 degC | +/- 0.5% | SHE | 12 | C |  | I.S |  |  |  | 0 | [7 empty] | 01
PD01 | PD01-TT-005 | PD01-T-005 | PKG | 107-DU | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 104.0 | TEMPERATURE | 8718 | -30 to 170 degC | +/- 0.5% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ROSEMOUNT | 248 |  | TI702-SP-5058 |  |  | 01
PD01 | PD01-TE-006 | PD01-T-006 | FLD | 107-DU | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9023939 |  | HTF SUPPLY TEMPERATURE | REF: GxP/SHE |  |  | 0 | [7 empty] | 01
PD01 | PD01-TI-006 | PD01-T-006 | FLD | 107-DU | INDICATOR - TEMPERATURE | LOCAL | 104.0 | HTF SUPPLY TEMPERATURE |  | -30 to 170 degC | +/- 1% | GxP/SHE | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KT0003 | TI702-SP-5073 |  |  | 01
PD01 | PD01-TIC-006 | PD01-T-006 | PCS | 107-DU | INDICATING CONTROLLER - TEMPERATURE |  |  | HTF SUPPLY TEMPERATURE | REF: GxP/SHE |  |  | 0 | [7 empty] | 01
PD01 | PD01-TT-006 | PD01-T-006 | FLD | 107-DU | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 104.0 | HTF SUPPLY TEMPERATURE | 8107 | -30 to 170 degC | +/- 1% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
PD01 | PD01-YS-002 | PD01-Y-002 | PKG | 107-DU | SWITCH - POSITION | PD01-GB1 | 104.0 | GLOVEBOX GUARD CLOSED | -: -; -: -; REF: SIL; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-YS-003 | PD01-Y-003 | PKG | 107-DU | SWITCH - BASE OPEN | PD01 | 104.0 | PD01 BASE OPEN | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-YI-004 | PD01-Y-004 | PCS | 107-DU | INDICATOR - PERMISSIVE |  |  | PERMISSIVE INTERLOCK | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PD01 | PD01-YS-004 | PD01-Y-004 | PKG | 107-DU | PERMISSIVE SIGNAL | SWITCHROOM | 104.0 | PERMISSIVE INTERLOCK | 6353 | - | - |  | REQ | F |  | N.I.S | DI |  |  | 35 | GP1 | [6 empty] | 01
PD01 | PD01-YI-007 | PD01-Y-007 | LCP | 107-DU | INDICATOR - LAMP | LCP ADJ TO PD01-GB1 | 104.0 | AGITATOR RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-YS-009 | PD01-Y-009 | PKG | 107-DU | SWITCH - AGITATOR RAISED | PD01 AGITATOR | 104.0 | AGITATOR RAISED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-YS-010 | PD01-Y-010 | PKG | 107-DU | SWITCH - AGITATOR LOWERED | PD01 AGITATOR | 104.0 | AGITATOR LOWERED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PD01 | PD01-YI-011 | PD01-Y-011 | LCP | 107-DU | INDICATOR - LAMP | LCP ADJ TO PD01-GB1 | 104.0 | NITROGEN PURGE COMPLETE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
| Final Calibrations | Pre start Calibration | bar: PKG
PW01 | PW01-AE-001 | PW01-A-001 | PKG | 107-NA | ELEMENT - ANALYSIS |  |  | RO INLET CONDUCTIVITY | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-AI-001A | PW01-A-001 | PCS | 107-NA | INDICATOR - ANALYSIS |  |  | RO INLET CONDUCTIVITY | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-AI-001B | PW01-A-001 | PLC | 107-NA | INDICATOR - ANALYSIS |  |  | RO INLET CONDUCTIVITY | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-AIT-001 | PW01-A-001 | PKG | 107-NA | TRANSMITTER - ANALYSIS - COND. | PW01 RO UNIT | 041.0 | RO INLET CONDUCTIVITY | -: 0 to 100 uS/cm; -: +/- 0.5%; REF: REF; REQ: By request; F: C |  |  | 51 | [6 empty] | * | 37
PW01 | PW01-AE-002 | PW01-A-002 | PKG | 107-NA | ELEMENT - ANALYSIS |  |  | RO OUTLET CONDUCTIVITY | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-AI-002A | PW01-A-002 | PCS | 107-NA | INDICATOR - ANALYSIS |  |  | RO OUTLET CONDUCTIVITY | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-AI-002B | PW01-A-002 | PLC | 107-NA | INDICATOR - ANALYSIS |  |  | RO OUTLET CONDUCTIVITY | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-AIT-002 | PW01-A-002 | PKG | 107-NA | TRANSMITTER - ANALYSIS - COND. | PW01 RO UNIT | 041.0 | RO OUTLET CONDUCTIVITY | -: 0 to 100 uS/cm; -: +/- 0.5%; REF: REF; REQ: By request; F: C |  |  | 51 | [6 empty] | * | 37
PW01 | PW01-AE-003 | PW01-A-003 | PKG | 107-NA | ELEMENT - ANALYSIS |  |  | PW01-UV1 UV MEASUREMENT | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-AI-003 | PW01-A-003 | [6 empty] | REF: REF; REQ: By request
PW01 | PW01-AI-003A | PW01-A-003 | PCS | 107-NA | INDICATOR - ANALYSIS |  |  | PW01-UV1 UV MEASUREMENT | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-AI-003B | PW01-A-003 | PLC | 107-NA | INDICATOR - ANALYSIS |  |  | PW01-UV1 UV MEASUREMENT | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 37
PW01 | PW01-AIT-003 | PW01-A-003 | PKG | 107-NA | TRANSMITTER - ANALYSIS - UV | PW01-UV1 | 041.0 | PW01-UV1 UV MEASUREMENT |  | 60 - 100% | +/- ___% | REF | By request | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-AE-004 | PW01-A-004 | PKG | 107-NA | ELEMENT - ANALYSIS |  |  | CDI UNIT OUTLET CONDUCTIVITY | PKG: L15747 |  |  | 0 | [5 empty] | INCLUDING TE-002 |  | 27
PW01 | PW01-AI-004A | PW01-A-004 | PCS | 107-NA | INDICATOR - ANALYSIS |  |  | CDI UNIT OUTLET CONDUCTIVITY | [11 empty] | 51 | [7 empty] | 01 | bar: DI
PW01 | PW01-AI-004B | PW01-A-004 | PLC | 107-NA | INDICATOR - ANALYSIS |  |  | CDI UNIT OUTLET CONDUCTIVITY | PKG: L15747 |  |  | 0 | [7 empty] | 27
PW01 | PW01-AIT-004 | PW01-A-004 | PKG | 107-NA | TRANSMITTER - ANALYSIS - COND. | PW01 | 041.0 | CDI UNIT OUTLET CONDUCTIVITY |  | 0 - 10 uS/cm | +/- 0.5% | REF | REQ | C |  | N.I.S |  |  |  | 12 | [5 empty] | INCLUDING TI-002 | AI | 01
PW01 | PW01-AT-004 | PW01-A-004 | PKG | 107-NA | TRANSMITTER - ANALYSIS |  |  |  | PKG: L15747 | [10 empty] | 27
PW01 | PW01-AE-005 | PW01-A-005 | PKG | 107-NB | ELEMENT - ANALYSIS |  |  | PURIFIED WATER RTN CONDUCTIVITY | PKG: L15748; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-AI-005A | PW01-A-005 | PCS | 107-NB | INDICATOR - ANALYSIS |  |  | PURIFIED WATER RTN CONDUCTIVITY | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-AI-005B | PW01-A-005 | PLC | 107-NB | INDICATOR - ANALYSIS |  |  | PURIFIED WATER RTN CONDUCTIVITY | PKG: L15748; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-AI-005C | PW01-A-005 | LCP | 107-NB | INDICATOR - ANALYSIS | PW01 LOCAL PANEL | 041.0 | PURIFIED WATER RTN CONDUCTIVITY | -: 0 - 10 uS/cm; -: +/- 0.5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 37
PW01 | PW01-AIT-005 | PW01-A-005 | LCP | 107-NB | TRANSMITTER - ANALYSIS - COND. | PW01 LOCAL PANEL | 041.0 | PURIFIED WATER RTN CONDUCTIVITY |  | 0 - 10 uS/cm | +/- 0.5% | REF | By request | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-AR-005 | PW01-A-005 | LCP | 107-NB | RECORDER - ANALYSIS | PW01 LOCAL PANEL | 041.0 | PURIFIED WATER RTN CONDUCTIVITY | L15748 L15745 L15746 L15749 | 0 - 10 uS/cm | +/- 0.5% | REF | By request | C | [5 empty] | 0 | [7 empty] | 37
PW01 | PW01-AT-005 | PW01-A-005 | PKG | 107-NB | TRANSMITTER - ANALYSIS |  |  |  | PKG: L15748 | [10 empty] | 27
PW01 | PW01-AE-006 | PW01-A-006 | PKG | 107-NB | ELEMENT - ANALYSIS |  |  | PW01-UV2 UV MEASUREMENT | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-AI-006A | PW01-A-006 | PCS | 107-NB | INDICATOR - ANALYSIS |  |  | PW01-UV2 UV MEASUREMENT | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-AI-006B | PW01-A-006 | PLC | 107-NB | INDICATOR - ANALYSIS |  |  | PW01-UV2 UV MEASUREMENT | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-AIT-006 | PW01-A-006 | PKG | 107-NB | TRANSMITTER - ANALYSIS - UV | PW01-UV2 | 041.0 | PW01-UV2 UV MEASUREMENT |  | 0 - 100% | +/- ___% | REF | By request | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-AI-007 | PW01-A-007 | FLD | 107-NB | INDICATOR - ANALYSIS - TOC |  | 041.0 | PW01-TOC CONDUCTIVITY | REQ: 6 | [10 empty] | 37
PW01 | PW01-AIT-007 | PW01-A-007 | FLD | 107-NB | TRANSMITTER - ANALYSIS - TOC |  | 041.0 | PW01-TOC MEASUREMENT | PKG: ?????; REQ: 6 | [10 empty] | 37
PW01 | PW01-AI-008 | PW01-A-008 | FLD | 107-NB | INDICATOR - ANALYSIS - TOC |  | 041.0 | PW01-TOC TOC | REQ: 6 | [10 empty] | 37
PW01 | PW01-AIT-009 | PW01-A-009 | PKG | 107-NA | TRANSMITTER - ANALYSIS - CHLORINE |  | 041.0 | CHLORINE CONCENTRATION | [19 empty] | 48 | bar: PKG
PW01 | PW01-AIT-010 | PW01-A-010 | PKG | 107-NA | TRANSMITTER - ANALYSIS - WATER HARDNESS |  | 041.0 | WATER HARDNESS | [19 empty] | 48 | bar: PKG
PW01 | PW01-AE-503 | PW01-A-503 | PKG | 107-NA | ELEMENT - ANALYSIS |  |  | CDI UNIT OUTLET CONDUCTIVITY | REQ: 12 |  |  | 0 | [7 empty] | 37
PW01 | PW01-AIT-503 | PW01-A-503 | PKG | 107-NA | TRANSMITTER - ANALYSIS - COND. | PW01 | 041.0 | CDI UNIT OUTLET CONDUCTIVITY | -: 0 - 10 uS/cm; -: +/- 0.5%; REQ: 12; F: C; I.S: N.I.S |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-CV-001 | PW01-C-001 | PKG | 107-NB | DIAPHRAGM VALVE - ON/OFF F.C. | PW01 | 041.0 | PURIFIED WATER RECYCLE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-001 | PW01-C-001 | PKG | 107-NB | SOLENOID VALVE | MTD. ON VALVE |  | PURIFIED WATER RECYCLE | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-002 | PW01-C-002 | PKG | 107-NB | DIAPHRAGM VALVE - ON/OFF - F.C. | PW01 | 041.0 | PURIFIED WATER FEED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-002 | PW01-C-002 | PKG | 107-NB | SOLENOID VALVE | MTD. ON VALVE |  | PURIFIED WATER FEED | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-003 | PW01-C-003 | PKG | 107-NB | GLOBE VALVE - CONTROL - F.C. | PW01 | 041.0 | STEAM TO HC1 |  | - | - | REF | REQ | F |  | N.I.S |  |  |  | 22 | [6 empty] | AO | 01
PW01 | PW01-CV-004 | PW01-C-004 | PKG | 107-NB | DIAPHRAGM VALVE - ON/OFF - F.C. | PW01 | 041.0 | PURIFIED WATER BLEED | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-004 | PW01-C-004 | PKG | 107-NB | SOLENOID VALVE | MTD. ON VALVE |  | PURIFIED WATER BLEED | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-005 | PW01-C-005 | PKG | 107-NB | BALL VALVE - ON/OFF - F.O. | PW01 | 041.0 | STEAM TO HC1 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-005 | PW01-C-005 | PKG | 107-NB | SOLENOID VALVE | MTD. ON VALVE |  | STEAM TO HC1 | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-006 | PW01-C-006 | PKG | 107-NB | BALL VALVE - ON/OFF - F.O. | PW01 | 041.0 | COOLING WATER TO HC2 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-006 | PW01-C-006 | PKG | 107-NB | SOLENOID VALVE | MTD. ON VALVE |  | COOLING WATER TO HC2 | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-007 | PW01-C-007 | PKG | 107-NB | DIAPHRAGM VALVE - ON/OFF - F.C. | PW01 | 041.0 | CP1 OUTLET TO DRAIN | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-007 | PW01-C-007 | PKG | 107-NB | SOLENOID VALVE | MTD. ON VALVE |  | CP1 OUTLET TO DRAIN | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-008 | PW01-C-008 | PKG | 107-NB | BALL VALVE - ON/OFF - F.O. | PW01 | 041.0 | COOLING WATER RTN | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-008 | PW01-C-008 | PKG | 107-NB | SOLENOID VALVE | MTD. ON VALVE |  | COOLING WATER RTN | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-009 | PW01-C-009 | PKG | 107-NA | DIAPHRAGM VALVE - ON/OFF - F.C. | PW01 | 041.0 | UTIL WATER INLET | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-009 | PW01-C-009 | PKG | 107-NA | SOLENOID VALVE | MTD. ON VALVE |  | UTIL WATER INLET | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-010 | PW01-C-010 | PKG | 107-NA | DIAPHRAGM VALVE - ON/OFF - F.O. | PW01 | 041.0 | SOFTENER OUTLET | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | CONTROL FROM KC-001 |  | 01
PW01 | PW01-CV-011 | PW01-C-011 | PKG | 107-NA | DIAPHRAGM VALVE - ON/OFF - F.O. | PW01 | 041.0 | SOFTENER OUTLET | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | CONTROL FROM KC-001 |  | 01
PW01 | PW01-CV-012 | PW01-C-012 | PKG | 107-NA | BALL VALVE - ON/OFF - F.C. | PW01 | 041.0 | RO UNIT INLET | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-012 | PW01-C-012 | PKG | 107-NA | SOLENOID VALVE | MTD. ON VALVE |  | RO UNIT INLET | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-013 | PW01-C-013 | PKG | 107-NA | DIAPHRAGM VALVE - ON/OFF - F.C. | PW01 | 041.0 | RO RECYCLE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-013 | PW01-C-013 | PKG | 107-NA | SOLENOID VALVE | MTD. ON VALVE |  | RO RECYCLE | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-CV-014 | PW01-C-014 | PKG | 107-NA | DIAPHRAGM VALVE - ON/OFF - F.O. | PW01 | 041.0 | RO UNIT TO DRAIN | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-CY-014 | PW01-C-014 | PKG | 107-NA | SOLENOID VALVE | MTD. ON VALVE |  | RO UNIT TO DRAIN | I.S: N.I.S |  |  | 42 | [6 empty] | DO | 01
PW01 | PW01-DIC-001 | PW01-D-001 | PLC | 107-NA | INDICATING CONTR. - MOTOR DRIVE |  | 041.0 | RO FEED PUMP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-DIC-002 | PW01-D-002 | PLC | 107-NA | INDICATING CONTR. - MOTOR DRIVE |  | 041.0 | CD1 RECIRC PUMP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-DIC-003 | PW01-D-003 | PLC | 107-NA | INDICATING CONTR. - MOTOR DRIVE |  | 041.0 | RAW WATER FEED PUMP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-DS-003 | PW01-D-003 | PCS | 107-NA | DRIVE - AVAILABLE |  |  | RAW WATER FEED PUMP | [11 empty] | 51 | [7 empty] | 01 | bar: PKG; DI
PW01 | PW01-DY-003 | PW01-D-003 | PCS | 107-NA | DRIVE - RUNNING |  |  | RAW WATER FEED PUMP | [11 empty] | 51 | [7 empty] | 01 | bar: PKG; DI
PW01 | PW01-DIC-004 | PW01-D-004 | PLC | 107-NB | INDICATING CONTR. - MOTOR DRIVE |  | 041.0 | CP1 PUMP | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-DS-004 | PW01-D-004 | PCS | 107-NB | DRIVE - AVAILABLE |  |  | CP1 PUMP | [11 empty] | 51 | [7 empty] | 01 | bar: PKG; DI
PW01 | PW01-DY-004 | PW01-D-004 | PCS | 107-NB | DRIVE - RUNNING |  |  | CP1 PUMP | [11 empty] | 51 | [7 empty] | 01 | bar: PKG; DI
PW01 | PW01-FQI-001 | PW01-F-001 | PKG | 107-NA | FLOW INDICATOR/TOTALISOR | PW01 | 041.0 | UTIL WATER FLOW | -: 0 - 10 m3/hr; -: +/- 2%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-FI-002 | PW01-F-002 | PKG | 107-NA | VA FLOW INDICATOR | PW01 | 041.0 | RAW WATER FLOW | -: 0.65 - 6.5 m3/h; -: +/- 3%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-FI-003A | PW01-F-003 | PCS | 107-NA | INDICATOR - FLOW |  |  | RO UNIT RECIRC FLOW | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-FI-003B | PW01-F-003 | PLC | 107-NA | INDICATOR - FLOW |  |  | RO UNIT RECIRC FLOW | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-FIT-003 | PW01-F-003 | PKG | 107-NA | TRANSMITTER - FLOW | PW01 | 041.0 | RO UNIT RECIRC FLOW | -: 2 - 30 l/min; -: +/- ___%; REF: REF; REQ: By request; F: C |  |  | 51 | [6 empty] | * | 01
PW01 | PW01-FI-004A | PW01-F-004 | PCS | 107-NA | INDICATOR - FLOW |  |  | RO RECYCLE FLOW | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-FI-004B | PW01-F-004 | PLC | 107-NA | INDICATOR - FLOW |  |  | RO RECYCLE FLOW | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-FIT-004 | PW01-F-004 | PKG | 107-NA | TRANSMITTER - FLOW | PW01 | 041.0 | RO RECYCLE FLOW | -: 2 - 30 l/min; -: +/- ___%; REF: REF; REQ: By request; F: C |  |  | 51 | [6 empty] | * | 01
PW01 | PW01-FI-005A | PW01-F-005 | PCS | 107-NA | INDICATOR - FLOW |  |  | RO UNIT OUTLET FLOW | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-FI-005B | PW01-F-005 | PLC | 107-NA | INDICATOR - FLOW |  |  | RO UNIT OUTLET FLOW | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-FIT-005 | PW01-F-005 | PKG | 107-NA | TRANSMITTER - FLOW | PW01 | 041.0 | RO UNIT OUTLET FLOW | -: 4 - 50 l/min; -: +/- ___%; REF: REF; REQ: By request; F: C |  |  | 51 | [6 empty] | * | 01
PW01 | PW01-FI-006 | PW01-F-006 | PKG | 107-NA | INDICATOR - FLOW |  |  | CD1 INLET FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-FT-006 | PW01-F-006 | PKG | 107-NA | TRANSMITTER - FLOW | PW01 | 041.0 | CD1 INLET FLOW | -: 1.7 - 167 l/min; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-FI-007 | PW01-F-007 | PKG | 107-NA | INDICATOR - FLOW |  |  | CD1 CONCENTRATE FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-FT-007 | PW01-F-007 | PKG | 107-NA | TRANSMITTER - FLOW | PW01 | 041.0 | CD1 CONCENTRATE FLOW | -: 1.7 - 167 l/min; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-FI-008 | PW01-F-008 | PKG | 107-NA | INDICATOR - FLOW |  |  | CD1 TO DRAIN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-FT-008 | PW01-F-008 | PKG | 107-NA | TRANSMITTER - FLOW | PW01 | 041.0 | CD1 TO DRAIN | -: 1.5 - 200 l/hr; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-FI-009 | PW01-F-009 | PKG | 107-NA | INDICATOR - FLOW |  |  | CD1 RECIRC TO DRAIN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-FT-009 | PW01-F-009 | PKG | 107-NA | TRANSMITTER - FLOW | PW01 | 041.0 | CD1 RECIRC TO DRAIN | -: 6 - 800 l/hr; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-FI-010 | PW01-F-010 | PKG | 107-NA | VA FLOW INDICATOR | PW01 | 041.0 | RO RECYCLE TO DRAIN | -: 100 - 1000 l/hr; -: +/- 3%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-FI-011A | PW01-F-011 | PCS | 107-NB | INDICATOR - FLOW |  |  | PURIFIED WATER RETURN | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-FI-011B | PW01-F-011 | PLC | 107-NB | INDICATOR - FLOW |  |  | PURIFIED WATER RETURN | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-FI-011C | PW01-F-011 | LCP | 107-NB | INDICATOR - FLOW |  | 041.0 | PURIFIED WATER RETURN | -: 25 - 255 l/min; -: +/- 0.5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 37
PW01 | PW01-FIT-011 | PW01-F-011 | PKG | 107-NB | TRANSMITTER - FLOW | PW01 | 041.0 | PURIFIED WATER RETURN |  | 25 - 255 l/min | +/- 0.5% | REF | By request | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-FQI-012 | PW01-F-012 | PKG | 107-NA | INDICATOR - FLOW/TOTALISER | PW01 | 041.0 | SOFTENER REGENERATION | -: 0 - 10 m3/hr; -: +/- 2%; REF: REF; REQ: By request; F: C |  |  | 0 | [5 empty] | INPUT TO KC-001 |  | 01
PW01 | PW01-FI-504 | PW01-F-504 | PKG | 107-NA | INDICATOR - FLOW |  |  | CEDI02 | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-FSL-504 | PW01-F-504 | PKG | 107-NA | SWITCH - LOW FLOW |  |  | CEDI02 | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-FI-507 | PW01-F-507 | PKG | 107-NA | INDICATOR - FLOW |  |  | CEDI02 | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-FSL-507 | PW01-F-507 | PKG | 107-NA | SWITCH - LOW FLOW |  |  | CEDI02 | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-FI-013 | PW01-FI-013 | FLD | 107-NA | INDICATOR - FLOW | PW01 | 041.0 | DEGASSER AIR FLOW | -: 10 - 100 l/min; -: +/- 2%; REF: REF; REQ: By request; F: C | [10 empty] | 01
PW01 | PW01-KC-001 | PW01-K-001 | PKG | 107-NA | CONTROLLER - TIMER |  |  | SOFTENER CONTROL | REF: REF; REQ: By request |  |  | 0 | [5 empty] | CONTROL FOR CV-010 & CV-011 |  | 37
PW01 | PW01-LAHH-001 | PW01-L-001 | PLC | 107-NA | ALARM - LEVEL - HI HI |  |  | BREAK TANK LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-LSHH-001 | PW01-L-001 | PKG | 107-NA | SWITCH - LEVEL - HI HI | PW01 BREAK TANK | 041.0 | BREAK TANK LEVEL |  | Fixed | - | REF | By request | F |  | N.I.S |  |  |  | 35 | [6 empty] | DI | 01
PW01 | PW01-LAH-002 | PW01-L-002 | PLC | 107-NA | ALARM - LEVEL - HIGH |  |  | BREAK TANK LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-LSH-002 | PW01-L-002 | PKG | 107-NA | SWITCH - LEVEL - HIGH | PW01 BREAK TANK | 041.0 | BREAK TANK LEVEL |  | Fixed | - | REF | By request | F |  | N.I.S |  |  |  | 35 | [6 empty] | DI | 01
PW01 | PW01-LAL-003 | PW01-L-003 | PLC | 107-NA | ALARM - LEVEL - LOW |  |  | BREAK TANK LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-LSL-003 | PW01-L-003 | PKG | 107-NA | SWITCH - LEVEL - LOW | PW01 BREAK TANK | 041.0 | BREAK TANK LEVEL |  | Fixed | - | REF | By request | F |  | N.I.S |  |  |  | 35 | [6 empty] | DI | 01
PW01 | PW01-LALL-004 | PW01-L-004 | PLC | 107-NA | ALARM - LEVEL - LO LO |  |  | BREAK TANK LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-LSLL-004 | PW01-L-004 | PKG | 107-NA | SWITCH - LEVEL - LO LO | PW01 BREAK TANK | 041.0 | BREAK TANK LEVEL |  | Fixed | - | REF | By request | F |  | N.I.S |  |  |  | 35 | [6 empty] | DI | 01
PW01 | PW01-LI-005A | PW01-L-005 | PCS | 107-NB | INDICATOR - LEVEL |  |  | ST1 LEVEL | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-LI-005B | PW01-L-005 | PLC | 107-NB | INDICATOR - LEVEL |  |  | ST1 LEVEL | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-LI-005C | PW01-L-005 | LCP | 107-NB | INDICATOR - LEVEL | PW01 LOCAL PANEL | 041.0 | ST1 LEVEL | -: 1000-6000 litre; -: +/- 1%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 37
PW01 | PW01-LIT-005 | PW01-L-005 | PKG | 107-NB | TRANSMITTER - LEVEL | PW01-ST1 | 041.0 | ST1 LEVEL |  | 1000-6000 litre | +/- 1% | REF | By request | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-PI-001 | PW01-P-001 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | SP02 INLET PRESSURE | -: 0 to 10 barg; -: +/- 1.6%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-002 | PW01-P-002 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | SP02 OUTLET PRESSURE | -: 0 to 10 barg; -: +/- 1.6%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PAL-002 | PW01-P-002A | PLC | 107-NB | ALARM - PRESSURE - LOW |  |  | PURIFIED RING LOW AIR PRESSURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
PW01 | PW01-PSL-002 | PW01-P-002A | PKG | 107-NB | SWITCH - PRESSURE - LOW | PW01 | 041.0 | PURIFIED RING LOW AIR PRESSURE |  | set @ 5 barg | +/- 3% | REF | By request | C |  | N.I.S |  |  |  | 35 | [6 empty] | DI | 01
PW01 | PW01-PRV-003 | PW01-P-003 | PKG | 107-NA | CONTROL VALVE SELF ACTUATING | PW01 | 041.0 | RAW WATER RECIRC | -: set @ ____ barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PAL-003 | PW01-P-003A | PLC | 107-NA | ALARM - PRESSURE - LOW |  |  | PRE-TREATMENT LOW AIR PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-PSL-003 | PW01-P-003A | PKG | 107-NA | SWITCH - PRESSURE - LOW | PW01 | 041.0 | PRE-TREATMENT LOW AIR PRESSURE |  | set @ 5 barg | +/- 3% | REF | By request | C |  | N.I.S |  |  |  | 35 | [6 empty] | DI | 01
PW01 | PW01-PI-004 | PW01-P-004 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | RAW FEED PUMP OUTLET | -: 0 to 7 barg; -: +/- 1.5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-005 | PW01-P-005 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | ACTIVATED CARBON FILTER | -: 0 to 7 barg; -: +/- 1.5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-006 | PW01-P-006 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | MICRO FILTER | -: 0 to 7 barg; -: +/- 1.5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-007 | PW01-P-007 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | FILTERS OUTLET PRESSURE | -: 0 to 7 barg; -: +/- 1.5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PS-008 | PW01-P-008 | PKG | 107-NA | SWITCH - PRESSURE | PW01 | 041.0 | RO FEED PUMP INLET | -: set @ 0.7 barg; -: +/- 3%; REF: REF; REQ: By request; F: C |  |  | 0 | [5 empty] | INPUT TO RO UNIT CONTROL |  | 01
PW01 | PW01-PI-009 | PW01-P-009 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | RO FEED PUMP OUTLET | -: 0 to 40 barg; -: +/- 1.6%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-010 | PW01-P-010 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | RO UNIT RECIRC PRESSURE | -: 0 to 40 barg; -: +/- 1.6%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-011 | PW01-P-011 | PKG | 107-NA | PRESSURE GAUGE - DIAPHRAGM SEAL | PW01 | 041.0 | CD1 INLET PRESSURE | -: 0 to 4 barg; -: +/- 1.6%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-012 | PW01-P-012 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | CD1 CONCENTRATE INLET | -: 0 to 4 barg; -: +/- 1.6%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-013 | PW01-P-013 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | CONCENTRATE PUMP INLET | -: 0 to 4 barg; -: +/- 1.6%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-014 | PW01-P-014 | PKG | 107-NA | PRESSURE GAUGE - DIAPHRAGM SEAL | PW01 | 041.0 | CD1 OUTLET PRESSURE | -: 0 to 4 barg; -: +/- 1.6%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-015 | PW01-P-015 | PKG | 107-NB | PRESSURE GAUGE - DIAPHRAGM SEAL | PW01 | 041.0 | PURIFIED WATER RTN PRESSURE | -: 0 to 10 barg; -: +/- 1.6%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PRV-016 | PW01-P-016 | PKG | 107-NB | CONTROL VALVE SELF ACTUATING | PW01 | 041.0 | PURIFIED WATER RTN | -: set @ ____ barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-018 | PW01-P-018 | PKG | 107-NB | PRESSURE GAUGE - DIAPHRAGM SEAL | PW01 | 041.0 | CP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 1.6%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-019 | PW01-P-019 | PKG | 107-NB | PRESSURE GAUGE | PW01 | 041.0 | STEAM TO HC1 | -: 0 to 10 barg; -: +/- 1%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-020 | PW01-P-020 | PKG | 107-NB | PRESSURE GAUGE | PW01 | 041.0 | STEAM SUPPLY PRESSURE | -: 0 to 10 barg; -: +/- 1%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-021 | PW01-P-021 | PKG | 107-NB | PRESSURE GAUGE | PW01 | 041.0 | COOLING WATER SUPPLY PRESSURE | -: 0 to 6 barg; -: +/- 1%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-022 | PW01-P-022 | PKG | 107-NB | PRESSURE GAUGE | PW01 | 041.0 | PURIFIED WATER SUPPLY PRESSURE | -: 0 to 10 barg; -: +/- 1.6%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PSV-023 | PW01-P-023 | PKG | 107-NB | PRESSURE RELIEF VALVE | PW01 | 041.0 | COOLING WATER RTN RELIEF | -: 4.5 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PRV-024 | PW01-P-024 | PKG | 107-NB | CONTROL VALVE SELF ACTUATING | PW01 | 041.0 | STEAM TO HC1 | -: set @ 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-024 | PW01-P-024A | PKG | 107-NB | PRESSURE GAUGE | PW01 | 041.0 | COOLING WATER RETURN | -: 0 to 10 barg; -: +/- 1%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PSV-025 | PW01-P-025 | PKG | 107-NB | PRESSURE RELIEF VALVE | PW01 | 041.0 | STEAM TO HC1 | -: 1.0 Barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-025 | PW01-P-025A | PKG | 107-NB | PRESSURE GAUGE | PW01 | 041.0 | SKID 2 SERVICE AIR | -: 0 to 10 barg; -: +/- 1%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-027 | PW01-P-027 | PKG | 107-NB | PRESSURE GAUGE | PW01 | 041.0 | SKID 1 SERVICE AIR | -: 0 to 10 barg; -: +/- 1.5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-027 | PW01-P-027 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | COMPRESSED AIR SUPPLY | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-PI-028 | PW01-P-028 | PKG | 107-NB | PRESSURE GAUGE | PW01 | 041.0 | SOFTENER INLET | -: 0 to 10 barg; -: +/- 1.5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-028 | PW01-P-028 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | SOFTENER INLET PRESSURE | REF: REF; REQ: By request
PW01 | PW01-PRV-029 | PW01-P-029 | PKG | 107-NA | CONTROL VALVE SELF ACTUATING | PW01 | 041.0 | PURIFIED RING AIR SUPPLY | -: set @ 4.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PRV-030 | PW01-P-030 | PKG | 107-NA | CONTROL VALVE SELF ACTUATING | PW01 | 041.0 | PRE-TREATMENT AIR SUPPLY | -: set @ 4.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PSV-031 | PW01-P-031 | PKG | 107-NB | PRESSURE RELIEF VALVE | PW01 PLANT ROOM | 041.0 | PW01 BACK-UP AIR SUPPLY | -: 7.0 Barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-032 | PW01-P-032 | PKG | 107-NB | PRESSURE GAUGE | PW01-PRV-033 | 041.0 | PW01-PRV-033 SUPPLY PRESSURE | -: 0 to ?? barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | MTD ON PW01-PRV-033 |  | 01
PW01 | PW01-PI-032 | PW01-P-032 | PKG | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | STAND UP COMPRESSED AIR SUPPLY | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-PRV-033 | PW01-P-033 | PKG | 107-NA | CONTROL VALVE SELF ACTUATING | PW01 PLANT ROOM | 041.0 | PW01 BACK-UP AIR SUPPLY | -: set @ ?.? barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
PW01 | PW01-PI-034 | PW01-P-034 | FLD | 107-NA | PRESSURE GAUGE | PW01 | 041.0 | DEGASSER AIR SUPPLY | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
PW01 | PW01-PRV-034 | PW01-P-034 | FLD | 107-NA | CONTROL VALVE SELF ACTUATING | PW01 | 041.0 | DEGASSER AIR SUPPLY | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
PW01 | PW01-PI-501 | PW01-P-501 | PKG | 107-NA | PRESSURE GAUGE |  |  | CEDI02 | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-PI-502 | PW01-P-502 | PKG | 107-NA | PRESSURE GAUGE |  |  | CEDI02 | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-PI-505 | PW01-P-505 | PKG | 107-NA | PRESSURE GAUGE |  |  | CEDI02 | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-PI-506 | PW01-P-506 | PKG | 107-NA | PRESSURE GAUGE |  |  | CEDI02 | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-RV-026 | PW01-R-026 | PKG | 107-NB | VACUUM BREATHER VALVE | PW01 | 041.0 | STEAM TO HC1 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-TE-001 | PW01-T-001 |  | 107-NA | ELEMENT - TEMPERATURE | PW01 | 041.0 | FILTERS OUTLET TEMPERATURE | REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-TI-001A | PW01-T-001 |  | 107-NA | INDICATOR - TEMPERATURE | PW01 | 041.0 | FILTERS OUTLET TEMPERATURE | REF: REF; REQ: By request
PW01 | PW01-TI-001B | PW01-T-001 |  | 107-NA | INDICATOR - TEMPERATURE | PW01 | 041.0 | FILTERS OUTLET TEMPERATURE | REF: REF; REQ: By request
PW01 | PW01-TT-001 | PW01-T-001 | PKG | 107-NA | TRANSMITTER - TEMPERATURE | PW01 | 041.0 | FILTERS OUTLET TEMPERATURE |  | 0 to 50 degC | +/- 1% | REF | By request | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 01
PW01 | PW01-TAL-003 | PW01-T-003 | [6 empty] | REQ: 12
PW01 | PW01-TE-003 | PW01-T-003 | PKG | 107-NB | ELEMENT - TEMPERATURE - RTD |  |  | PW01-F1 TEMPERATURE | REQ: 12 |  |  | 0 | [7 empty] | 37
PW01 | PW01-TIC-003 | PW01-T-003 | PLC | 107-NB | INDICATING CONTROLLER - TEMPERATURE |  |  | PW01-F1 TEMPERATURE | PKG: L15750; REQ: 12 |  |  | 0 | [7 empty] | 37
PW01 | PW01-TT-003 | PW01-T-003 | PKG | 107-NB | TRANSMITTER - TEMPERATURE | PW01 | 041.0 | PW01-F1 TEMPERATURE |  | 0 to 150 degC | +/- 1% | REF | 12 | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-TE-004 | PW01-T-004 | PKG | 1070NB | ELEMENT - TEMPERATURE - RTD |  |  | CP1 DISCHARGE TEMPERATURE | PKG: L15745; REQ: By request | [10 empty] | 37
PW01 | PW01-TI-004 | PW01-T-004 | PKG | 107-NB | INDICATOR - TEMPERATURE |  |  | CP1 DISCHARGE TEMPERATURE | PKG: L15745; REF: REF; REQ: REQ | [10 empty] | 37
PW01 | PW01-TI-004A | PW01-T-004 | PCS | 107-NB | INDICATOR - TEMPERATURE |  |  | CP1 DISCHARGE TEMPERATURE | REF: REF; REQ: By request; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-TI-004B | PW01-T-004 | PLC | 107-NB | INDICATOR - TEMPERATURE |  |  | CP1 DISCHARGE TEMPERATURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 37
PW01 | PW01-TI-004C | PW01-T-004 | PKG | 107-NB | INDICATOR - TEMPERATURE |  |  | CP1 DISCHARGE TEMPERATURE | PKG: L15745; REF: REF; REQ: By request | [10 empty] | 37
PW01 | PW01-TR-004 | PW01-T-004 | [6 empty] | REF: REF; REQ: By request
PW01 | PW01-TT-004 | PW01-T-004 | PKG | 107-NB | TRANSMITTER - TEMPERATURE | PW01 | 041.0 | CP1 DISCHARGE TEMPERATURE | L15745 | 0 to 150 degC | +/- 1% | REF | By request | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-TE-005 | PW01-T-005 | PKG | 107-NB | ELEMENT - TEMPERATURE - RTD |  |  | HC2 OUTLET TEMPERATURE | PKG: L15746; REQ: 12 | [10 empty] | 37
PW01 | PW01-TI-005 | PW01-T-005 | PKG | 107-NB | INDICATOR - TEMPERATURE |  |  | HC2 OUTLET TEMPERATURE | PKG: L15746 | [10 empty] | 27
PW01 | PW01-TI-005A | PW01-T-005 | PCS | 107-NB | INDICATOR - TEMPERATURE |  |  | HC2 OUTLET TEMPERATURE | REQ: 24; DI: * |  |  | 51 | [7 empty] | 37
PW01 | PW01-TI-005B | PW01-T-005 | PLC | 107-NB | INDICATOR - TEMPERATURE |  |  | HC2 OUTLET TEMPERATURE | REQ: 12 |  |  | 0 | [7 empty] | 37
PW01 | PW01-TIC-005 | PW01-T-005 | PKG | 107-NB | INDICATING CONTROLLER - TEMPERATURE |  |  | HC2 OUTLET TEMPERATURE | PKG: L15746; REQ: 12 | [10 empty] | 37
PW01 | PW01-TR-005 | PW01-T-005 | [6 empty] | REQ: By request
PW01 | PW01-TT-005 | PW01-T-005 | PKG | 107-NB | TRANSMITTER - TEMPERATURE | PW01 | 041.0 | HC2 OUTLET TEMPERATURE | L15746 | 0 to 150 degC | +/- 1% |  | 12 | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-TE-006 | PW01-T-006 | PKG | 107-NB | ELEMENT - TEMPERATURE - RTD |  |  | PURIFIED WATER RETURN | PKG: L15749; REQ: 12 | [10 empty] | 37
PW01 | PW01-TI-006C | PW01-T-006 | PKG | 107-NB | INDICATOR - TEMPERATURE |  |  | PURIFIED WATER RETURN | PKG: L15749; REQ: 12 | [10 empty] | 37
PW01 | PW01-TR-006 | PW01-T-006 | [6 empty] | REQ: By request
PW01 | PW01-TT-006 | PW01-T-006 | PKG | 107-NA | TRANSMITTER - TEMPERATURE |  | 041.0 | PURIFIED WATER RETURN | L15749 | 0 to 150 degC | +/- 1% |  | 12 | C |  | N.I.S |  |  |  | 12 | [6 empty] | AI | 37
PW01 | PW01-TI-006A | PW01-T-006A | [6 empty] | REQ: 24
PW01 | PW01-TI-006B | PW01-T-006B | [6 empty] | REQ: 12
PW01 | PW01-TI-007 | PW01-T-007 | FLD | 107-NB | INDICATOR - ANALYSIS - TOC |  | 041.0 | PW01-TOC TEMPERATURE | REQ: 6 | [10 empty] | 37
PW01 | PW01-XA-001 | PW01-X-001 | PCS | 107-NB | ALARM - STATUS |  |  | DISTRIBUTION GENERAL ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-XS-001 | PW01-X-001 | PLC | 107-NB | SWITCH - MISC. ALARM | PW01 PLC | 041.0 | DISTRIBUTION GENERAL ALARM | 8719 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
PW01 | PW01-XA-002 | PW01-X-002 | PCS | 107-NB | ALARM - AUDIBLE |  |  | SANITISATION IN PROGRESS | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-XS-002 | PW01-X-002 | PLC | 107-NB | SWITCH - MISC. ALARM | PW01 PLC | 041.0 | SANITISATION IN PROGRESS | 8720 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
PW01 | PW01-XA-003 | PW01-X-003 | PCS | 107-NB | ALARM - AUDIBLE |  |  | PURE WATER AVAILABLE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
PW01 | PW01-XS-003 | PW01-X-003 | PLC | 107-NB | SWITCH - MISC. ALARM | PW01 PLC | 041.0 | PURE WATER AVAILABLE | 8721 | - | - |  | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
PW01 | PW01-XS-004 | PW01-X-004 | PCS | 107-NB | SWITCH - MISC. ALARM |  | 041.0 | INITIATE SANITISATION | 8722 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
PW01 | PW01-XY-004 | PW01-X-004 | PLC | 107-NB | STATUS SIGNAL | PW01 PLC | 041.0 | INITIATE SANITISATION |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
PW01 | PW01-XA-005 | PW01-X-005 | PCS | 107-NA | ALARM - AUDIBLE |  | 041.0 | GENERATION GENERAL ALARM | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
PW01 | PW01-XS-005 | PW01-X-005 | PLC | 107-NA | SWITCH - MISC. ALARM | PW01 PLC | 041.0 | GENERATION GENERAL ALARM | 8723 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
PW01 | PW01-XA-006 | PW01-X-006 | PCS | 107-NB | ALARM - GMP INSTRUMENT OUT OF RANGE |  |  | GMP CRITICAL COMMON ALARM | PKG: TBC; -: ?
PW01 | PW01-XS-006 | PW01-X-006 | PKG | 107-NB | SWITCH - GMP COMMON ALARM | PW01 PKG | 041.0 | GMP CRITICAL COMMON ALARM | bar: PKG
PW01 | PW01-YA-001 | PW01-Y-001 | [6 empty] | REQ: 24
PW01 | PW01-YS-001 | PW01-Y-001 | PKG | 107-NB | RUPTURE DISC | PW01-ST1 | 041.0 | BURSTING DISC | -: -; -: -; REQ: 24; F: F; I.S: N.I.S |  |  | 35 | [6 empty] | DI | 37
PWF01 | PWF01-FE-001 | PWF01-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF01 SKID | 041.0 | PURIFIED WATER TO REACTORS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 |  |  |  |  | 01 | v15.0
PWF01 | PWF01-FI-001 | PWF01-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF01 SKID | 041.0 | PURIFIED WATER TO REACTORS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 | [5 empty] | v15.0
PWF02 | PWF02-FE-001 | PWF02-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF02 SKID | 041.0 | PURIFIED WATER TO REACTORS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 | [5 empty] | v15.0
PWF02 | PWF02-FI-001 | PWF02-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF02 SKID | 041.0 | PURIFIED WATER TO REACTORS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 | [5 empty] | v15.0
PWF03 | PWF03-FE-001 | PWF03-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF03 SKID | 041.0 | PURIFIED WATER TO REACTORS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 | [5 empty] | v15.0
PWF03 | PWF03-FI-001 | PWF03-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF03 SKID | 041.0 | PURIFIED WATER TO REACTORS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 | [5 empty] | v15.0
PWF04 | PWF04-FE-001 | PWF04-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF04 SKID | 041.0 | PURIFIED WATER TO REACTORS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 | [5 empty] | v15.0
PWF04 | PWF04-FI-001 | PWF04-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF04 SKID | 041.0 | PURIFIED WATER TO REACTORS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 | [5 empty] | v15.0
PWF05 | PWF05-FE-001 | PWF05-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF05 SKID | 041.0 | PURIFIED WATER TO FILTER DRYERS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 | [5 empty] | v16.0
PWF05 | PWF05-FI-001 | PWF05-F-001 | FLD | 902-007-002-000-00211 | MOBILE WATER BATCH METER | PWF05 SKID | 041.0 | PURIFIED WATER TO FILTER DRYERS | -: 18-180L per min; -: +/-5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NIXON | BNO 1000 | [5 empty] | v16.0
R01 | R01-AG-001 | R01-A-001 | PKG | 107-BA | SPEED MOORE DISPLAY |  | 047.0 | AGITATOR | PKG: 6940; REF: REF; REQ: By request | [10 empty] | 34
R01 | R01-BD-001 | R01-B-001 | FLD | 107-BA | RUPTURE DISC | 80-P-PT1A-H-9021103 | 047.0 | BURSTING DISC | 6734 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R01 | R01-YI-001 | R01-B-001 | PCS | 107-BA | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG; REQ
R01 | R01-CV-001 | R01-C-001 | PKG | 107-BA | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R01/K/80 | 047.0 | BOTTOM OUTLET VALVE | 6968 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCHUFF | [5 empty] | 01
R01 | R01-CY-001 | R01-C-001 | PKG | 107-BA | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R01 | R01-ZSC-001 | R01-C-001 | PKG | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R01 | R01-ZSO-001 | R01-C-001 | PKG | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R01 | R01-CV-004 | R01-C-004 | FLD | 107-BA | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9021130 | 047.0 | NITROGEN SUPPLY | 6779 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 3730-2 POSITIONER |  | TI702-SP-5008 |  |  | 01
R01 | R01-CV-005 | R01-C-005 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021111 | 047.0 | SCRUBBER 01 | 7178 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-CY-005 | R01-C-005 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-005 | R01-C-005 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-005 | R01-C-005 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-006 | R01-C-006 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021110 | 047.0 | SCRUBBER 02 | 7179 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-CY-006 | R01-C-006 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-006 | R01-C-006 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-006 | R01-C-006 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-007 | R01-C-007 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9021138 | 047.0 | PROCESS VACUUM | 7312 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-CY-007 | R01-C-007 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-007 | R01-C-007 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-007 | R01-C-007 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-008 | R01-C-008 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9021137 | 047.0 | HOUSE VACUUM | 7259 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-CY-008 | R01-C-008 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-008 | R01-C-008 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-008 | R01-C-008 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-009 | R01-C-009 | FLD | 107-BA | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9029313 | 047.0 | COLD HTF SUPPLY | 7498 | - | - | SHE | REQ | F | [5 empty] | 0 |  | WORCESTER | 52E ENVIROSAFE | KV0017 |  |  |  | 01
R01 | R01-CY-009 | R01-C-009 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-009 | R01-C-009 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-009 | R01-C-009 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-010 | R01-C-010 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 50-HT-CS3A-D-9029103 | 047.0 | HOT HTF SUPPLY | 7493 | - | - | SHE | REQ | F | [5 empty] | 0 |  | WORCESTER | 52E ENVIROSAFE | KV0017 |  |  |  | 01
R01 | R01-ZSC-010 | R01-C-010 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-010 | R01-C-010 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-011 | R01-C-011 | FLD | 107-BA | GLOBE VALVE - CONTROL - F.C. | 50-HT-CS3A-D-9021123 | 047.0 | HOT HTF RTN | 6360 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R01 | R01-CV-012 | R01-C-012 | FLD | 107-BA | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-D-9021156 | 047.0 | COLD HTF RTN | 6361 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R01 | R01-CV-013 | R01-C-013 | FLD | 107-BA | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-D-9021125 | 047.0 | DUAL JACKET | 7130 | - | - | REF | REQ | F | [5 empty] | 0 |  | WORCESTER | 52E ENVIROSAFE | KV0017 |  |  |  | 01
R01 | R01-CY-013 | R01-C-013 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-013 | R01-C-013 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-013 | R01-C-013 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-014 | R01-C-014 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9021159 | 047.0 | N2 TO BOTTOM OUTLET | 7137 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-CY-014 | R01-C-014 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-014 | R01-C-014 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-014 | R01-C-014 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-015 | R01-C-015 | FLD | 107-BA | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9021114 | 047.0 | PC1 TEMPERED HTF RTN | 6405 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R01 | R01-CV-016 | R01-C-016 | FLD | 107-BA | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9021117 | 047.0 | VC1 COLD HTF RTN | 6410 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R01 | R01-CV-018 | R01-C-018 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021105 | 047.0 | DISTILLATE VENT LINE | 7180 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-CY-018 | R01-C-018 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-018 | R01-C-018 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-018 | R01-C-018 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-019 | R01-C-019 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021825 | 047.0 | LIQUID INLET | 7229 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-CY-019 | R01-C-019 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-019 | R01-C-019 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-019 | R01-C-019 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-021 | R01-C-021 | FLD | 107-BA | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9021110 | 047.0 | +VE PRESSURE CONTROL | 6800 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R01 | R01-CV-022 | R01-C-022 | FLD | 107-BA | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9021137 | 047.0 | -VE PRESSURE CONTROL | 6821 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R01 | R01-CV-024 | R01-C-024 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9021167 | 047.0 | SOLIDS INLET | 7340 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-CX-024 | R01-C-024 | SGS | 107-BA | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R01 | R01-CY-024 | R01-C-024 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED | 047.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-024 | R01-C-024 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-024 | R01-C-024 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-CV-025 | R01-C-025 | FLD | 107-BA | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9021110 | 047.0 | SOLIDS ADDITION VENT | 7122 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-CX-025 | R01-C-025 | SGS | 107-BA | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R01 | R01-CY-025 | R01-C-025 | FLD | 107-BA | SOLENOID VALVE | RACK MOUNTED | 047.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 | TI702-SP-5004 | TI702-SP-5004 |  |  | 01
R01 | R01-ZSC-025 | R01-C-025 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-ZSO-025 | R01-C-025 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 047.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-DIC-001 | R01-D-001 | PCS | 107-BA | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R01 | R01-DS-001 | R01-D-001 | MCC | 107-BA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R01 | R01-DY-001 | R01-D-001 | MCC | 107-BA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R01 | R01-DYC-001 | R01-D-001 | MCC | 107-BA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 047.0 | JACKET PUMP | 8724 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R01 | R01-HS-002 | R01-H-002 | FLD | 107-BA | SWITCH - HAND OP. | ADJ TO R01 | 047.0 | CRASH COOL | 6690 | - | - | GxP | 6 | F | SOP | I.S | DI |  |  | 32 | GP1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R01 | R01-HV-008 | R01-H-008 | FLD | 107-BA | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028625 | 047.0 | N2 PRESSURE SELECT | 6982 | - | - | REF | REQ | F | [5 empty] | 0 |  | WORCESTER | SERIES 18 | KV0017 |  |  |  | 01
R01 | R01-HZSC-008 | R01-H-008 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R01 | R01-HZSO-008 | R01-H-008 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R01 | R01-HV-009 | R01-H-009 | FLD | 107-BA | HAND VALVE | 25-P-PT1A-0-9021162 | 047.0 | AUX. INLET | 6983 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-HZSC-009 | R01-H-009 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-HZSO-009 | R01-H-009 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R01 | R01-HV-010 | R01-H-010 | FLD | 107-BA | HAND VALVE | 40-P-PT1A-0-9021825 | 047.0 | REAGENTS INLET | 6984 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R01 | R01-HZSC-010 | R01-H-010 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-HZSO-010 | R01-H-010 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-HV-012 | R01-H-012 | FLD | 107-BA | HAND VALVE | 25-P-PT1A-0-9021824 | 047.0 | SOLVENTS INLET | 6985 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-HZSC-012 | R01-H-012 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-HZSO-012 | R01-H-012 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R01 | R01-HV-013 | R01-H-013 | FLD | 107-BA | HAND VALVE | 40-P-PT1A-0-9021825 | 047.0 | SLURRIES INLET | 6986 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R01 | R01-HZSC-013 | R01-H-013 | FLD | 107-BA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-HZSO-013 | R01-H-013 | FLD | 107-BA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R01 | R01-II-002 | R01-I-002 | PCS | 107-BA | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-IT-002 | R01-I-002 | MCC | 107-BA | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 047.0 | AGITATOR CURRENT | 8757 | 0 to 5 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP1 | [6 empty] | 01
R01 | R01-LAH-001 | R01-L-001 | PCS | 107-BA | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L8103; -: On/Off; -: On/Off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R01 | R01-LE-001 | R01-L-001 | FLD | 107-BA | ELEMENT - LEVEL | 80-P-PT1A-H-9021103 | 047.0 | HIGH LEVEL | L8103 | On/Off | On/Off | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R01 | R01-LSH-001 | R01-L-001 | CPR | 107-BA | SWITCH - LEVEL - HIGH | 80-P-PT1A-H-9021103 | 047.0 | HIGH LEVEL | L8103 | On/Off | On/Off | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | GP1 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R01 | R01-LG-002 | R01-L-002 | PKG | 107-BA | LEVEL GAUGE | AGITATOR SEAL POT | 047.0 | AGITATOR SEAL POT LEVEL | -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R01 | R01-PIC-001 | R01-P-001 | PCS | 107-BA | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: 7013; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-PIT-001 | R01-P-001 | FLD | 107-BA | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9021103 | 047.0 | PRESSURE | 7013 | -1 to 2.3 barg | +/- 0.066 barg | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | FOXBORO | 141GP (Note1) | KP0001 | TI702-SP-5006 |  |  | 01
R01 | R01-PI-002 | R01-P-002 | PCS | 107-BA | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: 6640; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R01 | R01-PIT-002 | R01-P-002 | FLD | 107-BA | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9021103 | 047.0 | PRESSURE | 6640 | -1 to 2.3 barg | +/- 0.066 barg | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R01 | R01-PAH-003 | R01-P-003 | PCS | 107-BA | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-PSH-003 | R01-P-003 | FLD | 107-BA | SWITCH - PRESSURE - DIAPHRAGM - HI | 80-P-PT1A-H-9021103 | 047.0 | HIGH PRESSURE | 6641 | set @ 2.2 barg | +/- 1% | SHE | By request | C |  | I.S | DI |  |  | 32 | GP1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R01 | R01-PI-004 | R01-P-004 | FLD | 107-BA | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9021130 | 047.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note3) | KP0006/1 |  |  |  | 01
R01 | R01-PI-007 | R01-P-007 | FLD | 107-BA | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-C-9029313 | 047.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R01 | R01-PI-008 | R01-P-008 | FLD | 107-BA | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-D-9021125 | 047.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R01 | R01-PSV-012 | R01-P-012 | FLD | 107-BA | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9021155 | 047.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REF: GxP; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R01 | R01-PSV-013 | R01-P-013 | FLD | 107-BA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021153 | 047.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REF: GxP; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R01 | R01-PSV-014 | R01-P-014 | FLD | 107-BA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021154 | 047.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REF: GxP; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R01 | R01-PRV-015 | R01-P-015 | FLD | 107-BA | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028624 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R01 | R01-PI-016 | R01-P-016 | PKG | 107-BA | PRESSURE GAUGE | AGITATOR SEAL POT | 047.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 25 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R01 | R01-SE-001 | R01-S-001 | PKG | 107-BA | ELEMENT - SPEED | AGITATOR SHAFT | 047.0 | AGITATOR | L6940 | 0 to 186 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R01 | R01-SI-001A | R01-S-001 | PCS | 107-BA | INDICATOR - SPEED |  |  | AGITATOR | PKG: L6940; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-SI-001B | R01-S-001 | FLD | 107-BA | INDICATOR - SPEED | ADJ TO R01 AGITATOR | 047.0 | AGITATOR | L6940 | 0 to 200 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R01 | R01-DS-002 | R01-S-002 | MCC | 107-BA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R01 | R01-DY-002 | R01-S-002 | MCC | 107-BA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R01 | R01-DYC-002 | R01-S-002 | MCC | 107-BA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 047.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R01 | R01-SC-002 | R01-S-002 | MCC | 107-BA | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 047.0 | AGITATOR | 8757 | 0 to 200 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP1 |  |  |  |  | SET Min 37 rpm & Max 186 rpm |  | 01
R01 | R01-SIC-002 | R01-S-002 | PCS | 107-BA | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | PKG: L8757; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TE-001 | R01-T-001 | PKG | 107-BA | ELEMENT - TEMPERATURE - RTD | WITH R01-CV-001 |  | TEMPERATURE #1 | PKG: L6855; -: -30 to 170 degC; -: +/- 2%; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R01 | R01-TI-001A | R01-T-001 | PCS | 107-BA | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6855; -: -30 to 170 degC; -: +/- 2%; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R01 | R01-TI-001B | R01-T-001 | FLD | 107-BA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R01 | 047.0 | TEMPERATURE #1 | PKG: L6855; REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R01 | R01-TT-001 | R01-T-001 | PKG | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | TEMPERATURE #1 | L6855 | -30 to 170 degC | +/- 2% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R01 | R01-TE-002 | R01-T-002 | PKG | 107-BA | ELEMENT - TEMPERATURE - RTD | WITH R01-CV-001 |  | TEMPERATURE #2 | PKG: L6856; -: -30 to 170 degC; -: +/- 2%; REF: GxP/SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TI-002A | R01-T-002 | PCS | 107-BA | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6856; -: -30 to 170 degC; -: +/- 2%; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R01 | R01-TI-002B | R01-T-002 | FLD | 107-BA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 047.0 | TEMPERATURE #2 | PKG: L6856; REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R01 | R01-TT-002 | R01-T-002 | PKG | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | TEMPERATURE #2 | L6856 | -30 to 170 degC | +/- 2% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R01 | R01-TE-003 | R01-T-003 | PKG | 107-BA | ELEMENT - TEMPERATURE - RTD | R01/N2/80 |  | BAFFLE TEMPERATURE | PKG: 6857; -: -30 to 170 degC; -: +/- 2%; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R01 | R01-TI-003A | R01-T-003 | PCS | 107-BA | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: 6857; -: -30 to 170 degC; -: +/- 2%; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R01 | R01-TI-003B | R01-T-003 | FLD | 107-BA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 047.0 | BAFFLE TEMPERATURE | PKG: 6857; REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R01 | R01-TT-003 | R01-T-003 | PKG | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | BAFFLE TEMPERATURE | 6857 | -30 to 170 degC | +/- 2% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R01 | R01-TE-004 | R01-T-004 | FLD | 107-BA | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9021125 |  | JACKET INLET TEMP. | PKG: L6858; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TI-004A | R01-T-004 | PCS | 107-BA | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6858; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TI-004B | R01-T-004 | FLD | 107-BA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 047.0 | JACKET INLET TEMP. | PKG: L6858; REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R01 | R01-TT-004 | R01-T-004 | FLD | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | JACKET INLET TEMP. | 6858 |  |  | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R01 | R01-TE-005 | R01-T-005 | FLD | 107-BA | ELEMENT - TEMPERATURE - RTD | 80-P-PT1A-H-9021103 |  | PC1 INLET TEMPERATURE | PKG: L6513; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TI-005 | R01-T-005 | PCS | 107-BA | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TT-005 | R01-T-005 | FLD | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | PC1 INLET TEMPERATURE | L6513 |  |  | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R01 | R01-TI-005A | R01-T-005A | [6 empty] | PKG: L6513; REF: REF; REQ: By request
R01 | R01-TE-006 | R01-T-006 | FLD | 107-BA | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9021110 |  | VC1 OFF-GAS TEMPERATURE | PKG: L6514; -: -20 to 80 degC; -: +/- 4%; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R01 | R01-TI-006A | R01-T-006 | PCS | 107-BA | INDICATOR - TEMPERATURE |  |  | VC1 OFF-GAS TEMPERATURE | PKG: L6514; -: -20 to 80 degC; -: +/- 4%; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R01 | R01-TI-006B | R01-T-006 | FLD | 107-BA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R01 | 047.0 | VC1 OFF-GAS TEMPERATURE | PKG: L6514; REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R01 | R01-TT-006 | R01-T-006 | FLD | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | VC1 OFF-GAS TEMPERATURE | 6514 | -20 to 80 degC | +/- 4% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R01 | R01-TE-007 | R01-T-007 | FLD | 107-BA | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9021117 |  | VC1 HTF RTN TEMPERATURE | PKG: L6515; -: -30 to 70 degC; -: +/- 1%; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TIC-007 | R01-T-007 | PCS | 107-BA | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | PKG: L6515; -: -30 to 70 degC; -: +/- 1%; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TT-007 | R01-T-007 | FLD | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | VC1 HTF RTN TEMPERATURE | 6515 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R01 | R01-TE-008 | R01-T-008 | FLD | 107-BA | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9021114 |  | PC1 HTF RTN TEMPERATURE | PKG: L6516; -: -30 to 70 degC; -: +/- 1%; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TIC-008 | R01-T-008 | PCS | 107-BA | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | PKG: L6516; -: -30 to 70 degC; -: +/- 1%; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TT-008 | R01-T-008 | FLD | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | PC1 HTF RTN TEMPERATURE | 6516 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R01 | R01-TE-009 | R01-T-009 | FLD | 107-BA | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9021102 |  | DISTILLATE RTN TEMP. | PKG: L6517; -: -20 to 80 degC; -: +/- 0.5%; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TI-009A | R01-T-009 | PCS | 107-BA | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | PKG: L6517; -: -20 to 80 degC; -: +/- 0.5%; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TI-009B | R01-T-009 | FLD | 107-BA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 047.0 | DISTILLATE RTN TEMP. | L6517 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R01 | R01-TT-009 | R01-T-009 | FLD | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | DISTILLATE RTN TEMP. | L6517 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5096 |  |  | 01
R01 | R01-TE-010 | R01-T-010 | FLD | 107-BA | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9021124 |  | OUTLET TEMPERATURE | PKG: L6518; -: -30 to 170 degC; -: +/- 1%; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TI-010A | R01-T-010 | PCS | 107-BA | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6518; -: -30 to 170 degC; -: +/- 1%; REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R01 | R01-TI-010B | R01-T-010 | FLD | 107-BA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R01 | 047.0 | OUTLET TEMPERATURE | L6518 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R01 | R01-TT-010 | R01-T-010 | FLD | 107-BA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 047.0 | OUTLET TEMPERATURE | 6518 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R01 | R01-YA-001 | R01-Y-001 | PCS | 107-BA | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R01 | R01-YS-001 | R01-Y-001 | FUT | 107-BA | COMMON ALARM | R01 GAS SEAL ASSEMBLY | 047.0 | AGITATOR SEAL COMMON ALARM | PKG: 8673; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R02 | R02-AG-001 | R02-A-001 | PKG | 107-BB | SPEED MOORE DISPLAY |  | 048.0 |  | PKG: L6941; REF: REF; REQ: By request | [10 empty] | 34
R02 | R02-BD-001 | R02-B-001 | FLD | 107-BB | RUPTURE DISC | 80-P-PT1A-H-9021203 | 048.0 | BURSTING DISC | 6735 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R02 | R02-YI-001 | R02-B-001 | PCS | 107-BB | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-CV-001 | R02-C-001 | PKG | 107-BB | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R02/K/80 | 048.0 | BOTTOM OUTLET VALVE | 8786 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R02 | R02-CY-001 | R02-C-001 | PKG | 107-BB | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R02 | R02-ZSC-001 | R02-C-001 | PKG | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R02 | R02-ZSO-001 | R02-C-001 | PKG | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R02 | R02-CV-004 | R02-C-004 | FLD | 107-BB | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9021230 | 048.0 | NITROGEN SUPPLY | 6780 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R02 | R02-CV-005 | R02-C-005 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021211 | 048.0 | SCRUBBER 01 | 7181 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-CY-005 | R02-C-005 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-005 | R02-C-005 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-005 | R02-C-005 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-006 | R02-C-006 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021210 | 048.0 | SCRUBBER 02 | 7182 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-CY-006 | R02-C-006 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-006 | R02-C-006 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-006 | R02-C-006 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-007 | R02-C-007 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9021238 | 048.0 | PROCESS VACUUM | 7313 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-CY-007 | R02-C-007 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-007 | R02-C-007 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-007 | R02-C-007 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-008 | R02-C-008 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9021237 | 048.0 | HOUSE VACUUM | 7260 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-CY-008 | R02-C-008 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-008 | R02-C-008 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-008 | R02-C-008 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-009 | R02-C-009 | FLD | 107-BB | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-C-9029416 | 048.0 | COLD HTF SUPPLY | 7499 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R02 | R02-CY-009 | R02-C-009 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-009 | R02-C-009 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-009 | R02-C-009 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-010 | R02-C-010 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 50-HT-CS3A-D-9029155 | 048.0 | HOT HTF SUPPLY | 7494 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R02 | R02-ZSC-010 | R02-C-010 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-010 | R02-C-010 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-011 | R02-C-011 | FLD | 107-BB | GLOBE VALVE - CONTROL - F.C. | 50-HT-CS3A-D-9021223 | 048.0 | HOT HTF RTN | 6363 | - | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R02 | R02-CV-012 | R02-C-012 | FLD | 107-BB | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-D-9021256 | 048.0 | COLD HTF RTN | 6367 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R02 | R02-CV-013 | R02-C-013 | FLD | 107-BB | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-D-9021225 | 048.0 | DUAL JACKET | 7131 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R02 | R02-CY-013 | R02-C-013 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-013 | R02-C-013 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-013 | R02-C-013 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-014 | R02-C-014 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9021259 | 048.0 | N2 TO BOTTOM OUTLET | 7138 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-CY-014 | R02-C-014 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-014 | R02-C-014 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-014 | R02-C-014 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-015 | R02-C-015 | FLD | 107-BB | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9021214 | 048.0 | PC1 TEMPERED HTF RTN | 6406 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R02 | R02-CV-016 | R02-C-016 | FLD | 107-BB | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9021217 | 048.0 | VC1 COLD HTF RTN | 6411 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R02 | R02-CV-018 | R02-C-018 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021205 | 048.0 | DISTILLATE VENT LINE | 7183 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-CY-018 | R02-C-018 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-018 | R02-C-018 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-018 | R02-C-018 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-019 | R02-C-019 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021865 | 048.0 | LIQUID INLET | 7230 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-CY-019 | R02-C-019 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-019 | R02-C-019 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-019 | R02-C-019 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-021 | R02-C-021 | FLD | 107-BB | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9021210 | 048.0 | +VE PRESSURE CONTROL | 6801 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R02 | R02-CV-022 | R02-C-022 | FLD | 107-BB | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9021237 | 048.0 | -VE PRESSURE CONTROL | 6822 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R02 | R02-CV-024 | R02-C-024 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-0-9021267 | 048.0 | SOLIDS INLET | 7341 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-CX-024 | R02-C-024 | SGS | 107-BB | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R02 | R02-CY-024 | R02-C-024 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED | 048.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-024 | R02-C-024 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-024 | R02-C-024 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-CV-025 | R02-C-025 | FLD | 107-BB | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9021210 | 048.0 | SOLIDS ADDITION VENT | 7284 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 | GP1 | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-CX-025 | R02-C-025 | SGS | 107-BB | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R02 | R02-CY-025 | R02-C-025 | FLD | 107-BB | SOLENOID VALVE | RACK MOUNTED | 048.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R02 | R02-ZSC-025 | R02-C-025 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-ZSO-025 | R02-C-025 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 048.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-DIC-001 | R02-D-001 | PCS | 107-BB | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R02 | R02-DS-001 | R02-D-001 | MCC | 107-BB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R02 | R02-DY-001 | R02-D-001 | MCC | 107-BB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R02 | R02-DYC-001 | R02-D-001 | MCC | 107-BB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 048.0 | JACKET PUMP | 8726 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R02 | R02-HS-002 | R02-H-002 | FLD | 107-BB | SWITCH - HAND OP. | ADJ TO R02 | 048.0 | CRASH COOL | 6693 | - | - | GxP | 6 | F | SOP | I.S | DI |  |  | 32 | GP1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R02 | R02-HV-008 | R02-H-008 | FLD | 107-BB | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028656 | 048.0 | N2 PRESSURE SELECT | 7470 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R02 | R02-HZSC-008 | R02-H-008 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R02 | R02-HZSO-008 | R02-H-008 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R02 | R02-HV-009 | R02-H-009 | FLD | 107-BB | HAND VALVE | 25-P-PT1A-0-9021262 | 048.0 | AUX. INLET | 7381 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-HZSC-009 | R02-H-009 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-HZSO-009 | R02-H-009 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R02 | R02-HV-010 | R02-H-010 | FLD | 107-BB | HAND VALVE | 40-P-PT1A-0-9021865 | 048.0 | REAGENTS INLET | 7362 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R02 | R02-HZSC-010 | R02-H-010 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-HZSO-010 | R02-H-010 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-HV-012 | R02-H-012 | FLD | 107-BB | HAND VALVE | 25-P-PT1A-0-9021842 | 048.0 | SOLVENTS INLET | 7382 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-HZSC-012 | R02-H-012 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-HZSO-012 | R02-H-012 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R02 | R02-HV-013 | R02-H-013 | FLD | 107-BB | HAND VALVE | 40-P-PT1A-0-9021865 | 048.0 | SLURRIES INLET | 7439 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R02 | R02-HZSC-013 | R02-H-013 | FLD | 107-BB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-HZSO-013 | R02-H-013 | FLD | 107-BB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R02 | R02-II-002 | R02-I-002 | PCS | 107-BB | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-IT-002 | R02-I-002 | MCC | 107-BB | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 048.0 | AGITATOR CURRENT | 8758 | 0 to 5 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP1 | [6 empty] | 01
R02 | R02-LAH-001 | R02-L-001 | PCS | 107-BB | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L6627; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R02 | R02-LE-001 | R02-L-001 | FLD | 107-BB | ELEMENT - LEVEL | 80-P-PT1A-H-9021203 | 048.0 | HIGH LEVEL | L6627 | Fixed | - | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R02 | R02-LSH-001 | R02-L-001 | CPR | 107-BB | SWITCH - LEVEL - HIGH | 80-P-PT1A-H-9021203 | 048.0 | HIGH LEVEL | 6627 | - | - | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | GP1 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R02 | R02-LG-002 | R02-L-002 | PKG | 107-BB | LEVEL GAUGE | AGITATOR SEAL POT | 048.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R02 | R02-PIC-001 | R02-P-001 | PCS | 107-BB | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: L7014; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-PIT-001 | R02-P-001 | FLD | 107-BB | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9021203 | 048.0 | PRESSURE | 7014 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | FOXBORO | 141GP (Note1) | KP0001 | TI702-SP-5006 |  |  | 01
R02 | R02-PI-002 | R02-P-002 | PCS | 107-BB | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6643; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R02 | R02-PIT-002 | R02-P-002 | FLD | 107-BB | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9021203 | 048.0 | PRESSURE | 6643 | -1 to 2.3 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R02 | R02-PAH-003 | R02-P-003 | PCS | 107-BB | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-PSH-003 | R02-P-003 | FLD | 107-BB | SWITCH - PRESSURE - DIAPHRAGM - HI | 80-P-PT1A-H-9021203 | 048.0 | HIGH PRESSURE | 6644 | set @ 2.2 barg | +/- 1% | REF | By request | C |  | I.S | DI |  |  | 32 | GP1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R02 | R02-PI-004 | R02-P-004 | FLD | 107-BB | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9021230 | 048.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R02 | R02-PI-007 | R02-P-007 | FLD | 107-BB | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-C-9029416 | 048.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R02 | R02-PI-008 | R02-P-008 | FLD | 107-BB | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-D-9021225 | 048.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R02 | R02-PSV-012 | R02-P-012 | FLD | 107-BB | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9021255 | 048.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REF: GxP; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R02 | R02-PSV-013 | R02-P-013 | FLD | 107-BB | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021253 | 048.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REF: GxP; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R02 | R02-PSV-014 | R02-P-014 | FLD | 107-BB | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021254 | 048.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REF: GxP; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R02 | R02-PRV-015 | R02-P-015 | FLD | 107-BB | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028655 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R02 | R02-PI-016 | R02-P-016 | PKG | 107-BB | PRESSURE GAUGE | AGITATOR SEAL POT | 048.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R02 | R02-SE-001 | R02-S-001 | PKG | 107-BB | ELEMENT - SPEED | AGITATOR SHAFT | 048.0 | AGITATOR | L6941 | 0 to 186 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R02 | R02-SI-001A | R02-S-001 | PCS | 107-BB | INDICATOR - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-SI-001B | R02-S-001 | FLD | 107-BB | INDICATOR - SPEED | ADJ TO RO2 AGITATOR | 048.0 | AGITATOR | 6941 | 0 to 200 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R02 | R02-DS-002 | R02-S-002 | MCC | 107-BB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R02 | R02-DY-002 | R02-S-002 | MCC | 107-BB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R02 | R02-DYC-002 | R02-S-002 | MCC | 107-BB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 048.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R02 | R02-SC-002 | R02-S-002 | MCC | 107-BB | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 048.0 | AGITATOR | 8758 | 0 to 200 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP1 |  |  |  |  | SET Min 37 rpm & Max 186 rpm |  | 01
R02 | R02-SIC-002 | R02-S-002 | PCS | 107-BB | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | PKG: L6941; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TE-001 | R02-T-001 | PKG | 107-BB | ELEMENT - TEMPERATURE - RTD | WITH R02-CV-001 |  | TEMPERATURE #1 | PKG: L6899; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R02 | R02-TI-001A | R02-T-001 | PCS | 107-BB | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6899; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R02 | R02-TI-001B | R02-T-001 | FLD | 107-BB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R02 | 048.0 | TEMPERATURE #1 | L6899 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R02 | R02-TT-001 | R02-T-001 | PKG | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | TEMPERATURE #1 | L6899 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R02 | R02-TE-002 | R02-T-002 | PKG | 107-BB | ELEMENT - TEMPERATURE - RTD | WITH R02-CV-001 |  | TEMPERATURE #2 | PKG: L6900; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R02 | R02-TI-002A | R02-T-002 | PCS | 107-BB | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6900; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R02 | R02-TI-002B | R02-T-002 | FLD | 107-BB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 048.0 | TEMPERATURE #2 | L6900 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R02 | R02-TT-002 | R02-T-002 | PKG | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | TEMPERATURE #2 | 6900 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R02 | R02-TE-003 | R02-T-003 | PKG | 107-BB | ELEMENT - TEMPERATURE - RTD | R02/N2/80 |  | BAFFLE TEMPERATURE | PKG: L6901; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R02 | R02-TI-003A | R02-T-003 | PCS | 107-BB | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6901; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R02 | R02-TI-003B | R02-T-003 | FLD | 107-BB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 048.0 | BAFFLE TEMPERATURE | L6901 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R02 | R02-TT-003 | R02-T-003 | PKG | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | BAFFLE TEMPERATURE | 6901 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R02 | R02-TE-004 | R02-T-004 | FLD | 107-BB | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9021225 |  | JACKET INLET TEMP. | PKG: L6902; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TI-004A | R02-T-004 | PCS | 107-BB | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6902; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TI-004B | R02-T-004 | FLD | 107-BB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 048.0 | JACKET INLET TEMP. | L6902 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R02 | R02-TT-004 | R02-T-004 | FLD | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | JACKET INLET TEMP. | 6902 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R02 | R02-TE-005 | R02-T-005 | FLD | 107-BB | ELEMENT - TEMPERATURE - RTD | 80-P-PT1A-H-9021203 |  | PC1 INLET TEMPERATURE | PKG: L6519; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TI-005 | R02-T-005 | PCS | 107-BB | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R02 | R02-TT-005 | R02-T-005 | FLD | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | PC1 INLET TEMPERATURE | 6519 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R02 | R02-TI-005A | R02-T-005A | [6 empty] | REQ: By request
R02 | R02-TE-006 | R02-T-006 | FLD | 107-BB | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-H-9021210 |  | VC1 OFF GAS TEMPERATURE | PKG: L6520; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R02 | R02-TI-006A | R02-T-006 | PCS | 107-BB | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6520; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R02 | R02-TI-006B | R02-T-006 | FLD | 107-BB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R02 | 048.0 | VC1 OFF GAS TEMPERATURE | L6520 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R02 | R02-TT-006 | R02-T-006 | FLD | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | VC1 OFF GAS TEMPERATURE | 6520 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R02 | R02-TE-007 | R02-T-007 | FLD | 107-BB | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9021217 |  | VC1 HTF RTN TEMPERATURE | PKG: L6521; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TIC-007 | R02-T-007 | PCS | 107-BB | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | PKG: L6521; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TT-007 | R02-T-007 | FLD | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | VC1 HTF RTN TEMPERATURE | 6521 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R02 | R02-TE-008 | R02-T-008 | FLD | 107-BB | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9021214 |  | PC1 HTF RTN TEMPERATURE | PKG: L6522; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TIC-008 | R02-T-008 | PCS | 107-BB | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | PKG: L6522; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TT-008 | R02-T-008 | FLD | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | PC1 HTF RTN TEMPERATURE | 6522 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R02 | R02-TE-009 | R02-T-009 | FLD | 107-BB | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9021202 |  | DISTILLATE RTN TEMP. | PKG: L6523; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TI-009A | R02-T-009 | PCS | 107-BB | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TI-009B | R02-T-009 | FLD | 107-BB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 048.0 | DISTILLATE RTN TEMP. | L6523 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R02 | R02-TT-009 | R02-T-009 | FLD | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | DISTILLATE RTN TEMP. | 6523 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R02 | R02-TE-010 | R02-T-010 | FLD | 107-BB | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9021224 |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TI-010A | R02-T-010 | PCS | 107-BB | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6524; REQ: By request |  |  | 0 | [7 empty] | 01
R02 | R02-TI-010B | R02-T-010 | FLD | 107-BB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R02 | 048.0 | OUTLET TEMPERATURE | L6524 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R02 | R02-TT-010 | R02-T-010 | FLD | 107-BB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 048.0 | OUTLET TEMPERATURE | 6524 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R02 | R02-YA-001 | R02-Y-001 | PCS | 107-BB | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R02 | R02-YS-001 | R02-Y-001 | FUT | 107-BB | COMMON ALARM | R02 GAS SEAL ASSEMBLY | 048.0 | AGITATOR SEAL COMMON ALARM | PKG: 8674; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R03 | R03-AG-001 | R03-A-001 | PKG | 107-BC | SPEED MOORE DISPLAY |  | 049.0 |  | PKG: L6942; REF: REF; REQ: By request | [10 empty] | 34
R03 | R03-BD-001 | R03-B-001 | FLD | 107-BC | RUPTURE DISC | 100-P-PT1A-H-9021303 | 049.0 | BURSTING DISC | 6736 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R03 | R03-YI-001 | R03-B-001 | PCS | 107-BC | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-CV-001 | R03-C-001 | PKG | 107-BC | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R03/K/100 | 049.0 | BOTTOM OUTLET VALVE | 8787 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R03 | R03-CY-001 | R03-C-001 | PKG | 107-BC | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R03 | R03-ZSC-001 | R03-C-001 | PKG | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R03 | R03-ZSO-001 | R03-C-001 | PKG | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R03 | R03-CV-004 | R03-C-004 | FLD | 107-BC | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9021330 | 049.0 | NITROGEN SUPPLY | 6781 | 0 to 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R03 | R03-CV-005 | R03-C-005 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021311 | 049.0 | SCRUBBER 01 | 7184 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-CY-005 | R03-C-005 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-005 | R03-C-005 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-005 | R03-C-005 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-006 | R03-C-006 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021311 | 049.0 | SCRUBBER 02 | 7185 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-CY-006 | R03-C-006 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-006 | R03-C-006 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-006 | R03-C-006 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-007 | R03-C-007 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9021338 | 049.0 | PROCESS VACUUM | 7314 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-CY-007 | R03-C-007 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-007 | R03-C-007 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-007 | R03-C-007 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-008 | R03-C-008 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9021337 | 049.0 | HOUSE VACUUM | 7261 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-CY-008 | R03-C-008 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-008 | R03-C-008 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-008 | R03-C-008 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-009 | R03-C-009 | FLD | 107-BC | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-D-9029315 | 049.0 | COLD HTF SUPPLY | 7531 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R03 | R03-CY-009 | R03-C-009 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-009 | R03-C-009 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-009 | R03-C-009 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-010 | R03-C-010 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029105 | 049.0 | HOT HTF SUPPLY | 7511 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R03 | R03-ZSC-010 | R03-C-010 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-010 | R03-C-010 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-011 | R03-C-011 | FLD | 107-BC | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9021323 | 049.0 | HOT HTF RTN | 6362 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R03 | R03-CV-012 | R03-C-012 | FLD | 107-BC | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9021356 | 049.0 | COLD HTF RTN | 6384 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R03 | R03-CV-013 | R03-C-013 | FLD | 107-BC | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9021325 | 049.0 | DUAL JACKET | 7503 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R03 | R03-CY-013 | R03-C-013 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-013 | R03-C-013 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-013 | R03-C-013 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-014 | R03-C-014 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9021359 | 049.0 | N2 TO BOTTOM OUTLET | 7139 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-CY-014 | R03-C-014 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-014 | R03-C-014 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-014 | R03-C-014 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-015 | R03-C-015 | FLD | 107-BC | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-C-9021314 | 049.0 | PC1 TEMPERED HTF RTN | 6415 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R03 | R03-CV-016 | R03-C-016 | FLD | 107-BC | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9021317 | 049.0 | VC1 COLD HTF RTN | 6422 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R03 | R03-CV-018 | R03-C-018 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-901305 | 049.0 | DISTILLATE VENT LINE | 7186 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-CY-018 | R03-C-018 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-018 | R03-C-018 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-018 | R03-C-018 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-019 | R03-C-019 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021832 | 049.0 | LIQUID INLET | 7231 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-CY-019 | R03-C-019 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-019 | R03-C-019 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-019 | R03-C-019 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-021 | R03-C-021 | FLD | 107-BC | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9021310 | 049.0 | +VE PRESSURE CONTROL | 6802 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R03 | R03-CV-022 | R03-C-022 | FLD | 107-BC | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9021337 | 049.0 | -VE PRESSURE CONTROL | 6823 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R03 | R03-CV-024 | R03-C-024 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9021367 | 049.0 | SOLIDS INLET | 7342 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-CX-024 | R03-C-024 | SGS | 107-BC | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R03 | R03-CY-024 | R03-C-024 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED | 049.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-024 | R03-C-024 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-024 | R03-C-024 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-CV-025 | R03-C-025 | FLD | 107-BC | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9021310 | 049.0 | SOLIDS ADDITION VENT | 7285 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-CX-025 | R03-C-025 | SGS | 107-BC | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R03 | R03-CY-025 | R03-C-025 | FLD | 107-BC | SOLENOID VALVE | RACK MOUNTED | 049.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R03 | R03-ZSC-025 | R03-C-025 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 049.0 | SOLIDS ADDITION VENT | -: -; -: -; REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-ZSO-025 | R03-C-025 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 049.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-DIC-001 | R03-D-001 | PCS | 107-BC | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R03 | R03-DS-001 | R03-D-001 | MCC | 107-BC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R03 | R03-DY-001 | R03-D-001 | MCC | 107-BC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R03 | R03-DYC-001 | R03-D-001 | MCC | 107-BC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 049.0 | JACKET PUMP | 8728 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R03 | R03-HS-002 | R03-H-002 | FLD | 107-BC | SWITCH - HAND OP. | ADJ TO R03 | 049.0 | CRASH COOL | 6696 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R03 | R03-HV-008 | R03-H-008 | FLD | 107-BC | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028622 | 049.0 | N2 PRESSURE SELECT | 7471 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R03 | R03-HZSC-008 | R03-H-008 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R03 | R03-HZSO-008 | R03-H-008 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R03 | R03-HV-009 | R03-H-009 | FLD | 107-BC | HAND VALVE | 25-P-PT1A-0-9021362 | 049.0 | AUX. INLET | 7383 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-HZSC-009 | R03-H-009 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-HZSO-009 | R03-H-009 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R03 | R03-HV-010 | R03-H-010 | FLD | 107-BC | HAND VALVE | 40-P-PT1A-0-9021823 | 049.0 | REAGENTS INLET | 7363 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R03 | R03-HZSC-010 | R03-H-010 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-HZSO-010 | R03-H-010 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-HV-012 | R03-H-012 | FLD | 107-BC | HAND VALVE | 25-P-PT1A-0-9021822 | 049.0 | SOLVENTS INLET | 7384 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-HZSC-012 | R03-H-012 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-HZSO-012 | R03-H-012 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R03 | R03-HV-013 | R03-H-013 | FLD | 107-BC | HAND VALVE | 40-P-PT1A-0-9021823 | 049.0 | SLURRIES INLET | 7440 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R03 | R03-HZSC-013 | R03-H-013 | FLD | 107-BC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-HZSO-013 | R03-H-013 | FLD | 107-BC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R03 | R03-II-002 | R03-I-002 | PCS | 107-BC | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R03 | R03-IT-002 | R03-I-002 | MCC | 107-BC | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 049.0 | AGITATOR CURRENT | 8759 | 0 to 8 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP1 | [6 empty] | 01
R03 | R03-LAH-001 | R03-L-001 | PCS | 107-BC | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L6628; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R03 | R03-LE-001 | R03-L-001 | FLD | 107-BC | ELEMENT - LEVEL | 100-P-PT1A-H-9021303 | 049.0 | HIGH LEVEL | L6628 | Fixed | - | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R03 | R03-LSH-001 | R03-L-001 | CPR | 107-BC | SWITCH - LEVEL - HIGH | 100-P-PT1A-H-9021303 | 049.0 | HIGH LEVEL | 6628 | - | - | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | GP1 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R03 | R03-LG-002 | R03-L-002 | PKG | 107-BC | LEVEL GAUGE | AGITATOR SEAL POT | 049.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R03 | R03-PIC-001 | R03-P-001 | PCS | 107-BC | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: L7015; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-PIT-001 | R03-P-001 | FLD | 107-BC | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9021303 | 049.0 | PRESSURE | 7015 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R03 | R03-PI-002 | R03-P-002 | PCS | 107-BC | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6646; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R03 | R03-PIT-002 | R03-P-002 | FLD | 107-BC | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9021303 | 049.0 | PRESSURE | 6646 | -1 to 2.3 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R03 | R03-PAH-003 | R03-P-003 | PCS | 107-BC | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-PSH-003 | R03-P-003 | FLD | 107-BC | SWITCH - PRESSURE - DIAPHRAGM - HI | 100-P-PT1A-H-9021303 | 049.0 | HIGH PRESSURE | 6647 | set @ 2.2 barg | +/- 1% | REF | By request | C |  | I.S | DI |  |  | 32 | GP1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R03 | R03-PI-004 | R03-P-004 | FLD | 107-BC | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-0-9021330 | 049.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R03 | R03-PI-007 | R03-P-007 | FLD | 107-BC | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029315 | 049.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R03 | R03-PI-008 | R03-P-008 | FLD | 107-BC | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9021325 | 049.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R03 | R03-PSV-012 | R03-P-012 | FLD | 107-BC | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9021355 | 049.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R03 | R03-PSV-013 | R03-P-013 | FLD | 107-BC | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021353 | 049.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R03 | R03-PSV-014 | R03-P-014 | FLD | 107-BC | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021354 | 049.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R03 | R03-PRV-015 | R03-P-015 | FLD | 107-BC | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028621 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R03 | R03-PI-016 | R03-P-016 | PKG | 107-BC | PRESSURE GAUGE | AGITATOR SEAL POT | 049.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 25 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R03 | R03-SE-001 | R03-S-001 | PKG | 107-BC | ELEMENT - SPEED | AGITATOR SHAFT | 049.0 | AGITATOR | L6942 | 0 to 153 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R03 | R03-SI-001A | R03-S-001 | PCS | 107-BC | INDICATOR - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-SI-001B | R03-S-001 | FLD | 107-BC | INDICATOR - SPEED | ADJ TO R03 AGITATOR | 049.0 | AGITATOR | 6942 | 0 to 200 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R03 | R03-DS-002 | R03-S-002 | MCC | 107-BC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R03 | R03-DY-002 | R03-S-002 | MCC | 107-BC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R03 | R03-DYC-002 | R03-S-002 | MCC | 107-BC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 049.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R03 | R03-SC-002 | R03-S-002 | MCC | 107-BC | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 049.0 | AGITATOR | 8759 | 0 to 160 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP1 |  |  |  |  | SET Min 31rpm & Max 153 rpm |  | 01
R03 | R03-SIC-002 | R03-S-002 | PCS | 107-BC | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | PKG: L8757; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TE-001 | R03-T-001 | PKG | 107-BC | ELEMENT - TEMPERATURE - RTD | WITH R03-CV-001 |  | TEMPERATURE #1 | PKG: L6903; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R03 | R03-TI-001A | R03-T-001 | PCS | 107-BC | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6903; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R03 | R03-TI-001B | R03-T-001 | FLD | 107-BC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R03 | 049.0 | TEMPERATURE #1 | L6903 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R03 | R03-TT-001 | R03-T-001 | PKG | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | TEMPERATURE #1 | 6903 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R03 | R03-TE-002 | R03-T-002 | PKG | 107-BC | ELEMENT - TEMPERATURE - RTD | WITH R03-CV-001 |  | TEMPERATURE #2 | PKG: L6904; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R03 | R03-TI-002A | R03-T-002 | PCS | 107-BC | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6904; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R03 | R03-TI-002B | R03-T-002 | FLD | 107-BC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 049.0 | TEMPERATURE #2 | L6904 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R03 | R03-TT-002 | R03-T-002 | PKG | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | TEMPERATURE #2 | 6904 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R03 | R03-TE-003 | R03-T-003 | PKG | 107-BC | ELEMENT - TEMPERATURE - RTD | R03/N2/100 |  | BAFFLE TEMPERATURE | PKG: L6905; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R03 | R03-TI-003A | R03-T-003 | PCS | 107-BC | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6905; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R03 | R03-TI-003B | R03-T-003 | FLD | 107-BC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 049.0 | BAFFLE TEMPERATURE | L6905 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R03 | R03-TT-003 | R03-T-003 | PKG | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | BAFFLE TEMPERATURE | 6905 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R03 | R03-TE-004 | R03-T-004 | FLD | 107-BC | ELEMENT - TEMPERATURE - RTD | 80-HT--CS3A-D-9021325 |  | JACKET INLET TEMP. | PKG: L6906; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TI-004A | R03-T-004 | PCS | 107-BC | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6906; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TI-004B | R03-T-004 | FLD | 107-BC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 049.0 | JACKET INLET TEMP. | L6906 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R03 | R03-TT-004 | R03-T-004 | FLD | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | JACKET INLET TEMP. | 6906 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R03 | R03-TE-005 | R03-T-005 | FLD | 107-BC | ELEMENT - TEMPERATURE - RTD | 100-P-PT1A-H-9021303 |  | PC1 INLET TEMPERATURE | PKG: L6525; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TI-005 | R03-T-005 | PCS | 107-BC | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R03 | R03-TT-005 | R03-T-005 | FLD | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | PC1 INLET TEMPERATURE | 6525 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R03 | R03-TI-005A | R03-T-005A | [6 empty] | PKG: L6525; REQ: By request
R03 | R03-TE-006 | R03-T-006 | FLD | 107-BC | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9021310 |  | VC1 OFF GAS TEMPERATURE | PKG: L6526; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R03 | R03-TI-006A | R03-T-006 | PCS | 107-BC | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6526; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R03 | R03-TI-006B | R03-T-006 | FLD | 107-BC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R03 | 049.0 | VC1 OFF GAS TEMPERATURE | L6526 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R03 | R03-TT-006 | R03-T-006 | FLD | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | VC1 OFF GAS TEMPERATURE | 6526 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R03 | R03-TE-007 | R03-T-007 | FLD | 107-BC | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9021317 |  | VC1 HTF RTN TEMPERATURE | PKG: L6527; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TIC-007 | R03-T-007 | PCS | 107-BC | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | PKG: L6527; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TT-007 | R03-T-007 | FLD | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | VC1 HTF RTN TEMPERATURE | 6527 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R03 | R03-TE-008 | R03-T-008 | FLD | 107-BC | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-C-9021314 |  | PC1 HTF RTN TEMPERATURE | PKG: L6528; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TIC-008 | R03-T-008 | PCS | 107-BC | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | PKG: L6528; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TT-008 | R03-T-008 | FLD | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | PC1 HTF RTN TEMPERATURE | 6528 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R03 | R03-TE-009 | R03-T-009 | FLD | 107-BC | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-H-9021302 |  | DISTILLATE RTN TEMPERATURE | PKG: L6529; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TI-009A | R03-T-009 | PCS | 107-BC | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TI-009B | R03-T-009 | FLD | 107-BC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 049.0 | DISTILLATE RTN TEMPERATURE | L6529 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R03 | R03-TT-009 | R03-T-009 | FLD | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | DISTILLATE RTN TEMPERATURE | 6529 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R03 | R03-TE-010 | R03-T-010 | FLD | 107-BC | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9021324 |  | OUTLET TEMPERATURE | PKG: L6530; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TI-010A | R03-T-010 | PCS | 107-BC | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6530; REQ: By request |  |  | 0 | [7 empty] | 01
R03 | R03-TI-010B | R03-T-010 | FLD | 107-BC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R03 | 049.0 | OUTLET TEMPERATURE | L6530 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R03 | R03-TT-010 | R03-T-010 | FLD | 107-BC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 049.0 | OUTLET TEMPERATURE | 6530 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R03 | R03-YA-001 | R03-Y-001 | PCS | 107-BC | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R03 | R03-YS-001 | R03-Y-001 | FUT | 107-BC | COMMON ALARM | R03 GAS SEAL ASSEMBLY | 049.0 | AGITATOR SEAL COMMON ALARM | PKG: 8675; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R04 | R04-AG-001 | R04-A-001 | PKG | 107-BD | SPEED MOORE DISPLAY |  |  |  | PKG: L6943; REF: REF; REQ: By request | [10 empty] | 34
R04 | R04-BD-001 | R04-B-001 | FLD | 107-BD | RUPTURE DISC | 100-P-PT1A-H-9021403 | 050.0 | BURSTING DISC | 6737 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R04 | R04-YI-001 | R04-B-001 | PCS | 107-BD | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-CV-001 | R04-C-001 | PKG | 107-BD | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R04/K/100 | 050.0 | BOTTOM OUTLET VALVE | 8788 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R04 | R04-CY-001 | R04-C-001 | PKG | 107-BD | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R04 | R04-ZSC-001 | R04-C-001 | PKG | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R04 | R04-ZSO-001 | R04-C-001 | PKG | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R04 | R04-CV-004 | R04-C-004 | FLD | 107-BD | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9021430 | 050.0 | NITROGEN SUPPLY | 6782 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R04 | R04-CV-005 | R04-C-005 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021411 | 050.0 | SCRUBBER 01 | 7187 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-CY-005 | R04-C-005 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-005 | R04-C-005 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-005 | R04-C-005 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-006 | R04-C-006 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021410 | 050.0 | SCRUBBER 02 | 7188 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-CY-006 | R04-C-006 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-006 | R04-C-006 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-006 | R04-C-006 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-007 | R04-C-007 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9021438 | 050.0 | PROCESS VACUUM | 7315 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-CY-007 | R04-C-007 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-007 | R04-C-007 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-007 | R04-C-007 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-008 | R04-C-008 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9021437 | 050.0 | HOUSE VACUUM | 7262 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-CY-008 | R04-C-008 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-008 | R04-C-008 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-008 | R04-C-008 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-009 | R04-C-009 | FLD | 107-BD | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029418 | 050.0 | COLD HTF SUPPLY | 7532 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R04 | R04-CY-009 | R04-C-009 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-009 | R04-C-009 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-009 | R04-C-009 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-010 | R04-C-010 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029157 | 050.0 | HOT HTF SUPPLY | 7512 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R04 | R04-ZSC-010 | R04-C-010 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-010 | R04-C-010 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-011 | R04-C-011 | FLD | 107-BD | GLOBE VALVE - CONTROL - F.C. | 50-HT-CS3A-D-9021423 | 050.0 | HOT HTF RTN | 6373 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R04 | R04-CV-012 | R04-C-012 | FLD | 107-BD | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9021456 | 050.0 | COLD HTF RTN | 6385 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R04 | R04-CV-013 | R04-C-013 | FLD | 107-BD | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9021425 | 050.0 | DUAL JACKET | 7504 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R04 | R04-CY-013 | R04-C-013 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-013 | R04-C-013 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-013 | R04-C-013 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-014 | R04-C-014 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9021459 | 050.0 | N2 TO BOTTOM OUTLET | 7140 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-CY-014 | R04-C-014 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-014 | R04-C-014 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-014 | R04-C-014 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-015 | R04-C-015 | FLD | 107-BD | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-C-9021414 | 050.0 | PC1 TEMPERED HTF RTN | 6416 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R04 | R04-CV-016 | R04-C-016 | FLD | 107-BD | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9021417 | 050.0 | VC1 COLD HTF RTN | 6423 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R04 | R04-CV-018 | R04-C-018 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021405 | 050.0 | DISTILLATE VENT LINE | 7189 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-CY-018 | R04-C-018 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-018 | R04-C-018 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-018 | R04-C-018 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-019 | R04-C-019 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021863 | 050.0 | LIQUID INLET | 7232 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-CY-019 | R04-C-019 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-019 | R04-C-019 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-019 | R04-C-019 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-021 | R04-C-021 | FLD | 107-BD | V-BALL VALVE - CONTROL - F.C. | 25-P-PT1A-0-9021410 | 050.0 | +VE PRESSURE CONTROL | 6803 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R04 | R04-CV-022 | R04-C-022 | FLD | 107-BD | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9021437 | 050.0 | -VE PRESSURE CONTROL | 6824 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R04 | R04-CV-024 | R04-C-024 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-C-9021467 | 050.0 | SOLIDS INLET | 7343 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-CX-024 | R04-C-024 | SGS | 107-BD | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R04 | R04-CY-024 | R04-C-024 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED | 050.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-024 | R04-C-024 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-024 | R04-C-024 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-025 | R04-C-025 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9021410 | 050.0 | SOLIDS ADDITION VENT | 7286 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-CX-025 | R04-C-025 | SGS | 107-BD | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R04 | R04-CY-025 | R04-C-025 | FLD | 107-BD | SOLENOID VALVE | RACK MOUNTED | 050.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-025 | R04-C-025 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-025 | R04-C-025 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 050.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-026 | R04-C-026 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 40-P-SS1C-0-9021470 | 050.0 | VENT | 7441 | - | - | REF | REQ | F | [7 empty] | XOMOX TUFLIN | R202 | KV0007/P1 |  |  |  | 01
R04 | R04-CY-026 | R04-C-026 | FLD | 107-BD | SOLENOID VALVE |  | 050.0 |  | -: -; -: -; I.S: I.S |  |  |  | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-026 | R04-C-026 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 050.0 |  | -: -; -: -; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-026 | R04-C-026 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 050.0 |  | -: -; -: -; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-CV-027 | R04-C-027 | FLD | 107-BD | BALL VALVE - ON/OFF - F.C. | 15-P-SS1U-0-9028743 | 050.0 | 2 BAR N2 SUPPLY | 12145 | - | - | REF | REQ | F | [7 empty] | WORCESTER |  | KV0017/P |  |  |  | 01
R04 | R04-CY-027 | R04-C-027 | FLD | 107-BD | SOLENOID VALVE |  | 050.0 |  | -: -; -: -; I.S: I.S |  |  |  | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R04 | R04-ZSC-027 | R04-C-027 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 050.0 |  | -: -; -: -; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-ZSO-027 | R04-C-027 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 050.0 |  | -: -; -: -; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-DIC-001 | R04-D-001 | PCS | 107-BD | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R04 | R04-DS-001 | R04-D-001 | MCC | 107-BD | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R04 | R04-DY-001 | R04-D-001 | MCC | 107-BD | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R04 | R04-DYC-001 | R04-D-001 | MCC | 107-BD | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 050.0 | JACKET PUMP | 8730 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R04 | R04-FAL-001 | R04-F-001 | FLD | 107-BD | ALARM - FLOW - LOW | DELETED | 050.0 | N2 FLOW | PKG: 12146; -: -; -: - | [8 empty] | DELETED |  | 02
R04 | R04-FI-001 | R04-F-001 | FLD | 107-BD | INDICATOR - FLOW | DELETED | 050.0 | N2 FLOW | 12146 | - | - | REF | REQ | C | [7 empty] | KROHNE | DK32 | KF0027/P2 |  | DELETED |  | 02
R04 | R04-FSL-001 | R04-F-001 | [5 empty] | H2 VENT PURGE LOW N2 FLOW | I.S: I.S; DI: DI |  |  |  | GP1 | KROHNE | DK32 |  | TI702-SP-5171 | Added 19-09-2018
R04 | R04-FAL-002 | R04-F-002 | PCS | 107-BD | NITROGEN LOW FLOW |  | 050.0 | HYDROGEN VENT PURGE | PKG: 14824; REQ: By request | [10 empty] | 02
R04 | R04-FIT-002 | R04-F-002 | FLD | 107-BD | FLOW TRANSMITTER | 15-N-SS1U-0-9028743 | 050.0 | HYDROGEN VENT PURGE | 14824 | 0 to 25 ml/min | +/-1% |  | By request |  |  | I.S | AI |  |  |  | GP1 | KHRONE | H250/RR/M9S/ESK-EX | KF0027/P6 | TI702-SP-5098 |  |  | 02
R04 | R04-FIAL-003 | R04-F-003 | FLD | 107-BD | FLOW INDICATOR - ALARM LOW | R04 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LOW FLOW ALARM | REQ: By request | [10 empty] | 52
R04 | R04-FISL-003 | R04-F-003 | FLD | 107-BD | FLOW INDICATOR - SWITCH LOW | R04 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LOW FLOW ALARM | -: 1 to 10 Nl/min N2; REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 | GP1 | KROHNE / PEPPERL + FUCHS | DK 800 / RC10-14-N3 |  | TI702-SP-5087 | LOW RANGE FLOW |  | 52
R04 | R04-FIAH-004 | R04-F-004 | PCS | 107-BD | FLOW INDICATOR - ALARM HIGH | R04 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL HIGH FLOW ALARM | REQ: By request | [10 empty] | 52
R04 | R04-FISH-004 | R04-F-004 | FLD | 107-BD | FLOW INDICATOR - SWITCH HIGH | R04 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL HIGH FLOW ALARM | -: 1 to 10 Nl/min N2; REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 | GP1 | KROHNE / PEPPERL + FUCHS | DK 800 / RC15-14-N3 |  | TI702-SP-5088 | HIGH RANGE FLOW |  | 52
R04 | R04-HS-002 | R04-H-002 | FLD | 107-BD | SWITCH - HAND OP. | ADJ TO R04 | 050.0 | CRASH COOL | 6990 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R04 | R04-HV-008 | R04-H-008 | FLD | 107-BD | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028653 | 050.0 | N2 PRESSURE SELECT | 7472 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R04 | R04-HZSC-008 | R04-H-008 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R04 | R04-HZSO-008 | R04-H-008 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R04 | R04-HV-009 | R04-H-009 | FLD | 107-BD | HAND VALVE | 25-P-PT1A-0-9021462 | 050.0 | AUX. INLET | 7385 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-HZSC-009 | R04-H-009 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HZSO-009 | R04-H-009 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | I.S: I.S |  |  | 0 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HV-010 | R04-H-010 | FLD | 107-BD | HAND VALVE | 40-P-PT1A-0-9021863 | 050.0 | REAGENTS INLET | 7378 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-HZSC-010 | R04-H-010 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HZSO-010 | R04-H-010 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HV-011 | R04-H-011 | FLD | 107-BD | HAND VALVE | DELETED | 050.0 | DELETED | 7441 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | DELETED |  | 01
R04 | R04-HZSC-011 | R04-H-011 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | DELETED |  | DELETED | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | DELETED |  | 01
R04 | R04-HZSO-011 | R04-H-011 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | DELETED |  | DELETED | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | DELETED |  | 01
R04 | R04-HV-012 | R04-H-012 | FLD | 107-BD | HAND VALVE | 25-P-PT1A-0-9021859 | 050.0 | REAGENTS INLET | 7386 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-HZSC-012 | R04-H-012 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HZSO-012 | R04-H-012 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R04 | R04-HV-013 | R04-H-013 | FLD | 107-BD | HAND VALVE | 40-P-PT1A-0-9021863 | 050.0 | SLURRIES INLET | 7442 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R04 | R04-HZSC-013 | R04-H-013 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HZSO-013 | R04-H-013 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HV-015 | R04-H-015 | FLD | 107-BD | HAND VALVE | 40-P-PT1A-0-9021412 | 050.0 | ACID SCRUBBER | PKG: 14820; -: 0 to 100 % |  |  |  |  | XOMOX TUFLIN | R202 |  |  |  |  | 02
R04 | R04-HZSC-015 | R04-H-015 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 050.0 | CLOSED | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HZSO-015 | R04-H-015 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 050.0 | OPEN | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HV-016 | R04-H-016 | FLD | 107-BD | HAND VALVE | 40-P-PT1A-0-9021411 | 050.0 | CAUSTIC SCRUBBER | PKG: 14821; -: 0 to 100 % |  |  |  |  | XOMOX TUFLIN | R202 |  |  |  |  | 02
R04 | R04-HZSC-016 | R04-H-016 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 050.0 | CLOSED | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HZSO-016 | R04-H-016 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 050.0 | OPEN | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HV-017 | R04-H-017 | FLD | 107-BD | HAND VALVE | 40-P-PT1A-0-9021438 | 050.0 | PROCESS VACUUM | PKG: 14822; -: 0 to 100 % |  |  |  |  | XOMOX TUFLIN | R202 |  |  |  |  | 02
R04 | R04-HZSC-017 | R04-H-017 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 050.0 | CLOSED | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HZSO-017 | R04-H-017 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 050.0 | OPEN | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HV-018 | R04-H-018 | FLD | 107-BD | HAND VALVE | 40-P-PT1A-0-9021437 | 050.0 | HOUSE VACUUM | PKG: 14823; -: 0 to 100 % |  |  |  |  | XOMOX TUFLIN | R202 |  |  |  |  | 02
R04 | R04-HZSC-018 | R04-H-018 | FLD | 107-BD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 050.0 | CLOSED | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-HZSO-018 | R04-H-018 | FLD | 107-BD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 050.0 | OPEN | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R04 | R04-II-002 | R04-I-002 | PCS | 107-BD | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-IT-002 | R04-I-002 | MCC | 107-BD | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 050.0 | AGITATOR CURRENT | 8760 | 0 to 5 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP1 | [6 empty] | 01
R04 | R04-LAH-001 | R04-L-001 | PCS | 107-BD | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L6629; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R04 | R04-LE-001 | R04-L-001 | FLD | 107-BD | ELEMENT - LEVEL | 100-P-PT1A-H-9021403 | 050.0 | HIGH LEVEL | L6629 | Fixed | - | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R04 | R04-LSH-001 | R04-L-001 | CPR | 107-BD | SWITCH - LEVEL - HIGH | 100-P-PT1A-H-9021403 | 050.0 | HIGH LEVEL | 6629 | - | - | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | GP1 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R04 | R04-LG-002 | R04-L-002 | PKG | 107-BD | LEVEL GAUGE | AGITATOR SEAL POT | 050.0 | AGITATOR SEAL POT LEVEL | -: Fixed; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R04 | R04-PIC-001 | R04-P-001 | PCS | 107-BD | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-PIT-001 | R04-P-001 | FLD | 107-BD | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9021403 | 050.0 | PRESSURE | 7016 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R04 | R04-PI-002 | R04-P-002 | PCS | 107-BD | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6649; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R04 | R04-PIT-002 | R04-P-002 | FLD | 107-BD | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9021403 | 050.0 | PRESSURE | 6649 | -1 to 2.3 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R04 | R04-PAH-003 | R04-P-003 | PCS | 107-BD | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REQ: By request |  |  | 0 |  | DELTA CONTROLS LTD | [5 empty] | 01
R04 | R04-PSH-003 | R04-P-003 | FLD | 107-BD | SWITCH - PRESSURE - DIAPHRAGM - HI | 100-P-PT1A-H-9021403 | 050.0 | HIGH PRESSURE | 6650 | set @ 2.2 barg | +/- 1% | REF | By request | C |  | I.S | DI |  |  | 32 | GP1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R04 | R04-PI-004 | R04-P-004 | FLD | 107-BD | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9021430 | 050.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R04 | R04-PI-007 | R04-P-007 | FLD | 107-BD | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9021424 | 050.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R04 | R04-PI-008 | R04-P-008 | FLD | 107-BD | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9021425 | 050.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R04 | R04-PSV-012 | R04-P-012 | FLD | 107-BD | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9021455 | 050.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R04 | R04-PSV-013 | R04-P-013 | FLD | 107-BD | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021453 | 050.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R04 | R04-PSV-014 | R04-P-014 | FLD | 107-BD | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021454 | 050.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R04 | R04-PRV-015 | R04-P-015 | FLD | 107-BD | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028652 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R04 | R04-PI-016 | R04-P-016 | PKG | 107-BD | PRESSURE GAUGE | AGITATOR SEAL POT | 050.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 52
R04 | R04-PRV-017 | R04-P-017 | FLD | 107-BD | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028652 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 6.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | GP1 | BURGMANN | Part of gas seal system |  |  |  |  | 52
R04 | R04-PIAL-018 | R04-P-018 | PCS | 107-BD | PRESSURE GAUGE - ALARM LOW | R04 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LP ALARM | -: SET @5BARG; REQ: By request; F: C |  |  |  | GP1 | [6 empty] | 52
R04 | R04-PISL-018 | R04-P-018 | FLD | 107-BD | PRESSURE GAUGE - SWITCH LOW | R04 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LP ALARM |  | SET @5BARG |  | REF | By request | C |  | I.S | DI |  |  | 0 | GP1 | PEPPERL + FUCHS | SJ2-N |  | TI702-SP-5099 |  |  | 52
R04 | R04-RO-001 | R04-R-001 | DEL | 107-BD | RESTRICTION ORIFICE PLATE | DELETED |  | DELETED | [11 empty] | 0 | [5 empty] | DELETED |  | 01 | bar: -
R04 | R04-SE-001 | R04-S-001 | PKG | 107-BD | ELEMENT - SPEED | AGITATOR SHAFT | 050.0 | AGITATOR | L6943 | 0 to 215 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R04 | R04-SI-001A | R04-S-001 | PCS | 107-BD | INDICATOR - SPEED |  |  | AGITATOR | PKG: L6943; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-SI-001B | R04-S-001 | FLD | 107-BD | INDICATOR - SPEED | ADJ TO R04 AGITATOR | 050.0 | AGITATOR | 6943 | 0 to 220 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R04 | R04-DS-002 | R04-S-002 | MCC | 107-BD | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R04 | R04-DY-002 | R04-S-002 | MCC | 107-BD | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R04 | R04-DYC-002 | R04-S-002 | MCC | 107-BD | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 050.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R04 | R04-SC-002 | R04-S-002 | MCC | 107-BD | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 050.0 | AGITATOR | 8760 | 0 to 220 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP1 |  |  |  |  | SET Min 43 rpm & Max 215 rpm |  | 01
R04 | R04-SIC-002 | R04-S-002 | PCS | 107-BD | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | PKG: L6943; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TE-001 | R04-T-001 | PKG | 107-BD | ELEMENT - TEMPERATURE - RTD | WITH R04-CV-001 |  | TEMPERATURE #1 | PKG: L6907; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R04 | R04-TI-001A | R04-T-001 | PCS | 107-BD | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6907; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R04 | R04-TI-001B | R04-T-001 | FLD | 107-BD | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R04 | 050.0 | TEMPERATURE #1 | L6907 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R04 | R04-TT-001 | R04-T-001 | PKG | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | TEMPERATURE #1 | 6907 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R04 | R04-TE-002 | R04-T-002 | PKG | 107-BD | ELEMENT - TEMPERATURE - RTD | WITH R04-CV-001 |  | TEMPERATURE #2 | PKG: L6908; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R04 | R04-TI-002A | R04-T-002 | PCS | 107-BD | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6908; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R04 | R04-TI-002B | R04-T-002 | FLD | 107-BD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 050.0 | TEMPERATURE #2 | L6908 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R04 | R04-TT-002 | R04-T-002 | PKG | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | TEMPERATURE #2 | 6908 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R04 | R04-TE-003 | R04-T-003 | PKG | 107-BD | ELEMENT - TEMPERATURE - RTD | R04/N2/100 |  | BAFFLE TEMPERATURE | PKG: L6909; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R04 | R04-TI-003A | R04-T-003 | PCS | 107-BD | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6909; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R04 | R04-TI-003B | R04-T-003 | FLD | 107-BD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 050.0 | BAFFLE TEMPERATURE | L6909 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R04 | R04-TT-003 | R04-T-003 | PKG | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | BAFFLE TEMPERATURE | 6909 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R04 | R04-TE-004 | R04-T-004 | FLD | 107-BD | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9021425 |  | JACKET INLET TEMP. | PKG: L6910; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TI-004A | R04-T-004 | PCS | 107-BD | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6910; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TI-004B | R04-T-004 | FLD | 107-BD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 050.0 | JACKET INLET TEMP. | L6910 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | [5 empty] | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R04 | R04-TT-004 | R04-T-004 | FLD | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | JACKET INLET TEMP. | 6910 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R04 | R04-TE-005 | R04-T-005 | FLD | 107-BD | ELEMENT - TEMPERATURE - RTD | 100-P-PT1A-H-9021403 |  | PC1 INLET TEMPERATURE | PKG: L6531; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TI-005 | R04-T-005 | PCS | 107-BD | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R04 | R04-TT-005 | R04-T-005 | FLD | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | PC1 INLET TEMPERATURE | 6531 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R04 | R04-TI-005A | R04-T-005A | [6 empty] | PKG: L6531; REQ: By request
R04 | R04-TE-006 | R04-T-006 | FLD | 107-BD | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9021410 |  | VC1 OFF GAS TEMPERATURE | PKG: L6532; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R04 | R04-TI-006A | R04-T-006 | PCS | 107-BD | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6532; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R04 | R04-TI-006B | R04-T-006 | FLD | 107-BD | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R04 | 050.0 | VC1 OFF GAS TEMPERATURE | L6532 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R04 | R04-TT-006 | R04-T-006 | FLD | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | VC1 OFF GAS TEMPERATURE | 6532 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R04 | R04-TE-007 | R04-T-007 | FLD | 107-BD | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9021417 |  | VC1 HTF RTN TEMPERATURE | PKG: L6533; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TIC-007 | R04-T-007 | PCS | 107-BD | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | PKG: L6533; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TT-007 | R04-T-007 | FLD | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | VC1 HTF RTN TEMPERATURE | 6533 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R04 | R04-TE-008 | R04-T-008 | FLD | 107-BD | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-C-9021414 |  | PC1 HTF RTN TEMPERATURE | PKG: L6534; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TIC-008 | R04-T-008 | PCS | 107-BD | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | PKG: L6534; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TT-008 | R04-T-008 | FLD | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | PC1 HTF RTN TEMPERATURE | 6534 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R04 | R04-TE-009 | R04-T-009 | FLD | 107-BD | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-C-9021402 |  | DISTILLATE RTN TEMP. | PKG: L6535; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TI-009A | R04-T-009 | PCS | 107-BD | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | PKG: L6535; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TI-009B | R04-T-009 | FLD | 107-BD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 050.0 | DISTILLATE RTN TEMP. | L6535 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R04 | R04-TT-009 | R04-T-009 | FLD | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | DISTILLATE RTN TEMP. | 6535 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R04 | R04-TE-010 | R04-T-010 | FLD | 107-BD | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9021424 |  | OUTLET TEMPERATURE | PKG: L6536; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TI-010A | R04-T-010 | PCS | 107-BD | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6536; REQ: By request |  |  | 0 | [7 empty] | 01
R04 | R04-TI-010B | R04-T-010 | FLD | 107-BD | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R04 | 050.0 | OUTLET TEMPERATURE | L6536 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R04 | R04-TT-010 | R04-T-010 | FLD | 107-BD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 050.0 | OUTLET TEMPERATURE | 6536 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R04 | R04-YA-001 | R04-Y-001 | PCS | 107-BD | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R04 | R04-YS-001 | R04-Y-001 | FUT | 107-BD | COMMON ALARM | R04 GAS SEAL ASSEMBLY | 050.0 | AGITATOR SEAL COMMON ALARM | PKG: 8678; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP1 |  |  |  |  | FUTURE(PCS I/O INSTALLED) |  | 01
R05 | R05-AG-001 | R05-A-001 | PKG | 107-BE | SPEED MOORE DISPLAY |  | 051.0 | AGITATOR | PKG: L6945; REF: REF; REQ: By request | [10 empty] | 34
R05 | R05-BD-001 | R05-B-001 | FLD | 107-BE | RUPTURE DISC | 150-P-PT1A-H-9021503 | 051.0 | BURSTING DISC | 6738 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R05 | R05-YI-001 | R05-B-001 | PCS | 107-BE | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-CV-001 | R05-C-001 | PKG | 107-BE | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R05/K/100 | 051.0 | BOTTOM OUTLET VALVE | 8789 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R05 | R05-CY-001 | R05-C-001 | PKG | 107-BE | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R05 | R05-ZSC-001 | R05-C-001 | PKG | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R05 | R05-ZSO-001 | R05-C-001 | PKG | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R05 | R05-CV-004 | R05-C-004 | FLD | 107-BE | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9021530 | 051.0 | NITROGEN SUPPLY | 6783 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R05 | R05-CV-005 | R05-C-005 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021511 | 051.0 | SCRUBBER 01 | 7190 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-CY-005 | R05-C-005 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-005 | R05-C-005 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-005 | R05-C-005 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-006 | R05-C-006 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021510 | 051.0 | SCRUBBER 02 | 7191 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-CY-006 | R05-C-006 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-006 | R05-C-006 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-006 | R05-C-006 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-007 | R05-C-007 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9021538 | 051.0 | PROCESS VACUUM | 7316 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-CY-007 | R05-C-007 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-007 | R05-C-007 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-007 | R05-C-007 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-008 | R05-C-008 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9021537 | 051.0 | HOUSE VACUUM | 7263 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-CY-008 | R05-C-008 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-008 | R05-C-008 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-008 | R05-C-008 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-009 | R05-C-009 | FLD | 107-BE | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029317 | 051.0 | COLD HTF SUPPLY | 7533 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R05 | R05-CY-009 | R05-C-009 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-009 | R05-C-009 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-009 | R05-C-009 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-010 | R05-C-010 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029107 | 051.0 | HOT HTF SUPPLY | 7520 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R05 | R05-ZSC-010 | R05-C-010 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-010 | R05-C-010 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-011 | R05-C-011 | FLD | 107-BE | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9021523 | 051.0 | HOT HTF RTN | 6374 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R05 | R05-CV-012 | R05-C-012 | FLD | 107-BE | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9021556 | 051.0 | COLD HTF RTN | 6386 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R05 | R05-CV-014 | R05-C-014 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9021559 | 051.0 | N2 TO BOTTOM OUTLET | 7141 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-CY-014 | R05-C-014 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-014 | R05-C-014 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-014 | R05-C-014 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-015 | R05-C-015 | FLD | 107-BE | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-C-9021514 | 051.0 | PC1 TEMPERED HTF RTN | 6429 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R05 | R05-CV-016 | R05-C-016 | FLD | 107-BE | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9021517 | 051.0 | VC1 COLD HTF RTN | 6435 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R05 | R05-CV-018 | R05-C-018 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021505 | 051.0 | DISTILLATE VENT LINE | 7192 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-CY-018 | R05-C-018 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-018 | R05-C-018 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-018 | R05-C-018 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-019 | R05-C-019 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021821 | 051.0 | LIQUID INLET | 7233 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-CY-019 | R05-C-019 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-019 | R05-C-019 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-019 | R05-C-019 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-021 | R05-C-021 | FLD | 107-BE | V-BALL VALVE - CONTROL - F.C. | 25-P-PT1A-0-9021510 | 051.0 | +VE PRESSURE CONTROL | 6804 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R05 | R05-CV-022 | R05-C-022 | FLD | 107-BE | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9021537 | 051.0 | -VE PRESSURE CONTROL | 6825 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R05 | R05-CV-024 | R05-C-024 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-0-9021567 | 051.0 | SOLIDS INLET | 7344 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-CX-024 | R05-C-024 | SGS | 107-BE | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R05 | R05-CY-024 | R05-C-024 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED | 051.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-024 | R05-C-024 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-024 | R05-C-024 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-CV-025 | R05-C-025 | FLD | 107-BE | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9021510 | 051.0 | SOLIDS ADDITION VENT | 7287 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-CX-025 | R05-C-025 | SGS | 107-BE | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R05 | R05-CY-025 | R05-C-025 | FLD | 107-BE | SOLENOID VALVE | RACK MOUNTED | 051.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R05 | R05-ZSC-025 | R05-C-025 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-ZSO-025 | R05-C-025 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 051.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-DIC-001 | R05-D-001 | PCS | 107-BE | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R05 | R05-DS-001 | R05-D-001 | MCC | 107-BE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R05 | R05-DY-001 | R05-D-001 | MCC | 107-BE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R05 | R05-DYC-001 | R05-D-001 | MCC | 107-BE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 051.0 | JACKET PUMP | 8732 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R05 | R05-HS-002 | R05-H-002 | FLD | 107-BE | SWITCH - HAND OP. | ADJ TO R05 | 051.0 | CRASH COOL | 6991 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R05 | R05-HV-008 | R05-H-008 | FLD | 107-BE | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028619 | 051.0 | N2 PRESSURE SELECT | 7473 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R05 | R05-HZSC-008 | R05-H-008 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R05 | R05-HZSO-008 | R05-H-008 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R05 | R05-HV-009 | R05-H-009 | FLD | 107-BE | HAND VALVE | 25-P-PT1A-0-9021562 | 051.0 | AUX. INLET | 7387 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-HZSC-009 | R05-H-009 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-HZSO-009 | R05-H-009 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R05 | R05-HV-010 | R05-H-010 | FLD | 107-BE | HAND VALVE | 40-P-PT1A-0-9021821 | 051.0 | REAGENTS INLET | 7364 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R05 | R05-HZSC-010 | R05-H-010 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-HZSO-010 | R05-H-010 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-HV-012 | R05-H-012 | FLD | 107-BE | HAND VALVE | 25-P-PT1A-0-9021820 | 051.0 | SOLVENTS INLET | 7388 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-HZSC-012 | R05-H-012 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-HZSO-012 | R05-H-012 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R05 | R05-HV-013 | R05-H-013 | FLD | 107-BE | HAND VALVE | 40-P-PT1A-0-9021821 | 051.0 | SLURRIES INLET | 7443 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R05 | R05-HZSC-013 | R05-H-013 | FLD | 107-BE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-HZSO-013 | R05-H-013 | FLD | 107-BE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R05 | R05-II-002 | R05-I-002 | PCS | 107-BE | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-IT-002 | R05-I-002 | MCC | 107-BE | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 051.0 | AGITATOR CURRENT | 8761 | 0 to 10 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP1 | [6 empty] | 01
R05 | R05-LI-001 | R05-L-001 | PCS | 107-BE | INDICATOR - LEVEL |  |  | LEVEL | REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-LT-001 | R05-L-001 | FLD | 107-BE | TRANSMITTER - LEVEL | R05/N4/100 | 051.0 | LEVEL | 6639 | 0-1600 litres | +/- 2% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | VEGA | VEGAPULS 63 | KL0028 | TI702-SP-5009 |  |  | 01
R05 | R05-LG-002 | R05-L-002 | PKG | 107-BE | LEVEL GAUGE | AGITATOR SEAL POT | 051.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R05 | R05-PIC-001 | R05-P-001 | PCS | 107-BE | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: L7017; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-PIT-001 | R05-P-001 | FLD | 107-BE | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9021503 | 051.0 | PRESSURE | 7017 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R05 | R05-PI-002 | R05-P-002 | PCS | 107-BE | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6652; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R05 | R05-PIT-002 | R05-P-002 | FLD | 107-BE | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9021503 | 051.0 | PRESSURE | 6652 | -1 to 2.3 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R05 | R05-PAH-003 | R05-P-003 | PCS | 107-BE | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-PSH-003 | R05-P-003 | FLD | 107-BE | SWITCH - PRESSURE - DIAPHRAGM - HI | 150-P-PT1A-H-9021503 | 051.0 | HIGH PRESSURE | L6641 | set @ 2.2 barg | +/- 1% | REF | By request | C |  | I.S | DI |  |  | 32 | GP1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R05 | R05-PI-004 | R05-P-004 | FLD | 107-BE | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9021530 | 051.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R05 | R05-PI-007 | R05-P-007 | FLD | 107-BE | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9021524 | 051.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R05 | R05-PI-008 | R05-P-008 | FLD | 107-BE | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9021525 | 051.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R05 | R05-PSV-012 | R05-P-012 | FLD | 107-BE | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9021555 | 051.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R05 | R05-PSV-013 | R05-P-013 | FLD | 107-BE | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021553 | 051.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R05 | R05-PSV-014 | R05-P-014 | FLD | 107-BE | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021554 | 051.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R05 | R05-PRV-015 | R05-P-015 | FLD | 107-BE | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028618 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R05 | R05-PI-016 | R05-P-016 | PKG | 107-BE | PRESSURE GAUGE | AGITATOR SEAL POT | 051.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R05 | R05-SE-001 | R05-S-001 | PKG | 107-BE | ELEMENT - SPEED | AGITATOR SHAFT | 051.0 | AGITATOR | L6945 | 0 to 118 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R05 | R05-SI-001A | R05-S-001 | PCS | 107-BE | INDICATOR - SPEED |  |  | AGITATOR | PKG: L6945; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-SI-001B | R05-S-001 | FLD | 107-BE | INDICATOR - SPEED | ADJ TO R05 AGITATOR | 051.0 | AGITATOR | 6945 | 0 to 200 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R05 | R05-DS-002 | R05-S-002 | MCC | 107-BE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R05 | R05-DY-002 | R05-S-002 | MCC | 107-BE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R05 | R05-DYC-002 | R05-S-002 | MCC | 107-BE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 051.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R05 | R05-SC-002 | R05-S-002 | MCC | 107-BE | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 051.0 | AGITATOR | 8761 | 0 to 120 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP1 |  |  |  |  | SET Min 24 rpm & Max 118 rpm |  | 01
R05 | R05-SIC-002 | R05-S-002 | PCS | 107-BE | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | PKG: L6945; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TE-001 | R05-T-001 | PKG | 107-BE | ELEMENT - TEMPERATURE - RTD | WITH R05-CV-001 |  | TEMPERATURE #1 | PKG: L6911; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R05 | R05-TI-001A | R05-T-001 | PCS | 107-BE | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6911; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R05 | R05-TI-001B | R05-T-001 | FLD | 107-BE | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R05 | 051.0 | TEMPERATURE #1 | 6911 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R05 | R05-TT-001 | R05-T-001 | PKG | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | TEMPERATURE #1 | L6911 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R05 | R05-TE-002 | R05-T-002 | PKG | 107-BE | ELEMENT - TEMPERATURE - RTD | WITH R05-CV-001 |  | TEMPERATURE #2 | PKG: L6912; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R05 | R05-TI-002A | R05-T-002 | PCS | 107-BE | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6912; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R05 | R05-TI-002B | R05-T-002 | FLD | 107-BE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 051.0 | TEMPERATURE #2 | 6912 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R05 | R05-TT-002 | R05-T-002 | PKG | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | TEMPERATURE #2 | L6912 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R05 | R05-TE-003 | R05-T-003 | PKG | 107-BE | ELEMENT - TEMPERATURE - RTD | R05/N2/150 |  | BAFFLE TEMPERATURE | PKG: L6913; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R05 | R05-TI-003A | R05-T-003 | PCS | 107-BE | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6913; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R05 | R05-TI-003B | R05-T-003 | FLD | 107-BE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 051.0 | BAFFLE TEMPERATURE | 6913 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R05 | R05-TT-003 | R05-T-003 | PKG | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | BAFFLE TEMPERATURE | L6913 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R05 | R05-TE-004 | R05-T-004 | FLD | 107-BE | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9021525 |  | JACKET INLET TEMP. | PKG: L6914; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TI-004A | R05-T-004 | PCS | 107-BE | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6914; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TI-004B | R05-T-004 | FLD | 107-BE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 051.0 | JACKET INLET TEMP. | L6914 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R05 | R05-TT-004 | R05-T-004 | FLD | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | JACKET INLET TEMP. | 6914 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R05 | R05-TE-005 | R05-T-005 | FLD | 107-BE | ELEMENT - TEMPERATURE - RTD | 150-P-PT1A-H-9021503 |  | PC1 INLET TEMPERATURE | PKG: L6537; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TI-005 | R05-T-005 | PCS | 107-BE | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R05 | R05-TT-005 | R05-T-005 | FLD | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | PC1 INLET TEMPERATURE | 6537 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R05 | R05-TI-005A | R05-T-005A | [6 empty] | PKG: L6945; REQ: By request
R05 | R05-TE-006 | R05-T-006 | FLD | 107-BE | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9021510 |  | VC1 OFF GAS TEMPERATURE | PKG: L6538; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R05 | R05-TI-006A | R05-T-006 | PCS | 107-BE | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6538; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R05 | R05-TI-006B | R05-T-006 | FLD | 107-BE | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R05 | 051.0 | VC1 OFF GAS TEMPERATURE | L6538 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R05 | R05-TT-006 | R05-T-006 | FLD | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | VC1 OFF GAS TEMPERATURE | 6538 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R05 | R05-TE-007 | R05-T-007 | FLD | 107-BE | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9021517 |  | VC1 HTF RTN TEMPERATURE | PKG: L6539; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TIC-007 | R05-T-007 | PCS | 107-BE | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | PKG: L6539; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TT-007 | R05-T-007 | FLD | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | VC1 HTF RTN TEMPERATURE | 6539 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R05 | R05-TE-008 | R05-T-008 | FLD | 107-BE | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9021514 |  | PC1 HTF RTN TEMPERATURE | PKG: L6540; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TIC-008 | R05-T-008 | PCS | 107-BE | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | PKG: L6540; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TT-008 | R05-T-008 | FLD | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | PC1 HTF RTN TEMPERATURE | 6540 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R05 | R05-TE-009 | R05-T-009 | FLD | 107-BE | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-C-9021502 |  | DISTILLATE RTN TEMP. | PKG: L6541; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TI-009A | R05-T-009 | PCS | 107-BE | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | PKG: L6541; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TI-009B | R05-T-009 | FLD | 107-BE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 051.0 | DISTILLATE RTN TEMP. | L6541 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R05 | R05-TT-009 | R05-T-009 | FLD | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | DISTILLATE RTN TEMP. | 6541 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R05 | R05-TE-010 | R05-T-010 | FLD | 107-BE | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9021524 |  | OUTLET TEMPERATURE | PKG: L6542; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TI-010A | R05-T-010 | PCS | 107-BE | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6542; REQ: By request |  |  | 0 | [7 empty] | 01
R05 | R05-TI-010B | R05-T-010 | FLD | 107-BE | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R05 | 051.0 | OUTLET TEMPERATURE | L6542 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R05 | R05-TT-010 | R05-T-010 | FLD | 107-BE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 051.0 | OUTLET TEMPERATURE | 6542 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R05 | R05-YA-001 | R05-Y-001 | PCS | 107-BE | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R05 | R05-YS-001 | R05-Y-001 | FUT | 107-BE | COMMON ALARM | R05 GAS SEAL ASSEMBLY | 051.0 | AGITATOR SEAL COMMON ALARM | PKG: 8679; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R06 | R06-AG-001 | R06-A-001 | PKG | 107-BF | SPEED MOORE DISPLAY |  | 052.0 |  | PKG: L6946; REF: REF; REQ: By request | [10 empty] | 34
R06 | R06-BD-001 | R06-B-001 | FLD | 107-BF | RUPTURE DISC | 150-P-PT1A-H-9021603 | 052.0 | BURSTING DISC | 6739 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R06 | R06-YI-001 | R06-B-001 | PCS | 107-BF | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-CV-001 | R06-C-001 | PKG | 107-BF | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R06/K/100 | 052.0 | BOTTOM OUTLET VALVE | 8790 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R06 | R06-CY-001 | R06-C-001 | PKG | 107-BF | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R06 | R06-ZSC-001 | R06-C-001 | PKG | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R06 | R06-ZSO-001 | R06-C-001 | PKG | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R06 | R06-CV-004 | R06-C-004 | FLD | 107-BF | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9021630 | 052.0 | NITROGEN SUPPLY | 6784 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R06 | R06-CV-005 | R06-C-005 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021611 | 052.0 | SCRUBBER 01 | 7251 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-CY-005 | R06-C-005 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-005 | R06-C-005 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-005 | R06-C-005 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-006 | R06-C-006 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021610 | 052.0 | SCRUBBER 02 | 7193 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-CY-006 | R06-C-006 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-006 | R06-C-006 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-006 | R06-C-006 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-007 | R06-C-007 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9021638 | 052.0 | PROCESS VACUUM | 7317 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-CY-007 | R06-C-007 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-007 | R06-C-007 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-007 | R06-C-007 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-008 | R06-C-008 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9021637 | 052.0 | HOUSE VACUUM | 7264 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-CY-008 | R06-C-008 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-008 | R06-C-008 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-008 | R06-C-008 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-009 | R06-C-009 | FLD | 107-BF | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-D-9029420 | 052.0 | COLD HTF SUPPLY | 7534 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R06 | R06-CY-009 | R06-C-009 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-009 | R06-C-009 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-009 | R06-C-009 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-010 | R06-C-010 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029159 | 052.0 | HOT HTF SUPPLY | 7521 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R06 | R06-ZSC-010 | R06-C-010 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-010 | R06-C-010 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-011 | R06-C-011 | FLD | 107-BF | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9021623 | 052.0 | HOT HTF RTN | 6375 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R06 | R06-CV-012 | R06-C-012 | FLD | 107-BF | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9021656 | 052.0 | COLD HTF RTN | 6387 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R06 | R06-CV-013 | R06-C-013 | FLD | 107-BF | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9021625 | 052.0 | DUAL JACKET | 7505 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R06 | R06-CY-013 | R06-C-013 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-013 | R06-C-013 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-013 | R06-C-013 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-014 | R06-C-014 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9021659 | 052.0 | N2 TO BOTTOM OUTLET | 7142 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-CY-014 | R06-C-014 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-014 | R06-C-014 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-014 | R06-C-014 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-015 | R06-C-015 | FLD | 107-BF | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9021614 | 052.0 | PC1 TEMPERED HTF RTN | 6430 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R06 | R06-CV-016 | R06-C-016 | FLD | 107-BF | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9021617 | 052.0 | VC1 COLD HTF RTN | 6436 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R06 | R06-CV-018 | R06-C-018 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021605 | 052.0 | DISTILLATE VENT LINE | 7194 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-CY-018 | R06-C-018 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-018 | R06-C-018 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-018 | R06-C-018 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-019 | R06-C-019 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021861 | 052.0 | LIQUID INLET | 7234 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-CY-019 | R06-C-019 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-019 | R06-C-019 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-019 | R06-C-019 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-021 | R06-C-021 | FLD | 107-BF | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9021610 | 052.0 | +VE PRESSURE CONTROL | 6805 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R06 | R06-CV-022 | R06-C-022 | FLD | 107-BF | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9021637 | 052.0 | -VE PRESSURE CONTROL | 6826 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R06 | R06-CV-024 | R06-C-024 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9021667 | 052.0 | SOLIDS INLET | 7345 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-CX-024 | R06-C-024 | SGS | 107-BF | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R06 | R06-CY-024 | R06-C-024 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED | 052.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-024 | R06-C-024 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. OV VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-024 | R06-C-024 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-025 | R06-C-025 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9021610 | 052.0 | SOLIDS ADDITION VENT | 7289 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-CX-025 | R06-C-025 | SGS | 107-BF | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R06 | R06-CY-025 | R06-C-025 | FLD | 107-BF | SOLENOID VALVE | RACK MOUNTED | 052.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R06 | R06-ZSC-025 | R06-C-025 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-025 | R06-C-025 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 052.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-CV-026 | R06-C-026 | FLD | 107-BF | BALL VALVE - ON/OFF - F.C. | 40-P-SS1C-0-9021610 | 052.0 | VENT | 7444 | - | - | REF | REQ | F | [7 empty] | XOMOX TUFLIN | R202 | KV0007/P1 |  |  |  | 01
R06 | R06-CY-026 | R06-C-026 |  | 107-BF | SOLENOID VALVE | RACK MOUNTED |  | H2 VENT VALVE | I.S: I.S; DI: DO |  |  |  | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004
R06 | R06-ZSC-026 | R06-C-026 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 052.0 |  | -: -; -: -; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-ZSO-026 | R06-C-026 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 052.0 |  | -: -; -: -; I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-DIC-001 | R06-D-001 | PCS | 107-BF | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R06 | R06-DS-001 | R06-D-001 | MCC | 107-BF | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R06 | R06-DY-001 | R06-D-001 | MCC | 107-BF | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 |  |  |  | TI702-SP-5048 |  |  | 01
R06 | R06-DYC-001 | R06-D-001 | MCC | 107-BF | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 052.0 | JACKET PUMP | 8734 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R06 | R06-FIAL-003 | R06-F-003 | FLD | 107-BF | FLOW INDICATOR - ALARM LOW | R06 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LOW FLOW ALARM | REQ: By request | [10 empty] | 52
R06 | R06-FISL-003 | R06-F-003 | FLD | 107-BF | SWITCH - LOW FLOW | R06 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LOW N2 FLOW |  | 1 to 10 Nl/min N2 |  | REF | By request | C |  | I.S | DI |  |  | 0 | GP1 | KROHNE / PEPPERL + FUCHS | DK 800 / RC10-14-N3 |  | TI702-SP-5087 | LOW RANGE FLOW |  | 52
R06 | R06-FIAH-004 | R06-F-004 | PCS | 107-BF | FLOW INDICATOR - ALARM HIGH | R06 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL HIGH FLOW ALARM | REQ: By request | [10 empty] | 52
R06 | R06-FISH-004 | R06-F-004 | FLD | 107-BF | SWITCH - HIGH FLOW | R06 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL HIGH N2 FLOW |  | 1 to 10 Nl/min N2 |  | REF | By request | C |  | I.S | DI |  |  | 0 | GP1 | KROHNE / PEPPERL + FUCHS | DK 800 / RC15-14-N3 |  | TI702-SP-5088 | HIGH RANGE FLOW |  | 52
R06 | R06-HS-002 | R06-H-002 | FLD | 107-BF | SWITCH - HAND OP. | ADJ TO R06 | 052.0 | CRASH COOL | 6992 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R06 | R06-HV-008 | R06-H-008 | FLD | 107-BF | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028650 | 052.0 | N2 PRESSURE SELECT | 7474 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R06 | R06-HZSC-008 | R06-H-008 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R06 | R06-HZSO-008 | R06-H-008 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R06 | R06-HV-009 | R06-H-009 | FLD | 107-BF | HAND VALVE | 25-P-PT1A-0-9021662 | 052.0 | AUX. INLET | 7389 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-HZSC-009 | R06-H-009 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HZSO-009 | R06-H-009 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R06 | R06-HV-010 | R06-H-010 | FLD | 107-BF | HAND VALVE | 40-P-PT1A-0-9021861 | 052.0 | REAGENTS INLET | 7365 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R06 | R06-HZSC-010 | R06-H-010 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HZSO-010 | R06-H-010 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HV-011 | R06-H-011 | FLD | 107-BF | HAND VALVE | DELETED | 052.0 | DELETED | 7444 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | DELETED |  | 01
R06 | R06-HZSC-011 | R06-H-011 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | DELETED |  | DELETED | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | DELETED |  | 01
R06 | R06-HZSO-011 | R06-H-011 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | DELETED |  | DELETED | I.S: I.S; DI: DI |  |  | 31 | GP1 |  |  |  |  | DELETED |  | 01
R06 | R06-HV-012 | R06-H-012 | FLD | 107-BF | HAND VALVE | 25-P-PT1A-0-9021831 | 052.0 | SOLVENTS INLET | 7390 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-HZSC-012 | R06-H-012 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HZSO-012 | R06-H-012 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R06 | R06-HV-013 | R06-H-013 | FLD | 107-BF | HAND VALVE | 40-P-PT1A-0-9021861 | 052.0 | SLURRIES INLET | 7445 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R06 | R06-HZSC-013 | R06-H-013 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HZSO-013 | R06-H-013 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HV-015 | R06-H-015 | FLD | 107-BF | HAND VALVE | 40-P-PT1A-0-9021612 | 052.0 | ACID SCRUBBER | PKG: 14825; -: 0 to 100 % |  |  |  |  | XOMOX TUFLIN | R202 |  |  |  |  | 02
R06 | R06-HZSC-015 | R06-H-015 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 052.0 | CLOSED | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HZSO-015 | R06-H-015 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 052.0 | OPEN | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HV-016 | R06-H-016 | FLD | 107-BF | HAND VALVE | 40-P-PT1A-0-9021611 | 052.0 | CAUSTIC SCRUBBER | PKG: 14826; -: 0 to 100 % |  |  |  |  | XOMOX TUFLIN | R202 |  |  |  |  | 02
R06 | R06-HZSC-016 | R06-H-016 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 052.0 | CLOSED | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 02
R06 | R06-HZSO-016 | R06-H-016 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 052.0 | OPEN | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 02
R06 | R06-HV-017 | R06-H-017 | FLD | 107-BF | HAND VALVE | 40-P-PT1A-0-9021638 | 052.0 | PROCESS VACUUM | PKG: 14827; -: 0 to 100 % |  |  |  |  | XOMOX TUFLIN | R202 |  |  |  |  | 02
R06 | R06-HZSC-017 | R06-H-017 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 052.0 | CLOSED | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HZSO-017 | R06-H-017 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 052.0 | OPEN | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HV-018 | R06-H-018 | FLD | 107-BF | HAND VALVE | 40-P-PT1A-0-9021637 | 052.0 | HOUSE VACUUM | PKG: 14828; -: 0 to 100 % |  |  |  |  | XOMOX TUFLIN | R202 |  |  |  |  | 02
R06 | R06-HZSC-018 | R06-H-018 | FLD | 107-BF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 052.0 | CLOSED | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-HZSO-018 | R06-H-018 | FLD | 107-BF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 052.0 | OPEN | I.S: I.S; DI: DI |  |  |  | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R06 | R06-II-002 | R06-I-002 | PCS | 107-BF | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-IT-002 | R06-I-002 | MCC | 107-BF | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 052.0 | AGITATOR CURRENT | 8762 | 0 to 5 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP1 | [6 empty] | 01
R06 | R06-LI-001 | R06-L-001 | PCS | 107-BF | INDICATOR - LEVEL |  |  | LEVEL | PKG: L6642; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-LT-001 | R06-L-001 | FLD | 107-BF | TRANSMITTER - LEVEL | R06/N3/100 | 052.0 | LEVEL | 6642 | 0-1600 litres | +/- 2% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | VEGA | VEGAPULS 63 | KL0028 | TI702-SP-5009 |  |  | 01
R06 | R06-LG-002 | R06-L-002 | PKG | 107-BF | LEVEL GAUGE | AGITATOR SEAL POT | 052.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R06 | R06-PIC-001 | R06-P-001 | PCS | 107-BF | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: L7018; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-PIT-001 | R06-P-001 | FLD | 107-BF | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9021603 | 052.0 | PRESSURE | 7018 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R06 | R06-PI-002 | R06-P-002 | PCS | 107-BF | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6655; -: -1 to 2.3barg; -: +/-0.066barg; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R06 | R06-PIT-002 | R06-P-002 | FLD | 107-BF | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9021603 | 052.0 | PRESSURE | 6655 | -1 to 2.3 barg | +/- 1% | SHE | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R06 | R06-PAH-003 | R06-P-003 | PCS | 107-BF | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-PSH-003 | R06-P-003 | FLD | 107-BF | SWITCH - PRESSURE - DIAPHRAGM - HI | 150-P-PT1A-H-9021603 | 052.0 | HIGH PRESSURE | 6656 | set @ 2.2 barg | +/- 1% | SHE | By request | C |  | I.S | DI |  |  | 32 | GP1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R06 | R06-PI-004 | R06-P-004 | FLD | 107-BF | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-0-9021630 | 052.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R06 | R06-PI-007 | R06-P-007 | FLD | 107-BF | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029420 | 052.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R06 | R06-PI-008 | R06-P-008 | FLD | 107-BF | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9021625 | 052.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R06 | R06-PSV-012 | R06-P-012 | FLD | 107-BF | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9021655 | 052.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R06 | R06-PSV-013 | R06-P-013 | FLD | 107-BF | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021653 | 052.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R06 | R06-PSV-014 | R06-P-014 | FLD | 107-BF | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021654 | 052.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R06 | R06-PRV-015 | R06-P-015 | FLD | 107-BF | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028649 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R06 | R06-PI-016 | R06-P-016 | PKG | 107-BF | PRESSURE GAUGE | AGITATOR SEAL POT | 052.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R06 | R06-PRV-017 | R06-P-017 | FLD | 107-BF | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028649 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 6.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | GP1 | BURGMANN | Part of gas seal system |  |  |  |  | 52
R06 | R06-PIAL-018 | R06-P-018 | PCS | 107-BF | PRESSURE GAUGE - ALARM LOW | R06 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LP ALARM | -: SET @5BARG; REQ: By request; F: C |  |  |  | GP1 | [6 empty] | 52
R06 | R06-PISL-018 | R06-P-018 | FLD | 107-BF | PRESSURE GAUGE - SWITCH LOW | R06 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LP ALARM |  | SET @5BARG |  | REF | By request | C |  | I.S | DI |  |  | 0 | GP1 | PEPPERL + FUCHS | SJ2-N |  | TI702-SP-5099 |  |  | 52
R06 | R06-RO-001 | R06-R-001 | DEL | 107-BF | RESTRICTION ORIFICE PLATE | DELETED |  | DELETED | [11 empty] | 0 | [5 empty] | DELETED |  | 01 | bar: -
R06 | R06-SE-001 | R06-S-001 | PKG | 107-BF | ELEMENT - SPEED | AGITATOR SHAFT | 052.0 | AGITATOR | 6946 | 0 to 215 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R06 | R06-SI-001A | R06-S-001 | PCS | 107-BF | INDICATOR - SPEED |  |  | AGITATOR | PKG: L6946; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-SI-001B | R06-S-001 | FLD | 107-BF | INDICATOR - SPEED | ADJ TO R06 AGITATOR | 052.0 | AGITATOR | L6946 | 0 to 220 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R06 | R06-DS-002 | R06-S-002 | MCC | 107-BF | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R06 | R06-DY-002 | R06-S-002 | MCC | 107-BF | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
R06 | R06-DYC-002 | R06-S-002 | MCC | 107-BF | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 052.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
R06 | R06-SC-002 | R06-S-002 | MCC | 107-BF | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 052.0 | AGITATOR | 8762 | 0 to 220 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP1 |  |  |  |  | SET Min 43 rpm & Max 215 rpm |  | 01
R06 | R06-SIC-002 | R06-S-002 | PCS | 107-BF | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TE-001 | R06-T-001 | PKG | 107-BF | ELEMENT - TEMPERATURE - RTD | WITH R06-CV-001 |  | TEMPERATURE #1 | PKG: L6915; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R06 | R06-TI-001A | R06-T-001 | PCS | 107-BF | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6915; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R06 | R06-TI-001B | R06-T-001 | FLD | 107-BF | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R06 | 052.0 | TEMPERATURE #1 | L6915 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R06 | R06-TT-001 | R06-T-001 | PKG | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | TEMPERATURE #1 | 6915 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R06 | R06-TE-002 | R06-T-002 | PKG | 107-BF | ELEMENT - TEMPERATURE - RTD | WITH R06-CV-001 |  | TEMPERATURE #2 | PKG: L6916; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R06 | R06-TI-002A | R06-T-002 | PCS | 107-BF | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6916; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R06 | R06-TI-002B | R06-T-002 | FLD | 107-BF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 052.0 | TEMPERATURE #2 | L6916 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R06 | R06-TT-002 | R06-T-002 | PKG | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | TEMPERATURE #2 | 6916 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R06 | R06-TE-003 | R06-T-003 | PKG | 107-BF | ELEMENT - TEMPERATURE - RTD | R06/N2/100 |  | BAFFLE TEMPERATURE | PKG: L6917; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R06 | R06-TI-003A | R06-T-003 | PCS | 107-BF | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6917; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R06 | R06-TI-003B | R06-T-003 | FLD | 107-BF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 052.0 | BAFFLE TEMPERATURE | L6917 | -30 to 170 degC | +/- 0.5% | SHE | by request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5089 |  |  | 34
R06 | R06-TT-003 | R06-T-003 | PKG | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | BAFFLE TEMPERATURE | 6917 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ROSEMOUNT | 644HAI1A1 |  | TI702-SP-5089 |  |  | 41
R06 | R06-TE-004 | R06-T-004 | FLD | 107-BF | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9021625 |  | JACKET INLET TEMP. | PKG: L6918; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TI-004A | R06-T-004 | PCS | 107-BF | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6918; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TI-004B | R06-T-004 | FLD | 107-BF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 052.0 | JACKET INLET TEMP. | L6918 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5074 |  |  | 34
R06 | R06-TT-004 | R06-T-004 | FLD | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | JACKET INLET TEMP. | 6918 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | THZ2/PRG / DM400X | KT0004 | TI702-SP-5074 |  |  | 01
R06 | R06-TE-005 | R06-T-005 | FLD | 107-BF | ELEMENT - TEMPERATURE - RTD | 150-P-PT1A-H-9021603 |  | PC1 INLET TEMPERATURE | PKG: L6543; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TI-005 | R06-T-005 | PCS | 107-BF | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R06 | R06-TT-005 | R06-T-005 | FLD | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | PC1 INLET TEMPERATURE | 6543 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R06 | R06-TI-005A | R06-T-005A | [6 empty] | PKG: L6543; REQ: By request
R06 | R06-TE-006 | R06-T-006 | FLD | 107-BF | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9021610 |  | VC1 OFF GAS TEMPERATURE | PKG: L6544; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R06 | R06-TI-006A | R06-T-006 | PCS | 107-BF | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6544; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R06 | R06-TI-006B | R06-T-006 | FLD | 107-BF | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R06 | 052.0 | VC1 OFF GAS TEMPERATURE | L6544 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R06 | R06-TT-006 | R06-T-006 | FLD | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | VC1 OFF GAS TEMPERATURE | 6544 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R06 | R06-TE-007 | R06-T-007 | FLD | 107-BF | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9021617 |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R06 | R06-TIC-007 | R06-T-007 | PCS | 107-BF | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | PKG: L6545; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TT-007 | R06-T-007 | FLD | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | VC1 HTF RTN TEMPERATURE | 6545 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R06 | R06-TE-008 | R06-T-008 | FLD | 107-BF | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9021614 |  | PC1 HTF RTN TEMPERATURE | PKG: L6546; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TI-008 | R06-T-008 | [6 empty] | PKG: L6546; REQ: By request
R06 | R06-TIC-008 | R06-T-008 | PCS | 107-BF | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | PKG: L6546; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TT-008 | R06-T-008 | FLD | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | PC1 HTF RTN TEMPERATURE | 6546 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R06 | R06-TE-009 | R06-T-009 | FLD | 107-BF | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9021602 |  | DISTILLATE RTN TEMP. | PKG: L6547; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TI-009A | R06-T-009 | PCS | 107-BF | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | PKG: L6547; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TI-009B | R06-T-009 | FLD | 107-BF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 052.0 | DISTILLATE RTN TEMP. | L6547 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R06 | R06-TT-009 | R06-T-009 | FLD | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | DISTILLATE RTN TEMP. | 6547 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R06 | R06-TE-010 | R06-T-010 | FLD | 107-BF | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9021624 |  | OUTLET TEMPERATURE | PKG: L6548; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TI-010A | R06-T-010 | PCS | 107-BF | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6548; REQ: By request |  |  | 0 | [7 empty] | 01
R06 | R06-TI-010B | R06-T-010 | FLD | 107-BF | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R06 | 052.0 | OUTLET TEMPERATURE | L6548 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R06 | R06-TT-010 | R06-T-010 | FLD | 107-BF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 052.0 | OUTLET TEMPERATURE | 6548 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R06 | R06-YA-001 | R06-Y-001 | PCS | 107-BF | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R06 | R06-YS-001 | R06-Y-001 | FUT | 107-BF | COMMON ALARM | R06 GAS SEAL ASSEMBLY | 052.0 | AGITATOR SEAL COMMON ALARM | PKG: 8682; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP1 | [6 empty] | 01
R07 | R07-AG-001 | R07-A-001 | PKG | 107-CA | SPEED MOORE DISPLAY |  | 053.0 | AGITATOR | PKG: L6947; REF: REF; REQ: By request | [10 empty] | 34
R07 | R07-BD-001 | R07-B-001 | FLD | 107-CA | RUPTURE DISC | 80-P-PT1A-H-9022103 | 053.0 | BURSTING DISC | 6740 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R07 | R07-YI-001 | R07-B-001 | PCS | 107-CA | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-CV-001 | R07-C-001 | PKG | 107-CA | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R07/K/80 | 053.0 | BOTTOM OUTLET VALVE | 8791 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R07 | R07-CY-001 | R07-C-001 | PKG | 107-CA | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP2 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R07 | R07-ZSC-001 | R07-C-001 | PKG | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R07 | R07-ZSO-001 | R07-C-001 | PKG | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R07 | R07-CV-004 | R07-C-004 | FLD | 107-CA | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9022130 | 053.0 | NITROGEN SUPPLY | 6785 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R07 | R07-CV-005 | R07-C-005 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022111 | 053.0 | SCRUBBER 01 | 7196 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-CY-005 | R07-C-005 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-005 | R07-C-005 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-005 | R07-C-005 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-006 | R07-C-006 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022110 | 053.0 | SCRUBBER 02 | 7197 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-CY-006 | R07-C-006 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-006 | R07-C-006 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-006 | R07-C-006 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-007 | R07-C-007 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9022138 | 053.0 | PROCESS VACUUM | 7318 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-CY-007 | R07-C-007 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-007 | R07-C-007 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-007 | R07-C-007 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-008 | R07-C-008 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9022137 | 053.0 | HOUSE VACUUM | 7267 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-CY-008 | R07-C-008 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-008 | R07-C-008 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-008 | R07-C-008 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-009 | R07-C-009 | FLD | 107-CA | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-C-9029415 | 053.0 | COLD HTF SUPPLY | 7500 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R07 | R07-CY-009 | R07-C-009 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-009 | R07-C-009 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-009 | R07-C-009 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-010 | R07-C-010 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 50-HT-C3SA-D-9029156 | 053.0 | HOT HTF SUPPLY | 7495 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R07 | R07-ZSC-010 | R07-C-010 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-010 | R07-C-010 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-011 | R07-C-011 | FLD | 107-CA | GLOBE VALVE - CONTROL - F.C. | 50-HT-CS3A-D-9022123 | 053.0 | HOT HTF RTN | 6364 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R07 | R07-CV-012 | R07-C-012 | FLD | 107-CA | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-D-9022156 | 053.0 | COLD HTF RTN | 6368 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R07 | R07-CV-013 | R07-C-013 | FLD | 107-CA | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-D-9022125 | 053.0 | DUAL JACKET | 7132 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R07 | R07-CY-013 | R07-C-013 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-013 | R07-C-013 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-013 | R07-C-013 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-014 | R07-C-014 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9022159 | 053.0 | N2 TO BOTTOM OUTLET | 7143 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-CY-014 | R07-C-014 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-014 | R07-C-014 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-014 | R07-C-014 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-015 | R07-C-015 | FLD | 107-CA | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9022114 | 053.0 | PC1 TEMPERED HTF RTN | 6407 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R07 | R07-CV-016 | R07-C-016 | FLD | 107-CA | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9022117 | 053.0 | VC1 COLD HTF RTN | 6412 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R07 | R07-CV-018 | R07-C-018 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022105 | 053.0 | DISTILLATE VENT LINE | 7198 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-CY-018 | R07-C-018 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-018 | R07-C-018 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-018 | R07-C-018 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-019 | R07-C-019 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022825 | 053.0 | LIQUID INLET | 7238 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-CY-019 | R07-C-019 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-019 | R07-C-019 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-019 | R07-C-019 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-021 | R07-C-021 | FLD | 107-CA | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9022110 | 053.0 | +VE PRESSURE CONTROL | 6806 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R07 | R07-CV-022 | R07-C-022 | FLD | 107-CA | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9022137 | 053.0 | -VE PRESSURE CONTROL | 6827 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R07 | R07-CV-024 | R07-C-024 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-0-9022167 | 053.0 | SOLIDS INLET | 7346 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-CX-024 | R07-C-024 | SGS | 107-CA | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R07 | R07-CY-024 | R07-C-024 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED | 053.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-024 | R07-C-024 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-024 | R07-C-024 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-CV-025 | R07-C-025 | FLD | 107-CA | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9022110 | 053.0 | SOLIDS ADDITION VENT | 7293 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-CX-025 | R07-C-025 | SGS | 107-CA | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R07 | R07-CY-025 | R07-C-025 | FLD | 107-CA | SOLENOID VALVE | RACK MOUNTED | 053.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R07 | R07-ZSC-025 | R07-C-025 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-ZSO-025 | R07-C-025 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 053.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-DIC-001 | R07-D-001 | PCS | 107-CA | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R07 | R07-DS-001 | R07-D-001 | MCC | 107-CA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R07 | R07-DY-001 | R07-D-001 | MCC | 107-CA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R07 | R07-DYC-001 | R07-D-001 | MCC | 107-CA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 053.0 | JACKET PUMP | 8742 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R07 | R07-HS-002 | R07-H-002 | FLD | 107-CA | SWITCH - HAND OP. | ADJ TO R07 | 053.0 | CRASH COOL | 6993 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP2 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R07 | R07-HV-008 | R07-H-008 | FLD | 107-CA | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028675 | 053.0 | N2 PRESSURE SELECT | 7475 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R07 | R07-HZSC-008 | R07-H-008 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R07 | R07-HZSO-008 | R07-H-008 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R07 | R07-HV-009 | R07-H-009 | FLD | 107-CA | HAND VALVE | 25-P-PT1A-0-9022162 | 053.0 | AUX. INLET | 7392 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-HZSC-009 | R07-H-009 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-HZSO-009 | R07-H-009 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R07 | R07-HV-010 | R07-H-010 | FLD | 107-CA | HAND VALVE | 40-P-PT1A-0-9022825 | 053.0 | REAGENTS INLET | 7366 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R07 | R07-HZSC-010 | R07-H-010 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-HZSO-010 | R07-H-010 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-HV-012 | R07-H-012 | FLD | 107-CA | HAND VALVE | 25-P-PT1A-0-9022824 | 053.0 | SOLVENTS INLET | 7393 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-HZSC-012 | R07-H-012 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-HZSO-012 | R07-H-012 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R07 | R07-HV-013 | R07-H-013 | FLD | 107-CA | HAND VALVE | 40-P-PT1A-0-9022825 | 053.0 | SLURRIES INLET | 7446 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R07 | R07-HZSC-013 | R07-H-013 | FLD | 107-CA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-HZSO-013 | R07-H-013 | FLD | 107-CA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R07 | R07-II-002 | R07-I-002 | PCS | 107-CA | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-IT-002 | R07-I-002 | MCC | 107-CA | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 053.0 | AGITATOR CURRENT | 8763 | 0 to 5 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP2 | [6 empty] | 01
R07 | R07-LAH-001 | R07-L-001 | PCS | 107-CA | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R07 | R07-LE-001 | R07-L-001 | FLD | 107-CA | ELEMENT - LEVEL | 80-P-PT1A-H-9022103 | 053.0 | HIGH LEVEL | L6631 | Fixed | - | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R07 | R07-LSH-001 | R07-L-001 | CPR | 107-CA | SWITCH - LEVEL - HIGH | 80-P-PT1A-H-9022103 | 053.0 | HIGH LEVEL | 6631 | - | - | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | GP2 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R07 | R07-LG-002 | R07-L-002 | PKG | 107-CA | LEVEL GAUGE | AGITATOR SEAL POT | 053.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R07 | R07-PIC-001 | R07-P-001 | PCS | 107-CA | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: L7019; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-PIT-001 | R07-P-001 | FLD | 107-CA | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9022103 | 053.0 | PRESSURE | 7019 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R07 | R07-PI-002 | R07-P-002 | PCS | 107-CA | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6660; -: -1 to 2.3barg; -: +/-0.066barg; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R07 | R07-PIT-002 | R07-P-002 | FLD | 107-CA | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9022103 | 053.0 | PRESSURE | 6660 | -1 to 2.3 barg | +/- 1% | SHE | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R07 | R07-PAH-003 | R07-P-003 | PCS | 107-CA | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-PSH-003 | R07-P-003 | FLD | 107-CA | SWITCH - PRESSURE - DIAPHRAGM - HI | 80-P-PT1A-H-9022103 | 053.0 | HIGH PRESSURE | 6661 | set @ 2.2 barg | +/- 1% | SHE | By request | C |  | I.S | DI |  |  | 32 | GP2 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R07 | R07-PI-004 | R07-P-004 | FLD | 107-CA | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-0-9022130 | 053.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R07 | R07-PI-007 | R07-P-007 | FLD | 107-CA | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-C-9029415 | 053.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R07 | R07-PI-008 | R07-P-008 | FLD | 107-CA | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-D-9022125 | 053.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R07 | R07-PSV-012 | R07-P-012 | FLD | 107-CA | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9022155 | 053.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R07 | R07-PSV-013 | R07-P-013 | FLD | 107-CA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022153 | 053.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R07 | R07-PSV-014 | R07-P-014 | FLD | 107-CA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022154 | 053.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R07 | R07-PRV-015 | R07-P-015 | FLD | 107-CA | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028674 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R07 | R07-PI-016 | R07-P-016 | PKG | 107-CA | PRESSURE GAUGE | AGITATOR SEAL POT | 053.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 25 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R07 | R07-SE-001 | R07-S-001 | PKG | 107-CA | ELEMENT - SPEED | AGITATOR SHAFT | 053.0 | AGITATOR | 6947 | 0 to 186 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP2 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R07 | R07-SI-001A | R07-S-001 | PCS | 107-CA | INDICATOR - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-SI-001B | R07-S-001 | FLD | 107-CA | INDICATOR - SPEED | ADJ TO R07 AGITATOR | 053.0 | AGITATOR | L6947 | 0 to 200 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP2 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R07 | R07-DS-002 | R07-S-002 | MCC | 107-CA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R07 | R07-DY-002 | R07-S-002 | MCC | 107-CA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R07 | R07-DYC-002 | R07-S-002 | MCC | 107-CA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 053.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R07 | R07-SC-002 | R07-S-002 | MCC | 107-CA | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 053.0 | AGITATOR | 8763 | 0 to 200 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP2 |  |  |  |  | SET Min 37 rpm & Max 186 rpm |  | 01
R07 | R07-SIC-002 | R07-S-002 | PCS | 107-CA | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TE-001 | R07-T-001 | PKG | 107-CA | ELEMENT - TEMPERATURE - RTD | WITH RO7-CV-001 |  | TEMPERATURE #1 | PKG: L6860; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R07 | R07-TI-001A | R07-T-001 | PCS | 107-CA | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6860; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R07 | R07-TI-001B | R07-T-001 | FLD | 107-CA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R07 | 053.0 | TEMPERATURE #1 | L6860 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R07 | R07-TT-001 | R07-T-001 | PKG | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | TEMPERATURE #1 | 6860 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R07 | R07-TE-002 | R07-T-002 | PKG | 107-CA | ELEMENT - TEMPERATURE - RTD | WITH RO7-CV-001 |  | TEMPERATURE #2 | PKG: L6861; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R07 | R07-TI-002A | R07-T-002 | PCS | 107-CA | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6861; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R07 | R07-TI-002B | R07-T-002 | FLD | 107-CA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 053.0 | TEMPERATURE #2 | L6861 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R07 | R07-TT-002 | R07-T-002 | PKG | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | TEMPERATURE #2 | 6861 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R07 | R07-TE-003 | R07-T-003 | PKG | 107-CA | ELEMENT - TEMPERATURE - RTD | R07/N2/80 |  | BAFFLE TEMPERATURE | PKG: L6862; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R07 | R07-TI-003A | R07-T-003 | PCS | 107-CA | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6862; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R07 | R07-TI-003B | R07-T-003 | FLD | 107-CA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 053.0 | BAFFLE TEMPERATURE | L6862 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R07 | R07-TT-003 | R07-T-003 | PKG | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | BAFFLE TEMPERATURE | 6862 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R07 | R07-TE-004 | R07-T-004 | FLD | 107-CA | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9022125 |  | JACKET INLET TEMP. | PKG: L6863; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TI-004A | R07-T-004 | PCS | 107-CA | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6863; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TI-004B | R07-T-004 | FLD | 107-CA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 053.0 | JACKET INLET TEMP. | L6863 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 01
R07 | R07-TT-004 | R07-T-004 | FLD | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | JACKET INLET TEMP. | 6863 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R07 | R07-TE-005 | R07-T-005 | FLD | 107-CA | ELEMENT - TEMPERATURE - RTD | 80-P-PT1A-H-9022103 |  | PC1 INLET TEMPERATURE | PKG: L6549; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TI-005 | R07-T-005 | PCS | 107-CA | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R07 | R07-TT-005 | R07-T-005 | FLD | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | PC1 INLET TEMPERATURE | 6549 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R07 | R07-TI-005A | R07-T-005A |  |  |  |  | L6549 |  | REQ: By request
R07 | R07-TE-006 | R07-T-006 | FLD | 107-CA | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9022110 |  | VC1 OFF GAS TEMPERATURE | PKG: L6550; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R07 | R07-TI-006A | R07-T-006 | PCS | 107-CA | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6550; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R07 | R07-TI-006B | R07-T-006 | FLD | 107-CA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R07 | 053.0 | VC1 OFF GAS TEMPERATURE | L6550 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R07 | R07-TT-006 | R07-T-006 | FLD | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | VC1 OFF GAS TEMPERATURE | 6550 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R07 | R07-TE-007 | R07-T-007 | FLD | 107-CA | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9022117 |  | VC1 HTF RTN TEMPERATURE | PKG: L6551; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TIC-007 | R07-T-007 | PCS | 107-CA | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | PKG: L6551; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TT-007 | R07-T-007 | FLD | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | VC1 HTF RTN TEMPERATURE | 6551 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R07 | R07-TE-008 | R07-T-008 | FLD | 107-CA | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9022114 |  | PC1 HTF RTN TEMPERATURE | PKG: L6552; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TIC-008 | R07-T-008 | PCS | 107-CA | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | PKG: L6552; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TT-008 | R07-T-008 | FLD | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | PC1 HTF RTN TEMPERATURE | 6552 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R07 | R07-TE-009 | R07-T-009 | FLD | 107-CA | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9022102 |  | DISTILLATE RTN TEMP. | PKG: L6553; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TI-009A | R07-T-009 | PCS | 107-CA | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | PKG: L6553; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TI-009B | R07-T-009 | FLD | 107-CA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 053.0 | DISTILLATE RTN TEMP. | L6553 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R07 | R07-TT-009 | R07-T-009 | FLD | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | DISTILLATE RTN TEMP. | 6553 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R07 | R07-TE-010 | R07-T-010 | FLD | 107-CA | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9022128 |  | OUTLET TEMPERATURE | PKG: L6554; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TI-010A | R07-T-010 | PCS | 107-CA | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6554; REQ: By request |  |  | 0 | [7 empty] | 01
R07 | R07-TI-010B | R07-T-010 | FLD | 107-CA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R07 | 053.0 | OUTLET TEMPERATURE | L6554 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R07 | R07-TT-010 | R07-T-010 | FLD | 107-CA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 053.0 | OUTLET TEMPERATURE | 6554 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R07 | R07-YA-001 | R07-Y-001 | PCS | 107-CA | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R07 | R07-YS-001 | R07-Y-001 | FUT | 107-CA | COMMON ALARM | R07 GAS SEAL ASSEMBLY | 053.0 | AGITATOR SEAL COMMON ALARM | PKG: 8683; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP2 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R08 | R08-AG-001 | R08-A-001 | PKG | 107-CB | SPEED MOORE DISPLAY |  | 054.0 | AGITATOR | REF: REF; REQ: By request | [10 empty] | 34
R08 | R08-BD-001 | R08-B-001 | FLD | 107-CB | RUPTURE DISC | 100-P-PT1A-H-9022203 | 054.0 | BURSTING DISC | 6741 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R08 | R08-YI-001 | R08-B-001 | PCS | 107-CB | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-CV-001 | R08-C-001 | PKG | 107-CB | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R08/K/100 | 054.0 | BOTTOM OUTLET VALVE | 8792 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R08 | R08-CY-001 | R08-C-001 | PKG | 107-CB | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP2 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R08 | R08-ZSC-001 | R08-C-001 | PKG | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R08 | R08-ZSO-001 | R08-C-001 | PKG | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R08 | R08-CV-004 | R08-C-004 | FLD | 107-CB | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9022230 | 054.0 | NITROGEN SUPPLY | 6786 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R08 | R08-CV-005 | R08-C-005 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022211 | 054.0 | SCRUBBER 01 | 7199 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-CY-005 | R08-C-005 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-005 | R08-C-005 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-005 | R08-C-005 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-006 | R08-C-006 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022210 | 054.0 | SCRUBBER 02 | 7200 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-CY-006 | R08-C-006 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-006 | R08-C-006 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-006 | R08-C-006 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-007 | R08-C-007 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9022238 | 054.0 | PROCESS VACUUM | 7319 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-CY-007 | R08-C-007 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-007 | R08-C-007 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-007 | R08-C-007 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-008 | R08-C-008 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9022237 | 054.0 | HOUSE VACUUM | 7268 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-CY-008 | R08-C-008 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-008 | R08-C-008 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-008 | R08-C-008 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-009 | R08-C-009 | FLD | 107-CB | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-D-9029428 | 054.0 | COLD HTF SUPPLY | 7535 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R08 | R08-CY-009 | R08-C-009 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-009 | R08-C-009 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-009 | R08-C-009 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-010 | R08-C-010 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029163 | 054.0 | HOT HTF SUPPLY | 7513 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R08 | R08-ZSC-010 | R08-C-010 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-010 | R08-C-010 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-011 | R08-C-011 | FLD | 107-CB | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9022223 | 054.0 | HOT HTF RTN | 6376 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R08 | R08-CV-012 | R08-C-012 | FLD | 107-CB | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9022256 | 054.0 | COLD HTF RTN | 6388 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R08 | R08-CV-013 | R08-C-013 | FLD | 107-CB | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9022225 | 054.0 | DUAL JACKET | 7506 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R08 | R08-CY-013 | R08-C-013 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-013 | R08-C-013 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-013 | R08-C-013 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-014 | R08-C-014 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9022259 | 054.0 | N2 TO BOTTOM OUTLET | 7144 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-CY-014 | R08-C-014 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-014 | R08-C-014 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-014 | R08-C-014 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-015 | R08-C-015 | FLD | 107-CB | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-C-9022214 | 054.0 | PC1 TEMPERED HTF RTN | 6417 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R08 | R08-CV-016 | R08-C-016 | FLD | 107-CB | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9022217 | 054.0 | VC1 COLD HTF RTN | 6424 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R08 | R08-CV-018 | R08-C-018 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022205 | 054.0 | DISTILLATE VENT LINE | 7201 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-CY-018 | R08-C-018 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-018 | R08-C-018 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-018 | R08-C-018 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-019 | R08-C-019 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022842 | 054.0 | LIQUID INLET | 7239 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-CY-019 | R08-C-019 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-019 | R08-C-019 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-019 | R08-C-019 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-021 | R08-C-021 | FLD | 107-CB | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9022210 | 054.0 | +VE PRESSURE CONTROL | 6807 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R08 | R08-CV-022 | R08-C-022 | FLD | 107-CB | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9022237 | 054.0 | -VE PRESSURE CONTROL | 6828 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R08 | R08-CV-024 | R08-C-024 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9022267 | 054.0 | SOLIDS INLET | 7347 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-CX-024 | R08-C-024 | SGS | 107-CB | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R08 | R08-CY-024 | R08-C-024 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED | 054.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-024 | R08-C-024 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-024 | R08-C-024 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-CV-025 | R08-C-025 | FLD | 107-CB | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-O-9022210 | 054.0 | SOLIDS ADDITION VENT | 7294 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-CX-025 | R08-C-025 | SGS | 107-CB | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R08 | R08-CY-025 | R08-C-025 | FLD | 107-CB | SOLENOID VALVE | RACK MOUNTED | 054.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R08 | R08-ZSC-025 | R08-C-025 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-ZSO-025 | R08-C-025 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 054.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-DIC-001 | R08-D-001 | PCS | 107-CB | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R08 | R08-DS-001 | R08-D-001 | MCC | 107-CB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R08 | R08-DY-001 | R08-D-001 | MCC | 107-CB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R08 | R08-DYC-001 | R08-D-001 | MCC | 107-CB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 054.0 | JACKET PUMP | 8745 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R08 | R08-HS-002 | R08-H-002 | FLD | 107-CB | SWITCH - HAND OP. | ADJ TO R08 | 054.0 | CRASH COOL | 6994 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP2 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R08 | R08-HV-008 | R08-H-008 | FLD | 107-CB | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028697 | 054.0 | N2 PRESSURE SELECT | 7476 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R08 | R08-HZSC-008 | R08-H-008 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R08 | R08-HZSO-008 | R08-H-008 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R08 | R08-HV-009 | R08-H-009 | FLD | 107-CB | HAND VALVE | 25-P-PT1A-0-9022262 | 054.0 | AUX. INLET | 7394 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-HZSC-009 | R08-H-009 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-HZSO-009 | R08-H-009 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R08 | R08-HV-010 | R08-H-010 | FLD | 107-CB | HAND VALVE | 25-P-PT1A-0-9022842 | 054.0 | REAGENTS INLET | 7367 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R08 | R08-HZSC-010 | R08-H-010 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-HZSO-010 | R08-H-010 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-HV-012 | R08-H-012 | FLD | 107-CB | HAND VALVE | 25-P-PT1A-0-9022842 | 054.0 | SOLVENTS INLET | 7395 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-HZSC-012 | R08-H-012 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-HZSO-012 | R08-H-012 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R08 | R08-HV-013 | R08-H-013 | FLD | 107-CB | HAND VALVE | 40-P-PT1A-0-9022865 | 054.0 | SLURRIES INLET | 7447 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R08 | R08-HZSC-013 | R08-H-013 | FLD | 107-CB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-HZSO-013 | R08-H-013 | FLD | 107-CB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R08 | R08-II-002 | R08-I-002 | PCS | 107-CB | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-IT-002 | R08-I-002 | MCC | 107-CB | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 054.0 | AGITATOR CURRENT | 8764 | 0 to 8 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP2 | [6 empty] | 01
R08 | R08-LAH-001 | R08-L-001 | PCS | 107-CB | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L8112; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R08 | R08-LE-001 | R08-L-001 | FLD | 107-CB | ELEMENT - LEVEL | 100-P-PT1A-H-9022203 | 054.0 | HIGH LEVEL | L8112 | Fixed | - | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R08 | R08-LSH-001 | R08-L-001 | CPR | 107-CB | SWITCH - LEVEL - HIGH | 100-P-PT1A-H-9022203 | 054.0 | HIGH LEVEL | 8112 | - | - | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | GP2 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R08 | R08-LG-002 | R08-L-002 | PKG | 107-CB | LEVEL GAUGE | AGITATOR SEAL POT | 054.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R08 | R08-PIC-001 | R08-P-001 | PCS | 107-CB | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: L7020; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-PIT-001 | R08-P-001 | FLD | 107-CB | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9022203 | 054.0 | PRESSURE | 7020 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R08 | R08-PI-002 | R08-P-002 | PCS | 107-CB | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6663; -: -1 to 2.3barg; -: +/-0.066barg; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R08 | R08-PIT-002 | R08-P-002 | FLD | 107-CB | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9022203 | 054.0 | PRESSURE | 6663 | -1 to 2.3 barg | +/- 1% | SHE | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R08 | R08-PAH-003 | R08-P-003 | PCS | 107-CB | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-PSH-003 | R08-P-003 | FLD | 107-CB | SWITCH - PRESSURE - DIAPHRAGM - HI | 100-P-PT1A-H-9022203 | 054.0 | HIGH PRESSURE | 6664 | set @ 2.2 barg | +/- 1% | SHE | By request | C |  | I.S | DI |  |  | 32 | GP2 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R08 | R08-PI-004 | R08-P-004 | FLD | 107-CB | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9022230 | 054.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R08 | R08-PI-007 | R08-P-007 | FLD | 107-CB | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029428 | 054.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R08 | R08-PI-008 | R08-P-008 | FLD | 107-CB | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9022225 | 054.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R08 | R08-PSV-012 | R08-P-012 | FLD | 107-CB | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9022255 | 054.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R08 | R08-PSV-013 | R08-P-013 | FLD | 107-CB | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022253 | 054.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R08 | R08-PSV-014 | R08-P-014 | FLD | 107-CB | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022254 | 054.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R08 | R08-PRV-015 | R08-P-015 | FLD | 107-CB | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028696 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R08 | R08-PI-016 | R08-P-016 | PKG | 107-CB | PRESSURE GAUGE | AGITATOR SEAL POT | 054.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R08 | R08-SE-001 | R08-S-001 | PKG | 107-CB | ELEMENT - SPEED | AGITATOR SHAFT | 054.0 | AGITATOR | 6948 | 0 to 153 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP2 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R08 | R08-SI-001A | R08-S-001 | PCS | 107-CB | INDICATOR - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-SI-001B | R08-S-001 | FLD | 107-CB | INDICATOR - SPEED | ADJ TO R08 AGITATOR | 054.0 | AGITATOR | L6948 | 0 to 200 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP2 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R08 | R08-DS-002 | R08-S-002 | MCC | 107-CB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R08 | R08-DY-002 | R08-S-002 | MCC | 107-CB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R08 | R08-DYC-002 | R08-S-002 | MCC | 107-CB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 054.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R08 | R08-SC-002 | R08-S-002 | MCC | 107-CB | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 054.0 | AGITATOR | 8764 | 0 to 160 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP2 |  |  |  |  | SET Min 31rpm & Max 153 rpm |  | 01
R08 | R08-SIC-002 | R08-S-002 | PCS | 107-CB | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | PKG: L6948; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TE-001 | R08-T-001 | PKG | 107-CB | ELEMENT - TEMPERATURE - RTD | WITH R08-CV-001 |  | TEMPERATURE #1 | PKG: L6864; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R08 | R08-TI-001A | R08-T-001 | PCS | 107-CB | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6864; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R08 | R08-TI-001B | R08-T-001 | FLD | 107-CB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R08 | 054.0 | TEMPERATURE #1 | L6864 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R08 | R08-TT-001 | R08-T-001 | PKG | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | TEMPERATURE #1 | 6864 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R08 | R08-TE-002 | R08-T-002 | PKG | 107-CB | ELEMENT - TEMPERATURE - RTD | WITH R08-CV-001 |  | TEMPERATURE #2 | PKG: L6865; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R08 | R08-TI-002A | R08-T-002 | PCS | 107-CB | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6865; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R08 | R08-TI-002B | R08-T-002 | FLD | 107-CB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 054.0 | TEMPERATURE #2 | L6865 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R08 | R08-TT-002 | R08-T-002 | PKG | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | TEMPERATURE #2 | 6865 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R08 | R08-TE-003 | R08-T-003 | PKG | 107-CB | ELEMENT - TEMPERATURE - RTD | R08/N2/100 |  | BAFFLE TEMPERATURE | PKG: L6866; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R08 | R08-TI-003A | R08-T-003 | PCS | 107-CB | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6866; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R08 | R08-TI-003B | R08-T-003 | FLD | 107-CB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 054.0 | BAFFLE TEMPERATURE | L6866 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R08 | R08-TT-003 | R08-T-003 | PKG | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | BAFFLE TEMPERATURE | 6866 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R08 | R08-TE-004 | R08-T-004 | FLD | 107-CB | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022225 |  | JACKET INLET TEMP. | PKG: L6867; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TI-004A | R08-T-004 | PCS | 107-CB | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6867; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TI-004B | R08-T-004 | FLD | 107-CB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 054.0 | JACKET INLET TEMP. | L6867 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R08 | R08-TT-004 | R08-T-004 | FLD | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | JACKET INLET TEMP. | 6867 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R08 | R08-TE-005 | R08-T-005 | FLD | 107-CB | ELEMENT - TEMPERATURE - RTD | 100-P-PT1A-H-9022203 |  | PC1 INLET TEMPERATURE | PKG: L6555; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TI-005 | R08-T-005 | PCS | 107-CB | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R08 | R08-TT-005 | R08-T-005 | FLD | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | PC1 INLET TEMPERATURE | 6555 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R08 | R08-TI-005A | R08-T-005A | [6 empty] | PKG: L6555; REQ: By request
R08 | R08-TE-006 | R08-T-006 | FLD | 107-CB | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9022210 |  | VC1 OFF GAS TEMPERATURE | PKG: L6556; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R08 | R08-TI-006A | R08-T-006 | PCS | 107-CB | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6556; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R08 | R08-TI-006B | R08-T-006 | FLD | 107-CB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R08 | 054.0 | VC1 OFF GAS TEMPERATURE | L6556 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R08 | R08-TT-006 | R08-T-006 | FLD | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | VC1 OFF GAS TEMPERATURE | 6556 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R08 | R08-TE-007 | R08-T-007 | FLD | 107-CB | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9022217 |  | VC1 HTF RTN TEMPERATURE | PKG: L6557; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TIC-007 | R08-T-007 | PCS | 107-CB | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TT-007 | R08-T-007 | FLD | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | VC1 HTF RTN TEMPERATURE | 6557 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R08 | R08-TE-008 | R08-T-008 | FLD | 107-CB | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-C-9022214 |  | PC1 HTF RTN TEMPERATURE | PKG: L6558; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TIC-008 | R08-T-008 | PCS | 107-CB | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TT-008 | R08-T-008 | FLD | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | PC1 HTF RTN TEMPERATURE | 6558 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R08 | R08-TE-009 | R08-T-009 | FLD | 107-CB | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9022202 |  | DISTILLATE RTN TEMP. | PKG: L6559; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TI-009A | R08-T-009 | PCS | 107-CB | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | PKG: L6559; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TI-009B | R08-T-009 | FLD | 107-CB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 054.0 | DISTILLATE RTN TEMP. | L6559 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 01
R08 | R08-TT-009 | R08-T-009 | FLD | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | DISTILLATE RTN TEMP. | 6559 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R08 | R08-TE-010 | R08-T-010 | FLD | 107-CB | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022228 |  | OUTLET TEMPERATURE | PKG: L6560; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TI-010A | R08-T-010 | PCS | 107-CB | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6560; REQ: By request |  |  | 0 | [7 empty] | 01
R08 | R08-TI-010B | R08-T-010 | FLD | 107-CB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R08 | 054.0 | OUTLET TEMPERATURE | L6560 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R08 | R08-TT-010 | R08-T-010 | FLD | 107-CB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 054.0 | OUTLET TEMPERATURE | 6560 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R08 | R08-YA-001 | R08-Y-001 | PCS | 107-CB | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R08 | R08-YS-001 | R08-Y-001 | FUT | 107-CB | COMMON ALARM | R08 GAS SEAL ASSEMBLY | 054.0 | AGITATOR SEAL COMMON ALARM | PKG: 8692; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP2 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R09 | R09-AG-001 | R09-A-001 | PKG | 107-CC | SPEED MOORE DISPLAY |  | 055.0 | AGITATOR | PKG: L6949; REF: REF; REQ: By request | [10 empty] | 34
R09 | R09-BD-001 | R09-B-001 | FLD | 107-CC | RUPTURE DISC | 100-P-PT1A-H-9022303 | 055.0 | BURSTING DISC | 6742 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R09 | R09-YI-001 | R09-B-001 | PCS | 107-CC | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-CV-001 | R09-C-001 | PKG | 107-CC | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R09/K/100 | 055.0 | BOTTOM OUTLET VALVE | 8793 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R09 | R09-CY-001 | R09-C-001 | PKG | 107-CC | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP2 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R09 | R09-ZSC-001 | R09-C-001 | PKG | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R09 | R09-ZSO-001 | R09-C-001 | PKG | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R09 | R09-CV-004 | R09-C-004 | FLD | 107-CC | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9022330 | 055.0 | NITROGEN SUPPLY | 6787 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R09 | R09-CV-005 | R09-C-005 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022311 | 055.0 | SCRUBBER 01 | 7202 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-CY-005 | R09-C-005 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-005 | R09-C-005 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-005 | R09-C-005 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-006 | R09-C-006 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022310 | 055.0 | SCRUBBER 02 | 7203 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-CY-006 | R09-C-006 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-006 | R09-C-006 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-006 | R09-C-006 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-007 | R09-C-007 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9022338 | 055.0 | PROCESS VACUUM | 7320 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-CY-007 | R09-C-007 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-007 | R09-C-007 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-007 | R09-C-007 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-008 | R09-C-008 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9022337 | 055.0 | HOUSE VACUUM | 7269 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-CY-008 | R09-C-008 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-008 | R09-C-008 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-008 | R09-C-008 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-009 | R09-C-009 | FLD | 107-CC | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029417 | 055.0 | COLD HTF SUPPLY | 7536 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R09 | R09-CY-009 | R09-C-009 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-009 | R09-C-009 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-009 | R09-C-009 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-010 | R09-C-010 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029158 | 055.0 | HOT HTF SUPPLY | 7522 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R09 | R09-ZSC-010 | R09-C-010 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-010 | R09-C-010 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-011 | R09-C-011 | FLD | 107-CC | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9022323 | 055.0 | HOT HTF RTN | 6377 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R09 | R09-CV-012 | R09-C-012 | FLD | 107-CC | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9022356 | 055.0 | COLD HTF RTN | 6389 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R09 | R09-CV-013 | R09-C-013 | FLD | 107-CC | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9022325 | 055.0 | DUAL JACKET | 7507 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R09 | R09-CY-013 | R09-C-013 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-013 | R09-C-013 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-013 | R09-C-013 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-014 | R09-C-014 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9022359 | 055.0 | N2 TO BOTTOM OUTLET | 7145 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-CY-014 | R09-C-014 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-014 | R09-C-014 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-014 | R09-C-014 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-015 | R09-C-015 | FLD | 107-CC | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-C-9022314 | 055.0 | PC1 TEMPERED HTF RTN | 6418 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R09 | R09-CV-016 | R09-C-016 | FLD | 107-CC | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9022317 | 055.0 | VC1 COLD HTF RTN | 6425 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R09 | R09-CV-018 | R09-C-018 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 40-P-PTIA-0-9022305 | 055.0 | DISTILLATE VENT LINE | 7204 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-CY-018 | R09-C-018 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-018 | R09-C-018 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-018 | R09-C-018 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-019 | R09-C-019 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022823 | 055.0 | LIQUID INLET | 7240 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-CY-019 | R09-C-019 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-019 | R09-C-019 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-019 | R09-C-019 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-021 | R09-C-021 | FLD | 107-CC | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9022310 | 055.0 | +VE PRESSURE CONTROL | 6808 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R09 | R09-CV-022 | R09-C-022 | FLD | 107-CC | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9022337 | 055.0 | -VE PRESSURE CONTROL | 6829 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R09 | R09-CV-024 | R09-C-024 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9022367 | 055.0 | SOLIDS INLET | 7348 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-CX-024 | R09-C-024 | SGS | 107-CC | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R09 | R09-CY-024 | R09-C-024 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED | 055.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-024 | R09-C-024 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-024 | R09-C-024 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-CV-025 | R09-C-025 | FLD | 107-CC | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9022310 | 055.0 | SOLIDS ADDITION VENT | 7295 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-CX-025 | R09-C-025 | SGS | 107-CC | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R09 | R09-CY-025 | R09-C-025 | FLD | 107-CC | SOLENOID VALVE | RACK MOUNTED | 055.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R09 | R09-ZSC-025 | R09-C-025 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-ZSO-025 | R09-C-025 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 055.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-DIC-001 | R09-D-001 | PCS | 107-CC | INDICATING CONTR. - MOTOR DRIVE | [14 empty] | 0 | [7 empty] | 01 | bar: PKG
R09 | R09-DS-001 | R09-D-001 | MCC | 107-CC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R09 | R09-DY-001 | R09-D-001 | MCC | 107-CC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R09 | R09-DYC-001 | R09-D-001 | MCC | 107-CC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 055.0 | JACKET PUMP | 8748 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R09 | R09-HS-002 | R09-H-002 | FLD | 107-CC | SWITCH - HAND OP. | ADJ TO R09 | 055.0 | CRASH COOL | 6995 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP2 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R09 | R09-HV-008 | R09-H-008 | FLD | 107-CC | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028672 | 055.0 | N2 PRESSURE SELECT | 7477 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R09 | R09-HZSC-008 | R09-H-008 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R09 | R09-HZSO-008 | R09-H-008 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R09 | R09-HV-009 | R09-H-009 | FLD | 107-CC | HAND VALVE | 25-P-PT1A-0-9022362 | 055.0 | AUX. INLET | 7396 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-HZSC-009 | R09-H-009 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-HZSO-009 | R09-H-009 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R09 | R09-HV-010 | R09-H-010 | FLD | 107-CC | HAND VALVE | 40-P-PT1A-0-9022823 | 055.0 | REAGENTS INLET | 7368 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE15mm |  | 01
R09 | R09-HZSC-010 | R09-H-010 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-HZSO-010 | R09-H-010 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-HV-012 | R09-H-012 | FLD | 107-CC | HAND VALVE | 25-P-PT1A-0-9022822 | 055.0 | SOLVENTS INLET | 7397 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-HZSC-012 | R09-H-012 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-HZSO-012 | R09-H-012 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R09 | R09-HV-013 | R09-H-013 | FLD | 107-CC | HAND VALVE | 40-P-PT1A-0-9022823 | 055.0 | SLURRIES INLET | 7448 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R09 | R09-HZSC-013 | R09-H-013 | FLD | 107-CC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-HZSO-013 | R09-H-013 | FLD | 107-CC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R09 | R09-II-002 | R09-I-002 | PCS | 107-CC | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-IT-002 | R09-I-002 | MCC | 107-CC | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 055.0 | AGITATOR CURRENT | 8765 | 0 to 8 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP2 | [6 empty] | 01
R09 | R09-LAH-001 | R09-L-001 | PCS | 107-CC | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R09 | R09-LE-001 | R09-L-001 | FLD | 107-CC | ELEMENT - LEVEL | 100-P-PT1A-H-9022303 | 055.0 | HIGH LEVEL |  | Fixed | - | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R09 | R09-LSH-001 | R09-L-001 | CPR | 107-CC | SWITCH - LEVEL - HIGH | 100-P-PT1A-H-9022303 | 055.0 | HIGH LEVEL | 6632 | - | - | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | GP2 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R09 | R09-LG-002 | R09-L-002 | PKG | 107-CC | LEVEL GAUGE | AGITATOR SEAL POT | 055.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R09 | R09-PIC-001 | R09-P-001 | PCS | 107-CC | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: L7021; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-PIT-001 | R09-P-001 | FLD | 107-CC | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9022303 | 055.0 | PRESSURE | 7021 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R09 | R09-PI-002 | R09-P-002 | PCS | 107-CC | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6666; -: -1 to 2.3barg; -: +/-0.066barg; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R09 | R09-PIT-002 | R09-P-002 | FLD | 107-CC | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9022303 | 055.0 | PRESSURE | 6666 | -1 to 2.3 barg | +/- 1% | SHE | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R09 | R09-PAH-003 | R09-P-003 | PCS | 107-CC | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-PSH-003 | R09-P-003 | FLD | 107-CC | SWITCH - PRESSURE - DIAPHRAGM - HI | 100-P-PT1A-H-9022303 | 055.0 | HIGH PRESSURE | 6667 | set @ 2.2 barg | +/- 1% | SHE | By request | C |  | I.S | DI |  |  | 32 | GP2 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R09 | R09-PI-004 | R09-P-004 | FLD | 107-CC | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9022330 | 055.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R09 | R09-PI-007 | R09-P-007 | FLD | 107-CC | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029417 | 055.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R09 | R09-PI-008 | R09-P-008 | FLD | 107-CC | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9022325 | 055.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R09 | R09-PSV-012 | R09-P-012 | FLD | 107-CC | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9022355 | 055.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R09 | R09-PSV-013 | R09-P-013 | FLD | 107-CC | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022353 | 055.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R09 | R09-PSV-014 | R09-P-014 | FLD | 107-CC | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022354 | 055.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R09 | R09-PRV-015 | R09-P-015 | FLD | 107-CC | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028671 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R09 | R09-PI-016 | R09-P-016 | PKG | 107-CC | PRESSURE GAUGE | AGITATOR SEAL POT | 055.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 25 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R09 | R09-SE-001 | R09-S-001 | PKG | 107-CC | ELEMENT - SPEED | AGITATOR SHAFT | 055.0 | AGITATOR | 6949 | 0 to 153 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP2 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R09 | R09-SI-001A | R09-S-001 | PCS | 107-CC | INDICATOR - SPEED |  |  | AGITATOR | PKG: L6949; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-SI-001B | R09-S-001 | FLD | 107-CC | INDICATOR - SPEED | ADJ TO R09 AGITATOR | 055.0 | AGITATOR | L6949 | 0 to 200 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP2 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R09 | R09-DS-002 | R09-S-002 | MCC | 107-CC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R09 | R09-DY-002 | R09-S-002 | MCC | 107-CC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R09 | R09-DYC-002 | R09-S-002 | MCC | 107-CC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 055.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R09 | R09-SC-002 | R09-S-002 | MCC | 107-CC | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 055.0 | AGITATOR | 8765 | 0 to 160 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP2 |  |  |  |  | SET Min 31rpm & Max 153 rpm |  | 01
R09 | R09-SIC-002 | R09-S-002 | PCS | 107-CC | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | PKG: L6949; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TE-001 | R09-T-001 | PKG | 107-CC | ELEMENT - TEMPERATURE - RTD | WITH R09-CV-001 |  | TEMPERATURE #1 | PKG: L6868; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R09 | R09-TI-001A | R09-T-001 | PCS | 107-CC | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6868; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R09 | R09-TI-001B | R09-T-001 | FLD | 107-CC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R09 | 055.0 | TEMPERATURE #1 |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R09 | R09-TT-001 | R09-T-001 | PKG | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | TEMPERATURE #1 | 6868 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R09 | R09-TE-002 | R09-T-002 | PKG | 107-CC | ELEMENT - TEMPERATURE - RTD | WITH R09-CV-001 |  | TEMPERATURE #2 | PKG: L6869; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R09 | R09-TI-002A | R09-T-002 | PCS | 107-CC | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6869; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R09 | R09-TI-002B | R09-T-002 | FLD | 107-CC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 055.0 | TEMPERATURE #2 | L6869 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R09 | R09-TT-002 | R09-T-002 | PKG | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | TEMPERATURE #2 | 6869 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R09 | R09-TE-003 | R09-T-003 | PKG | 107-CC | ELEMENT - TEMPERATURE - RTD | R09/N2/100 |  | BAFFLE TEMPERATURE | PKG: L6870; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R09 | R09-TI-003A | R09-T-003 | PCS | 107-CC | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6870; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R09 | R09-TI-003B | R09-T-003 | FLD | 107-CC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 055.0 | BAFFLE TEMPERATURE | L6870 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R09 | R09-TT-003 | R09-T-003 | PKG | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | BAFFLE TEMPERATURE | 6870 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R09 | R09-TE-004 | R09-T-004 | FLD | 107-CC | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022325 |  | JACKET INLET TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
R09 | R09-TI-004A | R09-T-004 | PCS | 107-CC | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6871; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TI-004B | R09-T-004 | FLD | 107-CC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 055.0 | JACKET INLET TEMP. | L6871 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R09 | R09-TT-004 | R09-T-004 | FLD | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | JACKET INLET TEMP. | 6871 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R09 | R09-TE-005 | R09-T-005 | FLD | 107-CC | ELEMENT - TEMPERATURE - RTD | 100-P-PT1A-H-9022303 |  | PC1 INLET TEMPERATURE | PKG: L6561; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TI-005 | R09-T-005 | PCS | 107-CC | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R09 | R09-TT-005 | R09-T-005 | FLD | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | PC1 INLET TEMPERATURE | 6561 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R09 | R09-TI-005A | R09-T-005A | [6 empty] | PKG: L6561; REQ: By request
R09 | R09-TE-006 | R09-T-006 | FLD | 107-CC | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9022310 |  | VC1 OFF GAS TEMPERATURE | PKG: L6562; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R09 | R09-TI-006A | R09-T-006 | PCS | 107-CC | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6562; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R09 | R09-TI-006B | R09-T-006 | FLD | 107-CC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R09 | 055.0 | VC1 OFF GAS TEMPERATURE | L6562 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R09 | R09-TT-006 | R09-T-006 | FLD | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | VC1 OFF GAS TEMPERATURE | 6562 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R09 | R09-TE-007 | R09-T-007 | FLD | 107-CC | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9022317 |  | VC1 HTF RTN TEMPERATURE | PKG: L6563; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TIC-007 | R09-T-007 | PCS | 107-CC | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TT-007 | R09-T-007 | FLD | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | VC1 HTF RTN TEMPERATURE | 6563 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R09 | R09-TE-008 | R09-T-008 | FLD | 107-CC | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-C-9022314 |  | PC1 HTF RTN TEMPERATURE | PKG: L6564; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TIC-008 | R09-T-008 | PCS | 107-CC | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TT-008 | R09-T-008 | FLD | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | PC1 HTF RTN TEMPERATURE | 6564 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R09 | R09-TE-009 | R09-T-009 | FLD | 107-CC | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9022302 |  | DISTILLATE RTN TEMP. | PKG: L6565; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TI-009A | R09-T-009 | PCS | 107-CC | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | PKG: L6565; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TI-009B | R09-T-009 | FLD | 107-CC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 055.0 | DISTILLATE RTN TEMP. | L6565 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R09 | R09-TT-009 | R09-T-009 | FLD | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | DISTILLATE RTN TEMP. | 6565 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R09 | R09-TE-010 | R09-T-010 | FLD | 107-CC | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022328 |  | OUTLET TEMPERATURE | PKG: L6566; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TI-010A | R09-T-010 | PCS | 107-CC | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6566; REQ: By request |  |  | 0 | [7 empty] | 01
R09 | R09-TI-010B | R09-T-010 | FLD | 107-CC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R09 | 055.0 | OUTLET TEMPERATURE | L6566 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R09 | R09-TT-010 | R09-T-010 | FLD | 107-CC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 055.0 | OUTLET TEMPERATURE | 6566 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R09 | R09-YA-001 | R09-Y-001 | PCS | 107-CC | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R09 | R09-YS-001 | R09-Y-001 | FUT | 107-CC | COMMON ALARM | R09 GAS SEAL ASSEMBLY | 055.0 | AGITATOR SEAL COMMON ALARM | PKG: 8693; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP2 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R10 | R10-AG-001 | R10-A-001 | PKG | 107-CD | SPEED MOORE DISPLAY |  | 056.0 | AGITATOR | PKG: L6950; REF: REF; REQ: By request | [10 empty] | 34
R10 | R10-BD-001 | R10-B-001 | FLD | 107-CD | RUPTURE DISC | 150-P-PT1A-H-9022403 | 056.0 | BURSTING DISC | 6743 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R10 | R10-YI-001 | R10-B-001 | PCS | 107-CD | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-CV-001 | R10-C-001 | PKG | 107-CD | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R10/K/100 | 056.0 | BOTTOM OUTLET VALVE | 8794 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R10 | R10-CY-001 | R10-C-001 | PKG | 107-CD | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP2 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R10 | R10-ZSC-001 | R10-C-001 | PKG | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R10 | R10-ZSO-001 | R10-C-001 | PKG | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R10 | R10-CV-004 | R10-C-004 | FLD | 107-CD | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9022430 | 056.0 | NITROGEN SUPPLY | 6788 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R10 | R10-CV-005 | R10-C-005 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022411 | 056.0 | SCRUBBER 01 | 7205 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-CY-005 | R10-C-005 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-005 | R10-C-005 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-005 | R10-C-005 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-006 | R10-C-006 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022410 | 056.0 | SCRUBBER 02 | 7206 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-CY-006 | R10-C-006 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-006 | R10-C-006 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-006 | R10-C-006 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-007 | R10-C-007 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9022438 | 056.0 | PROCESS VACUUM | 7321 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-CY-007 | R10-C-007 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-007 | R10-C-007 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-007 | R10-C-007 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-008 | R10-C-008 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9022437 | 056.0 | HOUSE VACUUM | 7270 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-CY-008 | R10-C-008 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-008 | R10-C-008 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-008 | R10-C-008 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-009 | R10-C-009 | FLD | 107-CD | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029429 | 056.0 | COLD HTF SUPPLY | 7537 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R10 | R10-CY-009 | R10-C-009 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-009 | R10-C-009 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-009 | R10-C-009 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-010 | R10-C-010 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029165 | 056.0 | HOT HTF SUPPLY | 7523 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R10 | R10-ZSC-010 | R10-C-010 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-010 | R10-C-010 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-011 | R10-C-011 | FLD | 107-CD | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9022423 | 056.0 | HOT HTF RTN | 6378 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R10 | R10-CV-012 | R10-C-012 | FLD | 107-CD | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9022456 | 056.0 | COLD HTF RTN | 6390 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R10 | R10-CV-014 | R10-C-014 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9022459 | 056.0 | N2 TO BOTTOM OUTLET | 7146 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-CY-014 | R10-C-014 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-014 | R10-C-014 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-014 | R10-C-014 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-015 | R10-C-015 | FLD | 107-CD | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9022414 | 056.0 | PC1 TEMPERED HTF RTN | 6431 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R10 | R10-CV-016 | R10-C-016 | FLD | 107-CD | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9022417 | 056.0 | VC1 COLD HTF RTN | 6437 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R10 | R10-CV-018 | R10-C-018 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022405 | 056.0 | DISTILLATE VENT LINE | 7207 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-CY-018 | R10-C-018 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-018 | R10-C-018 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-018 | R10-C-018 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-019 | R10-C-019 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022863 | 056.0 | LIQUID INLET | 7241 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-CY-019 | R10-C-019 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-019 | R10-C-019 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-019 | R10-C-019 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-021 | R10-C-021 | FLD | 107-CD | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9022410 | 056.0 | +VE PRESSURE CONTROL | 6809 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R10 | R10-CV-022 | R10-C-022 | FLD | 107-CD | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9022437 | 056.0 | -VE PRESSURE CONTROL | 6830 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R10 | R10-CV-024 | R10-C-024 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9022467 | 056.0 | SOLIDS INLET | 7349 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-CX-024 | R10-C-024 | SGS | 107-CD | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R10 | R10-CY-024 | R10-C-024 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED | 056.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-024 | R10-C-024 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-024 | R10-C-024 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-CV-025 | R10-C-025 | FLD | 107-CD | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9022410 | 056.0 | SOLIDS ADDITION VENT | 7296 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-CX-025 | R10-C-025 | SGS | 107-CD | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R10 | R10-CY-025 | R10-C-025 | FLD | 107-CD | SOLENOID VALVE | RACK MOUNTED | 056.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R10 | R10-ZSC-025 | R10-C-025 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-ZSO-025 | R10-C-025 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 056.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-DIC-001 | R10-D-001 | PCS | 107-CD | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R10 | R10-DS-001 | R10-D-001 | MCC | 107-CD | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R10 | R10-DY-001 | R10-D-001 | MCC | 107-CD | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R10 | R10-DYC-001 | R10-D-001 | MCC | 107-CD | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 056.0 | JACKET PUMP | 8751 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R10 | R10-HS-002 | R10-H-002 | FLD | 107-CD | SWITCH - HAND OP. | ADJ TO R10 | 056.0 | CRASH COOL | 6996 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP2 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R10 | R10-HV-008 | R10-H-008 | FLD | 107-CD | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028694 | 056.0 | N2 PRESSURE SELECT | 7478 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R10 | R10-HZSC-008 | R10-H-008 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R10 | R10-HZSO-008 | R10-H-008 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R10 | R10-HV-009 | R10-H-009 | FLD | 107-CD | HAND VALVE | 25-P-PT1A-0-9022462 | 056.0 | AUX. INLET | 7398 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-HZSC-009 | R10-H-009 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-HZSO-009 | R10-H-009 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R10 | R10-HV-010 | R10-H-010 | FLD | 107-CD | HAND VALVE | 40-P-PT1A-0-9022863 | 056.0 | REAGENTS INLET | 7369 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R10 | R10-HZSC-010 | R10-H-010 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-HZSO-010 | R10-H-010 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-HV-012 | R10-H-012 | FLD | 107-CD | HAND VALVE | 25-P-PT1A-0-9022859 | 056.0 | SOLVENTS INLET | 7399 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-HZSC-012 | R10-H-012 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-HZSO-012 | R10-H-012 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R10 | R10-HV-013 | R10-H-013 | FLD | 107-CD | HAND VALVE | 40-P-PT1A-0-9022863 | 056.0 | SLURRIES INLET | 7449 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R10 | R10-HZSC-013 | R10-H-013 | FLD | 107-CD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-HZSO-013 | R10-H-013 | FLD | 107-CD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R10 | R10-II-002 | R10-I-002 | PCS | 107-CD | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R10 | R10-IT-002 | R10-I-002 | MCC | 107-CD | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 056.0 | AGITATOR CURRENT | 8766 | 0 to 10 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP2 | [6 empty] | 01
R10 | R10-LI-001 | R10-L-001 | PCS | 107-CD | INDICATOR - LEVEL |  |  | HIGH LEVEL | PKG: L6645; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-LT-001 | R10-L-001 | FLD | 107-CD | TRANSMITTER - LEVEL | R10/N4/100 | 056.0 | HIGH LEVEL | 6645 | 0-1600 litres | +/- 2% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | VEGA | VEGAPULS 63 | KL0028 | TI702-SP-5009 |  |  | 01
R10 | R10-LG-002 | R10-L-002 | PKG | 107-CD | LEVEL GAUGE | AGITATOR SEAL POT | 056.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R10 | R10-PIC-001 | R10-P-001 | PCS | 107-CD | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: L7022; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-PIT-001 | R10-P-001 | FLD | 107-CD | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9022403 | 056.0 | PRESSURE | 7022 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R10 | R10-PI-002 | R10-P-002 | PCS | 107-CD | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6669; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R10 | R10-PIT-002 | R10-P-002 | FLD | 107-CD | TRANSMITTER - PRESSURE - DIAPHRAGM | 150 P-PT1A-H-9022403 | 056.0 | PRESSURE | 6669 | -1 to 2.3 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R10 | R10-PAH-003 | R10-P-003 | PCS | 107-CD | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-PSH-003 | R10-P-003 | FLD | 107-CD | SWITCH - PRESSURE - DIAPHRAGM - HI | 150-P-PT1A-H-9022403 | 056.0 | HIGH PRESSURE | 6670 | set @ 2.2 barg | +/- 1% | SHE | By request | C |  | I.S | DI |  |  | 32 | GP2 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R10 | R10-PI-004 | R10-P-004 | FLD | 107-CD | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9022430 | 056.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R10 | R10-PI-007 | R10-P-007 | FLD | 107-CD | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029429 | 056.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R10 | R10-PI-008 | R10-P-008 | FLD | 107-CD | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9022425 | 056.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R10 | R10-PSV-012 | R10-P-012 | FLD | 107-CD | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9022455 | 056.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R10 | R10-PSV-013 | R10-P-013 | FLD | 107-CD | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022453 | 056.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R10 | R10-PSV-014 | R10-P-014 | FLD | 107-CD | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022454 | 056.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R10 | R10-PRV-015 | R10-P-015 | FLD | 107-CD | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028693 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R10 | R10-PI-016 | R10-P-016 | PKG | 107-CD | PRESSURE GAUGE | AGITATOR SEAL POT | 056.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 25 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R10 | R10-SE-001 | R10-S-001 | PKG | 107-CD | ELEMENT - SPEED | AGITATOR SHAFT | 056.0 | AGITATOR | 6950 | 0 to 153 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP2 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R10 | R10-SI-001A | R10-S-001 | PCS | 107-CD | INDICATOR - SPEED |  |  | AGITATOR | PKG: L6950; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-SI-001B | R10-S-001 | FLD | 107-CD | INDICATOR - SPEED | ADJ TO R10 AGITATOR | 056.0 | AGITATOR | L6950 | 0 to 200 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP2 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R10 | R10-DS-002 | R10-S-002 | MCC | 107-CD | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R10 | R10-DY-002 | R10-S-002 | MCC | 107-CD | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R10 | R10-DYC-002 | R10-S-002 | MCC | 107-CD | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 056.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R10 | R10-SC-002 | R10-S-002 | MCC | 107-CD | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 056.0 | AGITATOR | 8766 | 0 to 160 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP2 |  |  |  |  | SET Min 30 rpm & Max 153 rpm |  | 01
R10 | R10-SIC-002 | R10-S-002 | PCS | 107-CD | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | PKG: L6950; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TE-001 | R10-T-001 | PKG | 107-CD | ELEMENT - TEMPERATURE - RTD | WITH R10-CV-001 |  | TEMPERATURE #1 | PKG: L6872; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R10 | R10-TI-001A | R10-T-001 | PCS | 107-CD | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6872; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R10 | R10-TI-001B | R10-T-001 | FLD | 107-CD | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R10 | 056.0 | TEMPERATURE #1 | L6872 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R10 | R10-TT-001 | R10-T-001 | PKG | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | TEMPERATURE #1 | 6872 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R10 | R10-TE-002 | R10-T-002 | PKG | 107-CD | ELEMENT - TEMPERATURE - RTD | WITH R10-CV-001 |  | TEMPERATURE #2 | PKG: L6873; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R10 | R10-TI-002A | R10-T-002 | PCS | 107-CD | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6873; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R10 | R10-TI-002B | R10-T-002 | FLD | 107-CD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 056.0 | TEMPERATURE #2 | L6873 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R10 | R10-TT-002 | R10-T-002 | PKG | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | TEMPERATURE #2 | 6873 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R10 | R10-TE-003 | R10-T-003 | PKG | 107-CD | ELEMENT - TEMPERATURE - RTD | R10/N6/100 |  | BAFFLE TEMPERATURE | PKG: L6874; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R10 | R10-TI-003A | R10-T-003 | PCS | 107-CD | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6874; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R10 | R10-TI-003B | R10-T-003 | FLD | 107-CD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 056.0 | BAFFLE TEMPERATURE | L6874 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R10 | R10-TT-003 | R10-T-003 | PKG | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | BAFFLE TEMPERATURE | 6874 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R10 | R10-TE-004 | R10-T-004 | FLD | 107-CD | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022425 |  | JACKET INLET TEMP. | PKG: L6875; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TI-004A | R10-T-004 | PCS | 107-CD | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6875; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TI-004B | R10-T-004 | FLD | 107-CD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 056.0 | JACKET INLET TEMP. | L6875 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R10 | R10-TT-004 | R10-T-004 | FLD | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | JACKET INLET TEMP. | 6875 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R10 | R10-TE-005 | R10-T-005 | FLD | 107-CD | ELEMENT - TEMPERATURE - RTD | 150-P-PT1A-H-9022403 |  | PC1 INLET TEMPERATURE | PKG: L6567; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TI-005 | R10-T-005 | PCS | 107-CD | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R10 | R10-TT-005 | R10-T-005 | FLD | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | PC1 INLET TEMPERATURE | 6567 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R10 | R10-TI-005A | R10-T-005A | [6 empty] | PKG: L6567; REQ: By request
R10 | R10-TE-006 | R10-T-006 | FLD | 107-CD | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9022410 |  | VC1 OFF GAS TEMPERATURE | PKG: L6568; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R10 | R10-TI-006A | R10-T-006 | PCS | 107-CD | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6568; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R10 | R10-TI-006B | R10-T-006 | FLD | 107-CD | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R10 | 056.0 | VC1 OFF GAS TEMPERATURE | L6568 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R10 | R10-TT-006 | R10-T-006 | FLD | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | VC1 OFF GAS TEMPERATURE | 6568 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R10 | R10-TE-007 | R10-T-007 | FLD | 107-CD | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9022417 |  | VC1 HTF RTN TEMPERATURE | PKG: L6569; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TIC-007 | R10-T-007 | PCS | 107-CD | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | PKG: L6569; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TT-007 | R10-T-007 | FLD | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | VC1 HTF RTN TEMPERATURE | 6569 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R10 | R10-TE-008 | R10-T-008 | FLD | 107-CD | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-902414 |  | PC1 HTF RTN TEMPERATURE | PKG: L6570; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TIC-008 | R10-T-008 | PCS | 107-CD | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | PKG: L6570; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TT-008 | R10-T-008 | FLD | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | PC1 HTF RTN TEMPERATURE | 6570 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R10 | R10-TE-009 | R10-T-009 | FLD | 107-CD | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9022402 |  | DISTILLATE RTN TEMP. | PKG: L6571; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TI-009A | R10-T-009 | PCS | 107-CD | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | PKG: L6571; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TI-009B | R10-T-009 | FLD | 107-CD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 056.0 | DISTILLATE RTN TEMP. | L6950 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R10 | R10-TT-009 | R10-T-009 | FLD | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | DISTILLATE RTN TEMP. | 6571 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R10 | R10-TE-010 | R10-T-010 | FLD | 107-CD | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022428 |  | OUTLET TEMPERATURE | PKG: L6572; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TI-010A | R10-T-010 | PCS | 107-CD | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6572; REQ: By request |  |  | 0 | [7 empty] | 01
R10 | R10-TI-010B | R10-T-010 | FLD | 107-CD | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R10 | 056.0 | OUTLET TEMPERATURE | L6572 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R10 | R10-TT-010 | R10-T-010 | FLD | 107-CD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 056.0 | OUTLET TEMPERATURE | 6572 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R10 | R10-YA-001 | R10-Y-001 | PCS | 107-CD | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R10 | R10-YS-001 | R10-Y-001 | FUT | 107-CD | COMMON ALARM | R10 GAS SEAL ASSEMBLY | 056.0 | AGITATOR SEAL COMMON ALARM | PKG: 8697; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP2 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R11 | R11-AG-001 | R11-A-001 | PKG | 107-CE | SPEED MOORE DISPLAY |  | 057.0 | AGITATOR | REF: REF; REQ: REQ | [10 empty] | 34
R11 | R11-BD-001 | R11-B-001 | FLD | 107-CE | RUPTURE DISC | 150-P-PT1A-0-9022503 | 057.0 | BURSTING DISC | 6744 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R11 | R11-YI-001 | R11-B-001 | PCS | 107-CE | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-CV-001 | R11-C-001 | PKG | 107-CE | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R11/K/100 | 057.0 | BOTTOM OUTLET VALVE | 8795 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R11 | R11-CY-001 | R11-C-001 | PKG | 107-CE | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP2 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R11 | R11-ZSC-001 | R11-C-001 | PKG | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R11 | R11-ZSO-001 | R11-C-001 | PKG | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R11 | R11-CV-004 | R11-C-004 | FLD | 107-CE | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9022530 | 057.0 | NITROGEN SUPPLY | 6789 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R11 | R11-CV-005 | R11-C-005 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022511 | 057.0 | SCRUBBER 01 | 7208 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-CY-005 | R11-C-005 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-005 | R11-C-005 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-005 | R11-C-005 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-006 | R11-C-006 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022510 | 057.0 | SCRUBBER 02 | 7209 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-CY-006 | R11-C-006 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-006 | R11-C-006 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-006 | R11-C-006 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-007 | R11-C-007 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9022538 | 057.0 | PROCESS VACUUM | 7322 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-CY-007 | R11-C-007 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-007 | R11-C-007 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-007 | R11-C-007 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-008 | R11-C-008 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9022537 | 057.0 | HOUSE VACUUM | 7271 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-CY-008 | R11-C-008 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-008 | R11-C-008 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-008 | R11-C-008 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-009 | R11-C-009 | FLD | 107-CE | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-D-9029419 | 057.0 | COLD HTF SUPPLY | 7538 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R11 | R11-CY-009 | R11-C-009 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-009 | R11-C-009 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-009 | R11-C-009 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-010 | R11-C-010 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029160 | 057.0 | HOT HTF SUPPLY | 7514 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R11 | R11-ZSC-010 | R11-C-010 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-010 | R11-C-010 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-011 | R11-C-011 | FLD | 107-CE | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9022523 | 057.0 | HOT HTF RTN | 6379 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R11 | R11-CV-012 | R11-C-012 | FLD | 107-CE | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9022556 | 057.0 | COLD HTF RTN | 6391 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R11 | R11-CV-014 | R11-C-014 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9022559 | 057.0 | N2 TO BOTTOM OUTLET | 7147 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-CY-014 | R11-C-014 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-014 | R11-C-014 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-014 | R11-C-014 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-015 | R11-C-015 | FLD | 107-CE | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9022514 | 057.0 | PC1 TEMPERED HTF RTN | 6432 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R11 | R11-CV-016 | R11-C-016 | FLD | 107-CE | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9022517 | 057.0 | VC1 COLD HTF RTN | 6438 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R11 | R11-CV-018 | R11-C-018 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022505 | 057.0 | DISTILLATE VENT LINE | 7210 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-CY-018 | R11-C-018 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-018 | R11-C-018 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-018 | R11-C-018 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-019 | R11-C-019 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022821 | 057.0 | LIQUID INLET | 7242 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-CY-019 | R11-C-019 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-019 | R11-C-019 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-019 | R11-C-019 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-021 | R11-C-021 | FLD | 107-CE | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9022510 | 057.0 | +VE PRESSURE CONTROL | 6810 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R11 | R11-CV-022 | R11-C-022 | FLD | 107-CE | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9022537 | 057.0 | -VE PRESSURE CONTROL | 6831 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R11 | R11-CV-024 | R11-C-024 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9022567 | 057.0 | SOLIDS INLET | 7350 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-CX-024 | R11-C-024 | SGS | 107-CE | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R11 | R11-CY-024 | R11-C-024 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED | 057.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-024 | R11-C-024 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-024 | R11-C-024 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-CV-025 | R11-C-025 | FLD | 107-CE | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9022510 | 057.0 | SOLIDS ADDITION VENT | 7297 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-CX-025 | R11-C-025 | SGS | 107-CE | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R11 | R11-CY-025 | R11-C-025 | FLD | 107-CE | SOLENOID VALVE | RACK MOUNTED | 057.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R11 | R11-ZSC-025 | R11-C-025 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-ZSO-025 | R11-C-025 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 057.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-DIC-001 | R11-D-001 | PCS | 107-CE | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-DS-001 | R11-D-001 | MCC | 107-CE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R11 | R11-DY-001 | R11-D-001 | MCC | 107-CE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R11 | R11-DYC-001 | R11-D-001 | MCC | 107-CE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 057.0 | JACKET PUMP | 8754 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R11 | R11-HS-002 | R11-H-002 | FLD | 107-CE | SWITCH - HAND OP. | ADJ TO R11 | 057.0 | CRASH COOL | 6997 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP2 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R11 | R11-HV-008 | R11-H-008 | FLD | 107-CE | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028669 | 057.0 | N2 PRESSURE SELECT | 7479 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R11 | R11-HZSC-008 | R11-H-008 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R11 | R11-HZSO-008 | R11-H-008 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R11 | R11-HV-009 | R11-H-009 | FLD | 107-CE | HAND VALVE | 25-P-PT1A-0-9022562 | 057.0 | AUX. INLET | 7400 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-HZSC-009 | R11-H-009 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-HZSO-009 | R11-H-009 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R11 | R11-HV-010 | R11-H-010 | FLD | 107-CE | HAND VALVE | 40-P-PT1A-0-9022821 | 057.0 | REAGENTS INLET | 7370 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R11 | R11-HZSC-010 | R11-H-010 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-HZSO-010 | R11-H-010 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-HV-012 | R11-H-012 | FLD | 107-CE | HAND VALVE | 25-P-PT1A-0-9022820 | 057.0 | SOLVENTS INLET | 7401 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-HZSC-012 | R11-H-012 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-HZSO-012 | R11-H-012 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R11 | R11-HV-013 | R11-H-013 | FLD | 107-CE | HAND VALVE | 40-P-PT1A-0-9022821 | 057.0 | SLURRIES INLET | 7450 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R11 | R11-HZSC-013 | R11-H-013 | FLD | 107-CE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-HZSO-013 | R11-H-013 | FLD | 107-CE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R11 | R11-II-002 | R11-I-002 | PCS | 107-CE | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-IT-002 | R11-I-002 | MCC | 107-CE | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 057.0 | AGITATOR CURRENT | 8767 | 0 to 10 amp | +/- 1% | REF | REQ | C |  | N.I.S | AI |  |  | 13 | GP2 | [6 empty] | 01
R11 | R11-LI-001 | R11-L-001 | PCS | 107-CE | INDICATOR - LEVEL |  |  | HIGH LEVEL | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-LT-001 | R11-L-001 | FLD | 107-CE | TRANSMITTER - LEVEL | R11/N4/100 | 057.0 | HIGH LEVEL | 6648 | 0-1600 litres | +/- 2% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | VEGA | VEGAPULS 63 | KL0028 | TI702-SP-5009 |  |  | 01
R11 | R11-LG-002 | R11-L-002 | PKG | 107-CE | LEVEL GAUGE | AGITATOR SEAL POT | 057.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
R11 | R11-PIC-001 | R11-P-001 | PCS | 107-CE | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-PIT-001 | R11-P-001 | FLD | 107-CE | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9022503 | 057.0 | PRESSURE | 7023 | -1 to 2.3 barg | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R11 | R11-PI-002 | R11-P-002 | PCS | 107-CE | INDICATOR - PRESSURE |  |  | PRESSURE | -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R11 | R11-PIT-002 | R11-P-002 | FLD | 107-CE | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9022503 | 057.0 | PRESSURE | 6672 | -1 to 2.3 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R11 | R11-PAH-003 | R11-P-003 | PCS | 107-CE | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-PSH-003 | R11-P-003 | FLD | 107-CE | SWITCH - PRESSURE - DIAPHRAGM - HI | 150-P-PT1A-H-9022503 | 057.0 | HIGH PRESSURE | 6673 | set @ 2.2 barg | +/- 1% | SHE | REQ | C |  | I.S | DI |  |  | 32 | GP2 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R11 | R11-PI-004 | R11-P-004 | FLD | 107-CE | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-0-9022530 | 057.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R11 | R11-PI-007 | R11-P-007 | FLD | 107-CE | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029419 | 057.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R11 | R11-PI-008 | R11-P-008 | FLD | 107-CE | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9022525 | 057.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R11 | R11-PSV-012 | R11-P-012 | FLD | 107-CE | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9022555 | 057.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R11 | R11-PSV-013 | R11-P-013 | FLD | 107-CE | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022553 | 057.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R11 | R11-PSV-014 | R11-P-014 | FLD | 107-CE | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022554 | 057.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R11 | R11-PRV-015 | R11-P-015 | FLD | 107-CE | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028668 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R11 | R11-PI-016 | R11-P-016 | PKG | 107-CE | PRESSURE GAUGE | AGITATOR SEAL POT | 057.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 25 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R11 | R11-SE-001 | R11-S-001 | PKG | 107-CE | ELEMENT - SPEED | AGITATOR SHAFT | 057.0 | AGITATOR | 6951 | 0 to 118 rpm | - | REF | REQ | C |  | I.S | DI |  |  | 33 | GP2 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R11 | R11-SI-001A | R11-S-001 | PCS | 107-CE | INDICATOR - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-SI-001B | R11-S-001 | FLD | 107-CE | INDICATOR - SPEED | ADJ TO R11 AGITATOR | 057.0 | AGITATOR |  | 0 to 200 rpm | +/- 1% | REF | REQ | C |  | I.S | AO |  |  | 21 | GP2 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R11 | R11-DS-002 | R11-S-002 | MCC | 107-CE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R11 | R11-DY-002 | R11-S-002 | MCC | 107-CE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R11 | R11-DYC-002 | R11-S-002 | MCC | 107-CE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 057.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R11 | R11-SC-002 | R11-S-002 | MCC | 107-CE | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 057.0 | AGITATOR | 8767 | 0 to 120 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP2 |  |  |  |  | SET Min 24 rpm & Max 118 rpm |  | 01
R11 | R11-SIC-002 | R11-S-002 | PCS | 107-CE | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TE-001 | R11-T-001 | PKG | 107-CE | ELEMENT - TEMPERATURE - RTD | WITH R11-CV-001 |  | TEMPERATURE #1 | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TI-001A | R11-T-001 | PCS | 107-CE | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-TI-001B | R11-T-001 | FLD | 107-CE | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R11 | 057.0 | TEMPERATURE #1 |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R11 | R11-TT-001 | R11-T-001 | PKG | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | TEMPERATURE #1 | 6876 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R11 | R11-TE-002 | R11-T-002 | PKG | 107-CE | ELEMENT - TEMPERATURE - RTD | WITH R11-CV-001 |  | TEMPERATURE #2 | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-TI-002A | R11-T-002 | PCS | 107-CE | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-TI-002B | R11-T-002 | FLD | 107-CE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 057.0 | TEMPERATURE #2 |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R11 | R11-TT-002 | R11-T-002 | PKG | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | TEMPERATURE #2 | 6877 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R11 | R11-TE-003 | R11-T-003 | PKG | 107-CE | ELEMENT - TEMPERATURE - RTD | R11/N6/100 |  | BAFFLE TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-TI-003A | R11-T-003 | PCS | 107-CE | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-TI-003B | R11-T-003 | FLD | 107-CE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 057.0 | BAFFLE TEMPERATURE |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R11 | R11-TT-003 | R11-T-003 | PKG | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | BAFFLE TEMPERATURE | 6878 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R11 | R11-TE-004 | R11-T-004 | FLD | 107-CE | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022525 |  | JACKET INLET TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-TI-004A | R11-T-004 | PCS | 107-CE | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-TI-004B | R11-T-004 | FLD | 107-CE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 057.0 | JACKET INLET TEMP. |  | -30 to 170 degC | +/- 1% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R11 | R11-TT-004 | R11-T-004 | FLD | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | JACKET INLET TEMP. | 6879 | -30 to 170 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R11 | R11-TE-005 | R11-T-005 | FLD | 107-CE | ELEMENT - TEMPERATURE - RTD | 150-P-PT1A-H-9022503 |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TI-005 | R11-T-005 | PCS | 107-CE | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TT-005 | R11-T-005 | FLD | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | PC1 INLET TEMPERATURE | 6573 | -20 to 180 degC | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R11 | R11-TE-006 | R11-T-006 | FLD | 107-CE | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9022510 |  | VC1 OFF GAS TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-TI-006A | R11-T-006 | PCS | 107-CE | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R11 | R11-TI-006B | R11-T-006 | FLD | 107-CE | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R11 | 057.0 | VC1 OFF GAS TEMPERATURE |  | -30 to 170 degC | +/- 1% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R11 | R11-TT-006 | R11-T-006 | FLD | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | VC1 OFF GAS TEMPERATURE | 6574 | -20 to 80 degC | +/- 1% | SHE | 6 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R11 | R11-TE-007 | R11-T-007 | FLD | 107-CE | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9022517 |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TIC-007 | R11-T-007 | PCS | 107-CE | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TT-007 | R11-T-007 | FLD | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | VC1 HTF RTN TEMPERATURE | 6575 | -30 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R11 | R11-TE-008 | R11-T-008 | FLD | 107-CE | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9022514 |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TIC-008 | R11-T-008 | PCS | 107-CE | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TT-008 | R11-T-008 | FLD | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | PC1 HTF RTN TEMPERATURE | 6576 | -20 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R11 | R11-TE-009 | R11-T-009 | FLD | 107-CE | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9022502 |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TI-009A | R11-T-009 | PCS | 107-CE | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TI-009B | R11-T-009 | FLD | 107-CE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 057.0 | DISTILLATE RTN TEMP. |  | -20 to 80 degC | +/- 0.5% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R11 | R11-TT-009 | R11-T-009 | FLD | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | DISTILLATE RTN TEMP. | 6577 | -20 to 80 degC | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R11 | R11-TE-010 | R11-T-010 | FLD | 107-CE | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022528 |  | OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TI-010A | R11-T-010 | PCS | 107-CE | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-TI-010B | R11-T-010 | FLD | 107-CE | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R11 | 057.0 | OUTLET TEMPERATURE |  | -30 to 170 degC | +/- 1% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R11 | R11-TT-010 | R11-T-010 | FLD | 107-CE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 057.0 | OUTLET TEMPERATURE | 6578 | -30 to 170 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R11 | R11-YA-001 | R11-Y-001 | PCS | 107-CE | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R11 | R11-YS-001 | R11-Y-001 | FUT | 107-CE | COMMON ALARM | R11 GAS SEAL ASSEMBLY | 057.0 | AGITATOR SEAL COMMON ALARM | PKG: 8698; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP2 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R12 | R12-AG-001 | R12-A-001 | PKG | 107-CF | SPEED MOORE DISPLAY |  | 058.0 | AGITATOR | PKG: L6952; REF: REF; REQ: By request | [10 empty] | 34
R12 | R12-BD-001 | R12-B-001 | FLD | 107-CF | RUPTURE DISC | 150-P-PT1A-H-9022603 | 058.0 | BURSTING DISC | 6745 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R12 | R12-YI-001 | R12-B-001 | PCS | 107-CF | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-CV-001 | R12-C-001 | PKG | 107-CF | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R12/K/100 | 058.0 | BOTTOM OUTLET VALVE | 8796 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R12 | R12-CY-001 | R12-C-001 | PKG | 107-CF | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | GP2 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R12 | R12-ZSC-001 | R12-C-001 | PKG | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R12 | R12-ZSO-001 | R12-C-001 | PKG | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R12 | R12-CV-004 | R12-C-004 | FLD | 107-CF | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9022630 | 058.0 | NITROGEN SUPPLY | 6790 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R12 | R12-CV-005 | R12-C-005 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022611 | 058.0 | SCRUBBER 01 | 7211 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-CY-005 | R12-C-005 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-005 | R12-C-005 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-005 | R12-C-005 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-006 | R12-C-006 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022610 | 058.0 | SCRUBBER 02 | 7212 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-CY-006 | R12-C-006 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-006 | R12-C-006 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-006 | R12-C-006 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-007 | R12-C-007 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9022638 | 058.0 | PROCESS VACUUM | 7323 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-CY-007 | R12-C-007 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-007 | R12-C-007 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-007 | R12-C-007 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-008 | R12-C-008 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9022637 | 058.0 | HOUSE VACUUM | 7272 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-CY-008 | R12-C-008 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-008 | R12-C-008 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-008 | R12-C-008 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-009 | R12-C-009 | FLD | 107-CF | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-C-9029431 | 058.0 | COLD HTF SUPPLY | 7539 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R12 | R12-CY-009 | R12-C-009 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-009 | R12-C-009 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-009 | R12-C-009 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-010 | R12-C-010 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029166 | 058.0 | HOT HTF SUPPLY | 7515 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R12 | R12-ZSC-010 | R12-C-010 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-010 | R12-C-010 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-011 | R12-C-011 | FLD | 107-CF | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9022623 | 058.0 | HOT HTF RTN | 6396 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R12 | R12-CV-012 | R12-C-012 | FLD | 107-CF | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9022656 | 058.0 | COLD HTF RTN | 6397 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R12 | R12-CV-014 | R12-C-014 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9022659 | 058.0 | N2 TO BOTTOM OUTLET | 7148 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-CY-014 | R12-C-014 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-014 | R12-C-014 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-014 | R12-C-014 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-015 | R12-C-015 | FLD | 107-CF | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9022614 | 058.0 | PC1 TEMPERED HTF RTN | 6441 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R12 | R12-CV-016 | R12-C-016 | FLD | 107-CF | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9022617 | 058.0 | VC1 COLD HTF RTN | 6442 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | GP2 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R12 | R12-CV-018 | R12-C-018 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9022605 | 058.0 | DISTILLATE VENT LINE | 7213 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-CY-018 | R12-C-018 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-018 | R12-C-018 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-018 | R12-C-018 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-019 | R12-C-019 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-C-9022831 | 058.0 | LIQUID INLET | 7243 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-CY-019 | R12-C-019 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-019 | R12-C-019 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-019 | R12-C-019 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-021 | R12-C-021 | FLD | 107-CF | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9022610 | 058.0 | +VE PRESSURE CONTROL | 6811 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R12 | R12-CV-022 | R12-C-022 | FLD | 107-CF | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9022637 | 058.0 | -VE PRESSURE CONTROL | 6832 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | GP2 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R12 | R12-CV-024 | R12-C-024 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-0-9022667 | 058.0 | SOLIDS INLET | 7351 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-CX-024 | R12-C-024 | SGS | 107-CF | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R12 | R12-CY-024 | R12-C-024 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED | 058.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-024 | R12-C-024 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-024 | R12-C-024 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-CV-025 | R12-C-025 | FLD | 107-CF | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9022610 | 058.0 | SOLIDS ADDITION VENT | 7298 | -- | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-CX-025 | R12-C-025 | SGS | 107-CF | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | GP2 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R12 | R12-CY-025 | R12-C-025 | FLD | 107-CF | SOLENOID VALVE | RACK MOUNTED | 058.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R12 | R12-ZSC-025 | R12-C-025 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-ZSO-025 | R12-C-025 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 058.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-DIC-001 | R12-D-001 | PCS | 107-CF | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R12 | R12-DS-001 | R12-D-001 | MCC | 107-CF | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R12 | R12-DY-001 | R12-D-001 | MCC | 107-CF | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R12 | R12-DYC-001 | R12-D-001 | MCC | 107-CF | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 058.0 | JACKET PUMP | 8768 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R12 | R12-HS-002 | R12-H-002 | FLD | 107-CF | SWITCH - HAND OP. | ADJ TO R12 | 058.0 | CRASH COOL | 6998 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | GP2 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R12 | R12-HV-008 | R12-H-008 | FLD | 107-CF | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028691 | 058.0 | N2 PRESSURE SELECT | 7480 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R12 | R12-HZSC-008 | R12-H-008 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R12 | R12-HZSO-008 | R12-H-008 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R12 | R12-HV-009 | R12-H-009 | FLD | 107-CF | HAND VALVE | 25-P-PT1A-0-9022662 | 058.0 | AUX. INLET | 7402 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-HZSC-009 | R12-H-009 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-HZSO-009 | R12-H-009 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R12 | R12-HV-010 | R12-H-010 | FLD | 107-CF | HAND VALVE | 25-P-PT1A-0-9022831 | 058.0 | REAGENTS INLET | 7371 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R12 | R12-HZSC-010 | R12-H-010 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-HZSO-010 | R12-H-010 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-HV-012 | R12-H-012 | FLD | 107-CF | HAND VALVE | 25-P-PT1A-0-9022831 | 058.0 | SOLVENTS INLET | 7403 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-HZSC-012 | R12-H-012 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-HZSO-012 | R12-H-012 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | GP2 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R12 | R12-HV-013 | R12-H-013 | FLD | 107-CF | HAND VALVE | 40-P-PT1A-0-9022861 | 058.0 | SLURRIES INLET | 7451 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R12 | R12-HZSC-013 | R12-H-013 | FLD | 107-CF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-HZSO-013 | R12-H-013 | FLD | 107-CF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R12 | R12-II-002 | R12-I-002 | PCS | 107-CF | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R12 | R12-IT-002 | R12-I-002 | MCC | 107-CF | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 058.0 | AGITATOR CURRENT | 8771 | 0 to 20 amp | +/- 1% | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP2 | [6 empty] | 01
R12 | R12-LI-001 | R12-L-001 | PCS | 107-CF | INDICATOR - LEVEL |  |  | HIGH LEVEL | PKG: L6651; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-LT-001 | R12-L-001 | FLD | 107-CF | TRANSMITTER - LEVEL | R12/N4/100 | 058.0 | HIGH LEVEL | 6651 | 0-2500 litres | +/- 2% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | VEGA | VEGAPULS 63 | KL0028 | TI702-SP-5009 |  |  | 01
R12 | R12-LG-002 | R12-L-002 | PKG | 107-CF | LEVEL GAUGE | AGITATOR SEAL POT | 058.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R12 | R12-PIC-001 | R12-P-001 | PCS | 107-CF | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | PKG: L7024; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-PIT-001 | R12-P-001 | FLD | 107-CF | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9022603 | 058.0 | PRESSURE | 7024 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 3051S2 | KP0001 | TI702-SP-5013 |  |  | 01
R12 | R12-PI-002 | R12-P-002 | PCS | 107-CF | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6675; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R12 | R12-PIT-002 | R12-P-002 | FLD | 107-CF | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9022603 | 058.0 | PRESSURE | 6675 | -1 to 2.3 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R12 | R12-PAH-003 | R12-P-003 | PCS | 107-CF | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-PSH-003 | R12-P-003 | FLD | 107-CF | SWITCH - PRESSURE - DIAPHRAGM - HI | 150-P-PT1A-H-9022603 | 058.0 | HIGH PRESSURE | 6676 | set @ 2.2 barg | +/- 1% | SHE | By request | C |  | I.S | DI |  |  | 32 | GP2 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R12 | R12-PI-004 | R12-P-004 | FLD | 107-CF | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-H-9022630 | 058.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R12 | R12-PI-007 | R12-P-007 | FLD | 107-CF | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9022624 | 058.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R12 | R12-PI-008 | R12-P-008 | FLD | 107-CF | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9022625 | 058.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R12 | R12-PSV-012 | R12-P-012 | FLD | 107-CF | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9022655 | 058.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R12 | R12-PSV-013 | R12-P-013 | FLD | 107-CF | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022653 | 058.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R12 | R12-PSV-014 | R12-P-014 | FLD | 107-CF | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9022654 | 058.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R12 | R12-PRV-015 | R12-P-015 | FLD | 107-CF | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028690 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R12 | R12-PI-016 | R12-P-016 | PKG | 107-CF | PRESSURE GAUGE | AGITATOR SEAL POT | 058.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 25 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
R12 | R12-SE-001 | R12-S-001 | PKG | 107-CF | ELEMENT - SPEED | AGITATOR SHAFT | 058.0 | AGITATOR | 6952 | 0 to 118 rpm | - | REF | By request | C |  | I.S | DI |  |  | 33 | GP2 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R12 | R12-SI-001A | R12-S-001 | PCS | 107-CF | INDICATOR - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R12 | R12-SI-001B | R12-S-001 | FLD | 107-CF | INDICATOR - SPEED | ADJ TO R12 AGITATOR | 058.0 | AGITATOR | L6952 | 0 to 200 rpm | +/- 1% | REF | By request | C |  | I.S | AO |  |  | 21 | GP2 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R12 | R12-DS-002 | R12-S-002 | MCC | 107-CF | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R12 | R12-DY-002 | R12-S-002 | MCC | 107-CF | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
R12 | R12-DYC-002 | R12-S-002 | MCC | 107-CF | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 058.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
R12 | R12-SC-002 | R12-S-002 | MCC | 107-CF | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 058.0 | AGITATOR | 8771 | 0 to 120 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | GP2 |  |  |  |  | SET Min 24 rpm & Max 118 rpm |  | 01
R12 | R12-SIC-002 | R12-S-002 | PCS | 107-CF | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | PKG: L6952; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TE-001 | R12-T-001 | PKG | 107-CF | ELEMENT - TEMPERATURE - RTD | WITH R12-CV-001 |  | TEMPERATURE #1 | PKG: L6880; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R12 | R12-TI-001A | R12-T-001 | PCS | 107-CF | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6880; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R12 | R12-TI-001B | R12-T-001 | FLD | 107-CF | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R12 | 058.0 | TEMPERATURE #1 | L6880 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R12 | R12-TT-001 | R12-T-001 | PKG | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | TEMPERATURE #1 | 6880 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R12 | R12-TE-002 | R12-T-002 | PKG | 107-CF | ELEMENT - TEMPERATURE - RTD | WITH R12-CV-001 |  | TEMPERATURE #2 | PKG: L6881; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R12 | R12-TI-002A | R12-T-002 | PCS | 107-CF | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6881; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R12 | R12-TI-002B | R12-T-002 | FLD | 107-CF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 058.0 | TEMPERATURE #2 | L6881 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R12 | R12-TT-002 | R12-T-002 | PKG | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | TEMPERATURE #2 | 6881 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R12 | R12-TE-003 | R12-T-003 | PKG | 107-CF | ELEMENT - TEMPERATURE - RTD | R12/N6/100 |  | BAFFLE TEMPERATURE | PKG: L6882; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R12 | R12-TI-003A | R12-T-003 | PCS | 107-CF | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6882; REF: GxP/SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R12 | R12-TI-003B | R12-T-003 | FLD | 107-CF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 058.0 | BAFFLE TEMPERATURE | L6882 | -30 to 170 degC | +/- 0.5% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R12 | R12-TT-003 | R12-T-003 | PKG | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | BAFFLE TEMPERATURE | 6882 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R12 | R12-TE-004 | R12-T-004 | FLD | 107-CF | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022625 |  | JACKET INLET TEMP. | PKG: L6883; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TI-004A | R12-T-004 | PCS | 107-CF | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | PKG: L6883; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TI-004B | R12-T-004 | FLD | 107-CF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 058.0 | JACKET INLET TEMP. | L6883 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R12 | R12-TT-004 | R12-T-004 | FLD | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | JACKET INLET TEMP. | 6883 | -30 to 170 degC | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R12 | R12-TE-005 | R12-T-005 | FLD | 107-CF | ELEMENT - TEMPERATURE - RTD | 150-P-PT1A-H-9022603 |  | PC1 INLET TEMPERATURE | PKG: L6579; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TI-005 | R12-T-005 | PCS | 107-CF | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R12 | R12-TT-005 | R12-T-005 | FLD | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | PC1 INLET TEMPERATURE | 6579 | -20 to 180 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R12 | R12-TI-005A | R12-T-005A | [6 empty] | PKG: L6579; REQ: By request
R12 | R12-TE-006 | R12-T-006 | FLD | 107-CF | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9022610 |  | VC1 OFF GAS TEMPERATURE | PKG: L6580; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R12 | R12-TI-006A | R12-T-006 | PCS | 107-CF | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6580; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R12 | R12-TI-006B | R12-T-006 | FLD | 107-CF | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R12 | 058.0 | VC1 OFF GAS TEMPERATURE | L6580 | -20 to 80 degC | +/- 1% | SHE | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R12 | R12-TT-006 | R12-T-006 | FLD | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | VC1 OFF GAS TEMPERATURE | 6580 | -20 to 80 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R12 | R12-TE-007 | R12-T-007 | FLD | 107-CF | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9022617 |  | VC1 HTF RTN TEMPERATURE | PKG: L6581; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TIC-007 | R12-T-007 | PCS | 107-CF | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | PKG: L6581; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TT-007 | R12-T-007 | FLD | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | VC1 HTF RTN TEMPERATURE | 6581 | -30 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R12 | R12-TE-008 | R12-T-008 | FLD | 107-CF | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9022614 |  | PC1 HTF RTN TEMPERATURE | PKG: L6582; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TIC-008 | R12-T-008 | PCS | 107-CF | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | PKG: L6582; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TT-008 | R12-T-008 | FLD | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | PC1 HTF RTN TEMPERATURE | 6582 | -20 to 70 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R12 | R12-TE-009 | R12-T-009 | FLD | 107-CF | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9022602 |  | DISTILLATE RTN TEMP. | PKG: L6583; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TI-009A | R12-T-009 | PCS | 107-CF | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | PKG: L6583; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TI-009B | R12-T-009 | FLD | 107-CF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 058.0 | DISTILLATE RTN TEMP. | L6583 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R12 | R12-TT-009 | R12-T-009 | FLD | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | DISTILLATE RTN TEMP. | 6583 | -20 to 80 degC | +/- 0.5% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R12 | R12-TE-010 | R12-T-010 | FLD | 107-CF | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9022628 |  | OUTLET TEMPERATURE | PKG: L6584; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TI-010A | R12-T-010 | PCS | 107-CF | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | PKG: L6584; REQ: By request |  |  | 0 | [7 empty] | 01
R12 | R12-TI-010B | R12-T-010 | FLD | 107-CF | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R12 | 058.0 | OUTLET TEMPERATURE | L6584 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R12 | R12-TT-010 | R12-T-010 | FLD | 107-CF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 058.0 | OUTLET TEMPERATURE | 6584 | -30 to 170 degC | +/- 1% | REF | By request | C |  | I.S | AI |  |  | 11 | GP2 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R12 | R12-YA-001 | R12-Y-001 | PCS | 107-CF | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R12 | R12-YS-001 | R12-Y-001 | FUT | 107-CF | COMMON ALARM | R12 GAS SEAL ASSEMBLY | 058.0 | AGITATOR SEAL COMMON ALARM | PKG: 8702; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | GP2 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R13 | R13-AG-001 | R13-A-001 | PKG | 107-DA | SPEED MOORE DISPLAY |  | 113.0 | AGITATOR | REF: REF; REQ: By request | [10 empty] | 34
R13 | R13-BD-001 | R13-B-001 | FLD | 107-DA | RUPTURE DISC | 100-P-PT1A-H-9023103 | 113.0 | BURSTING DISC | 8168 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | FG1 | BS&B | BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R13 | R13-YI-001 | R13-B-001 | PCS | 107-DA | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R13 | R13-CV-001 | R13-C-001 | PKG | 107-DA | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R13/K/100 | 113.0 | BOTTOM OUTLET VALVE | 8785 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R13 | R13-CY-001 | R13-C-001 | PKG | 107-DA | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | FG1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R13 | R13-ZSC-001 | R13-C-001 | PKG | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R13 | R13-ZSO-001 | R13-C-001 | PKG | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R13 | R13-CV-004 | R13-C-004 | FLD | 107-DA | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9023130 | 113.0 | NITROGEN SUPPLY | 8772 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R13 | R13-CV-005 | R13-C-005 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023111 | 113.0 | SCRUBBER 01 | 8185 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-CY-005 | R13-C-005 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-005 | R13-C-005 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-005 | R13-C-005 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-006 | R13-C-006 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023110 | 113.0 | SCRUBBER 02 | 8186 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-CY-006 | R13-C-006 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-006 | R13-C-006 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-006 | R13-C-006 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-007 | R13-C-007 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9023138 | 113.0 | PROCESS VACUUM | PKG: 8187; -: -; -: -; REQ: REQ; F: F |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-CY-007 | R13-C-007 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | REF: REF; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-007 | R13-C-007 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-007 | R13-C-007 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-008 | R13-C-008 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9023164 | 113.0 | HOUSE VACUUM | PKG: 8188; -: -; -: -; REQ: REQ; F: F |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-CY-008 | R13-C-008 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | REF: REF; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-008 | R13-C-008 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-008 | R13-C-008 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-009 | R13-C-009 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-C-9029523 | 113.0 | COLD HTF SUPPLY | 8230 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R13 | R13-CY-009 | R13-C-009 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-009 | R13-C-009 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-009 | R13-C-009 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-010 | R13-C-010 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029205 | 113.0 | HOT HTF SUPPLY | 8231 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R13 | R13-ZSC-010 | R13-C-010 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-010 | R13-C-010 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-011 | R13-C-011 | FLD | 107-DA | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9023123 | 113.0 | HOT HTF RTN | 8172 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R13 | R13-CV-012 | R13-C-012 | FLD | 107-DA | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9023156 | 113.0 | COLD HTF RTN | 8173 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R13 | R13-CV-013 | R13-C-013 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 50-HT-CS3A-D-9023125 | 113.0 | DUAL JACKET | 8232 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R13 | R13-CY-013 | R13-C-013 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-013 | R13-C-013 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-013 | R13-C-013 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-014 | R13-C-014 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9023159 | 113.0 | N2 TO BOTTOM OUTLET | 8189 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-CY-014 | R13-C-014 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-014 | R13-C-014 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-014 | R13-C-014 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-015 | R13-C-015 | FLD | 107-DA | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-C-9023114 | 113.0 | PC1 TEMPERED HTF RTN | 8174 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R13 | R13-CV-016 | R13-C-016 | FLD | 107-DA | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9023117 | 113.0 | VC1 COLD HTF RTN | 8175 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R13 | R13-CV-018 | R13-C-018 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023105 | 113.0 | DISTILLATE VENT LINE | 8190 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-CY-018 | R13-C-018 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-018 | R13-C-018 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-018 | R13-C-018 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-019 | R13-C-019 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023825 | 113.0 | LIQUID INLET | 8191 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-CY-019 | R13-C-019 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-019 | R13-C-019 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-019 | R13-C-019 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-021 | R13-C-021 | FLD | 107-DA | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9023110 | 113.0 | +VE PRESSURE CONTROL | 8773 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R13 | R13-CV-022 | R13-C-022 | FLD | 107-DA | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9023137 | 113.0 | -VE PRESSURE CONTROL | 8774 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R13 | R13-CV-024 | R13-C-024 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-0-9023167 | 113.0 | SOLIDS INLET | 8192 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-CX-024 | R13-C-024 | SGS | 107-DA | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R13 | R13-CY-024 | R13-C-024 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED | 113.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-024 | R13-C-024 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-024 | R13-C-024 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-CV-025 | R13-C-025 | FLD | 107-DA | BALL VALVE - ON/OFF - F.C. | 50-RV-CS1A-0-9023166 | 113.0 | SOLIDS ADDITION VENT | 8193 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-CX-025 | R13-C-025 | SGS | 107-DA | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R13 | R13-CY-025 | R13-C-025 | FLD | 107-DA | SOLENOID VALVE | RACK MOUNTED | 113.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R13 | R13-ZSC-025 | R13-C-025 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-ZSO-025 | R13-C-025 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 113.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-DIC-001 | R13-D-001 | PCS | 107-DA | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R13 | R13-DS-001 | R13-D-001 | MCC | 107-DA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R13 | R13-DY-001 | R13-D-001 | MCC | 107-DA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R13 | R13-DYC-001 | R13-D-001 | MCC | 107-DA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 113.0 | JACKET PUMP | 8775 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R13 | R13-FIAH-001 | R13-F-001 | PCS | 107-DA | FLOW INDICATOR - ALARM HIGH | R13 GAS SEAL ASSEMBLY | 113.0 | AGITATOR SEAL HIGH FLOW ALARM | REQ: By request | [10 empty] | 04
R13 | R13-FISH-002 | R13-F-001 | PKG | 107-DA | FLOW INDICATOR - SWITCH HIGH | R13 GAS SEAL ASSEMBLY | 113.0 | AGITATOR SEAL HIGH FLOW ALARM | REF: REF; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 0 | FG1 | PEPPERL + FUCHS | RC15-14-N3 |  | TI702-SP-5088 |  |  | 04
R13 | R13-FI-002 | R13-F-002 | PKG | 107-DA | VA FLOW METER | R13 GAS SEAL ASSEMBLY | 113.0 | AGITATOR SEAL N2 FLOW | REF: REF; REQ: By request; F: C |  |  | 0 |  | KROHNE | DK 800 |  |  | LOW RANGE FLOW |  | 04
R13 | R13-HS-002 | R13-H-002 | FLD | 107-DA | SWITCH - HAND OP. | ADJ TO R13 | 113.0 | CRASH COOL | 8226 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | FG1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R13 | R13-HV-008 | R13-H-008 | FLD | 107-DA | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028876 | 113.0 | N2 PRESSURE SELECT | 8229 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R13 | R13-HZSC-008 | R13-H-008 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R13 | R13-HZSO-008 | R13-H-008 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R13 | R13-HV-009 | R13-H-009 | FLD | 107-DA | HAND VALVE | 25-P-PT1A-0-9023162 | 113.0 | AUX. INLET | 8194 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-HZSC-009 | R13-H-009 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-HZSO-009 | R13-H-009 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R13 | R13-HV-010 | R13-H-010 | FLD | 107-DA | HAND VALVE | 40-P-PT1A-0-9023825 | 113.0 | REAGENTS INLET | 8195 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R13 | R13-HZSC-010 | R13-H-010 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-HZSO-010 | R13-H-010 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-HV-012 | R13-H-012 | FLD | 107-DA | HAND VALVE | 25-P-PT1A-0-9023882 | 113.0 | SOLVENTS INLET | 8196 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-HZSC-012 | R13-H-012 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-HZSO-012 | R13-H-012 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R13 | R13-HV-013 | R13-H-013 | FLD | 107-DA | HAND VALVE | 40-P-PT1A-0-9023825 | 113.0 | SLURRIES INLET | 8197 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R13 | R13-HZSC-013 | R13-H-013 | FLD | 107-DA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-HZSO-013 | R13-H-013 | FLD | 107-DA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R13 | R13-II-002 | R13-I-002 | PCS | 107-DA | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R13 | R13-IT-002 | R13-I-002 | MCC | 107-DA | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 113.0 | AGITATOR CURRENT | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 13 | FG1 | [6 empty] | 01
R13 | R13-LAH-001 | R13-L-001 | PCS | 107-DA | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L8245; -: On/off; -: On/off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R13 | R13-LE-001 | R13-L-001 | FLD | 107-DA | ELEMENT - LEVEL | 100-P-PT1A-H-9023103 | 113.0 | HIGH LEVEL | L8245 | On/off | On/off | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R13 | R13-LSH-001 | R13-L-001 | CPR | 107-DA | SWITCH - LEVEL - HIGH | 100-P-PT1A-H-9023103 | 113.0 | HIGH LEVEL | 8245 | On/off | On/off | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | FG1 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R13 | R13-PIC-001 | R13-P-001 | PCS | 107-DA | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R13 | R13-PIT-001 | R13-P-001 | FLD | 107-DA | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9023103 | 113.0 | PRESSURE | 8255 | -1 to 2.3 barg | +/- 1% | SHE | By request | C |  | I.S | AI |  |  | 11 | FG1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R13 | R13-PI-002 | R13-P-002 | PCS | 107-DA | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L8256; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R13 | R13-PIT-002 | R13-P-002 | FLD | 107-DA | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9023103 | 113.0 | PRESSURE | 8256 | -1 to 2.3 barg | +/-0.033barg | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R13 | R13-PAH-003 | R13-P-003 | PCS | 107-DA | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R13 | R13-PSH-003 | R13-P-003 | FLD | 107-DA | SWITCH - PRESSURE - DIAPHRAGM - HI | 100-P-PT1A-H-9023103 | 113.0 | HIGH PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 32 | FG1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R13 | R13-PI-004 | R13-P-004 | FLD | 107-DA | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9023130 | 113.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R13 | R13-PI-007 | R13-P-007 | FLD | 107-DA | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029523 | 113.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R13 | R13-PI-008 | R13-P-008 | FLD | 107-DA | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9023125 | 113.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R13 | R13-PSV-012 | R13-P-012 | FLD | 107-DA | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9023155 | 113.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R13 | R13-PSV-013 | R13-P-013 | FLD | 107-DA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023153 | 113.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R13 | R13-PSV-014 | R13-P-014 | FLD | 107-DA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023154 | 113.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R13 | R13-PIAL-015 | R13-P-015 | PCS | 107-DA | PRESSURE GAUGE - ALARM LOW | R13 GAS SEAL ASSEMBLY | 113.0 | AGITATOR SEAL LP ALARM | REQ: By request | [10 empty] | 04
R13 | R13-PISL-001 | R13-P-015 | PKG | 107-DA | PRESSURE GAUGE - SWITCH LOW | R13 GAS SEAL ASSEMBLY | 113.0 | AGITATOR SEAL LP ALARM | REF: REF; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 0 | FG1 | TURCK | SI2-K08-Y1X |  | TI702-SP-5170 |  |  | 04
R13 | R13-PRV-016 | R13-P-016 | PKG | 107-DA | CONTROL VALVE SELF ACTUATING | R13 GAS SEAL ASSEMBLY | 113.0 | N2 TO AGITATOR SEAL | -: Set @ 5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R13 | R13-SE-001 | R13-S-001 | PKG | 107-DA | ELEMENT - SPEED | AGITATOR SHAFT | 113.0 | AGITATOR | REF: REF; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 33 | FG1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R13 | R13-SI-001A | R13-S-001 | PCS | 107-DA | INDICATOR - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R13 | R13-SI-001B | R13-S-001 | FLD | 107-DA | INDICATOR - SPEED | ADJ TO R13 AGITATOR | 113.0 | AGITATOR | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AO |  |  | 21 | FG1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R13 | R13-DS-002 | R13-S-002 | MCC | 107-DA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R13 | R13-DY-002 | R13-S-002 | MCC | 107-DA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R13 | R13-DYC-002 | R13-S-002 | MCC | 107-DA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 113.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R13 | R13-SC-002 | R13-S-002 | MCC | 107-DA | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 113.0 | AGITATOR | 8780 | 0 to 160 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | FG1 |  |  |  |  | SET Min 31rpm & Max 153 rpm |  | 01
R13 | R13-SIC-002 | R13-S-002 | PCS | 107-DA | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R13 | R13-TE-001 | R13-T-001 | PKG | 107-DA | ELEMENT - TEMPERATURE - RTD | WITH R13-CV-001 |  | TEMPERATURE #1 | PKG: L8782; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R13 | R13-TI-001A | R13-T-001 | PCS | 107-DA | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L8782; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R13 | R13-TI-001B | R13-T-001 | FLD | 107-DA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R13 | 113.0 | TEMPERATURE #1 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R13 | R13-TT-001 | R13-T-001 | PKG | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | TEMPERATURE #1 | 8782 | -30 to 170 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R13 | R13-TE-002 | R13-T-002 | PKG | 107-DA | ELEMENT - TEMPERATURE - RTD | WITH R13-CV-001 |  | TEMPERATURE #2 | PKG: L8783; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R13 | R13-TI-002A | R13-T-002 | PCS | 107-DA | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L8783; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R13 | R13-TI-002B | R13-T-002 | FLD | 107-DA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 113.0 | TEMPERATURE #2 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R13 | R13-TT-002 | R13-T-002 | PKG | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | TEMPERATURE #2 | 8783 | -30 to 170 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R13 | R13-TE-003 | R13-T-003 | PKG | 107-DA | ELEMENT - TEMPERATURE - RTD | R13/N2/100 |  | BAFFLE TEMPERATURE | PKG: L8784; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R13 | R13-TI-003A | R13-T-003 | PCS | 107-DA | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L8784; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R13 | R13-TI-003B | R13-T-003 | FLD | 107-DA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 113.0 | BAFFLE TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R13 | R13-TT-003 | R13-T-003 | PKG | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | BAFFLE TEMPERATURE | 8784 | -30 to 170 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R13 | R13-TE-004 | R13-T-004 | FLD | 107-DA | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023125 |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 |  | MOORE INDUSTRIES | [5 empty] | 01
R13 | R13-TI-004A | R13-T-004 | PCS | 107-DA | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R13 | R13-TI-004B | R13-T-004 | FLD | 107-DA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 113.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BE324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R13 | R13-TT-004 | R13-T-004 | FLD | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R13 | R13-TE-005 | R13-T-005 | FLD | 107-DA | ELEMENT - TEMPERATURE - RTD | 100-P-PT1A-H-9023103 |  | PC1 INLET TEMPERATURE | REQ: By request |  |  | 0 |  | MOORE INDUSTRIES | [5 empty] | 30
R13 | R13-TI-005 | R13-T-005 | PCS | 107-DA | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | REQ: REQ |  |  | 0 | [7 empty] | 30
R13 | R13-TT-005 | R13-T-005 | FLD | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | PC1 INLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 30
R13 | R13-TI-005A | R13-T-005A | [6 empty] | REQ: By request
R13 | R13-TE-006 | R13-T-006 | FLD | 107-DA | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9023110 |  | VC1 OFF-GAS TEMPERATURE | PKG: L8160; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12 |  |  | 0 |  | MOORE INDUSTRIES | [5 empty] | 01
R13 | R13-TI-006A | R13-T-006 | PCS | 107-DA | INDICATOR - TEMPERATURE |  |  | VC1 OFF-GAS TEMPERATURE | PKG: L8160; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R13 | R13-TI-006B | R13-T-006 | FLD | 107-DA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R13 | 113.0 | VC1 OFF-GAS TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R13 | R13-TT-006 | R13-T-006 | FLD | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | VC1 OFF-GAS TEMPERATURE | 8160 | -20 to 80 degC | +/-2degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R13 | R13-TE-007 | R13-T-007 | FLD | 107-DA | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9023117 |  | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request |  |  | 0 |  | MOORE INDUSTRIES | [5 empty] | 01
R13 | R13-TIC-007 | R13-T-007 | PCS | 107-DA | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R13 | R13-TT-007 | R13-T-007 | FLD | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R13 | R13-TE-008 | R13-T-008 | FLD | 107-DA | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-C-9023114 |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 |  | MOORE INDUSTRIES | [5 empty] | 01
R13 | R13-TIC-008 | R13-T-008 | PCS | 107-DA | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R13 | R13-TT-008 | R13-T-008 | FLD | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | PC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R13 | R13-TE-009 | R13-T-009 | FLD | 107-DA | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-C-9023102 |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 |  | MOORE INDUSTRIES | [5 empty] | 01
R13 | R13-TI-009A | R13-T-009 | PCS | 107-DA | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R13 | R13-TI-009B | R13-T-009 | FLD | 107-DA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 113.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5100 |  |  | 34
R13 | R13-TT-009 | R13-T-009 | FLD | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | THZ2/PRG | KT0004 | TI702-SP-5100 |  |  | 01
R13 | R13-TE-010 | R13-T-010 | FLD | 107-DA | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023124 |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 |  | MOORE INDUSTRIES | [5 empty] | 01
R13 | R13-TI-010A | R13-T-010 | PCS | 107-DA | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R13 | R13-TI-010B | R13-T-010 | FLD | 107-DA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R13 | 113.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 01
R13 | R13-TT-010 | R13-T-010 | FLD | 107-DA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 113.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R13 | R13-YA-001 | R13-Y-001 | PCS | 107-DA | ALARM - COMMON | DELETED | 113.0 | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [5 empty] | DELETED |  | 04
R13 | R13-YS-001 | R13-Y-001 | PKG | 107-DA | COMMON ALARM | DELETED | 113.0 | AGITATOR SEAL COMMON ALARM | 8777 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | FG1 |  |  |  |  | DELETED |  | 04
R14 | R14-AG-001 | R14-A-001 | PKG | 107-DB | SPEED MOORE DISPLAY |  | 059.0 | AGITATOR | REF: REF; REQ: By request | [10 empty] | 34
R14 | R14-BD-001 | R14-B-001 | FLD | 107-DB | RUPTURE DISC | 80-P-PT1A-H-9023203 | 059.0 | BURSTING DISC | 6746 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | FG1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R14 | R14-YI-001 | R14-B-001 | PCS | 107-DB | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R14 | R14-CV-001 | R14-C-001 | PKG | 107-DB | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R14/K/80 | 059.0 | BOTTOM OUTLET VALVE | 8797 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R14 | R14-CY-001 | R14-C-001 | PKG | 107-DB | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | FG1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R14 | R14-ZSC-001 | R14-C-001 | PKG | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R14 | R14-ZSO-001 | R14-C-001 | PKG | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R14 | R14-CV-004 | R14-C-004 | FLD | 107-DB | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9023230 | 059.0 | NITROGEN SUPPLY | 6791 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R14 | R14-CV-005 | R14-C-005 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023211 | 059.0 | SCRUBBER 01 | 7214 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-CY-005 | R14-C-005 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-005 | R14-C-005 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-005 | R14-C-005 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-006 | R14-C-006 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023210 | 059.0 | SCRUBBER 02 | 7215 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-CY-006 | R14-C-006 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-006 | R14-C-006 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-006 | R14-C-006 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-007 | R14-C-007 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9023238 | 059.0 | PROCESS VACUUM | 7324 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-CY-007 | R14-C-007 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-007 | R14-C-007 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-007 | R14-C-007 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-008 | R14-C-008 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9023237 | 059.0 | HOUSE VACUUM | 7274 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-CY-008 | R14-C-008 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-008 | R14-C-008 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-008 | R14-C-008 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-009 | R14-C-009 | FLD | 107-DB | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9029601 | 059.0 | COLD HTF SUPPLY | 7501 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R14 | R14-CY-009 | R14-C-009 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-009 | R14-C-009 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-009 | R14-C-009 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-010 | R14-C-010 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 50-HT-CS3A-D-9029255 | 059.0 | HOT HTF SUPPLY | 7496 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R14 | R14-ZSC-010 | R14-C-010 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-010 | R14-C-010 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-011 | R14-C-011 | FLD | 107-DB | GLOBE VALVE - CONTROL - F.C. | 50-HT-CS3A-D-9023223 | 059.0 | HOT HTF RTN | 6365 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R14 | R14-CV-012 | R14-C-012 | FLD | 107-DB | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-D-9023256 | 059.0 | COLD HTF RTN | 6369 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R14 | R14-CV-013 | R14-C-013 | FLD | 107-DB | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-D-9023225 | 059.0 | DUAL JACKET | 7488 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R14 | R14-CY-013 | R14-C-013 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-013 | R14-C-013 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-013 | R14-C-013 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-014 | R14-C-014 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9023259 | 059.0 | N2 TO BOTTOM OUTLET | 7149 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-CY-014 | R14-C-014 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-014 | R14-C-014 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-014 | R14-C-014 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-015 | R14-C-015 | FLD | 107-DB | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9023214 | 059.0 | PC1 TEMPERED HTF RTN | 6408 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R14 | R14-CV-016 | R14-C-016 | FLD | 107-DB | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9023217 | 059.0 | VC1 COLD HTF RTN | 6413 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R14 | R14-CV-018 | R14-C-018 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023205 | 059.0 | DISTILLATE VENT LINE | 7216 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-CY-018 | R14-C-018 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-018 | R14-C-018 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-018 | R14-C-018 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-019 | R14-C-019 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023865 | 059.0 | LIQUID INLET | 7244 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-CY-019 | R14-C-019 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-019 | R14-C-019 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-019 | R14-C-019 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-021 | R14-C-021 | FLD | 107-DB | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9023210 | 059.0 | +VE PRESSURE CONTROL | 6812 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R14 | R14-CV-022 | R14-C-022 | FLD | 107-DB | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9023237 | 059.0 | -VE PRESSURE CONTROL | 6833 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R14 | R14-CV-024 | R14-C-024 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9023267 | 059.0 | SOLIDS INLET | 7352 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-CX-024 | R14-C-024 | SGS | 107-DB | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R14 | R14-CY-024 | R14-C-024 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED | 059.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-024 | R14-C-024 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-024 | R14-C-024 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-025 | R14-C-025 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023210 | 059.0 | SOLIDS ADDITION VENT | 7300 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-CX-025 | R14-C-025 | SGS | 107-DB | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R14 | R14-CY-025 | R14-C-025 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED | 059.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R14 | R14-ZSC-025 | R14-C-025 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-ZSO-025 | R14-C-025 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 059.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-CV-030 | R14-C-030 | FLD | 107-DB | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9023210 | 059 | CARBON DRUM DIVERT | L15692 | - | - | REF | REQ | F | [5 empty] | 0 |  | ATOMAC | AMP3 | KV0007/P6 |  |  |  | 23
R14 | R14-CY-030A | R14-C-030 |  | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT | REF: REF; I.S: I.S; DI: DO |  |  |  | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004
R14 | R14-CY-030B | R14-C-030 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S | DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R14 | R14-ZSC-030 | R14-C-030 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM DIVERT | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-ZSO-030 | R14-C-030 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-CV-031 | R14-C-031 | FLD | 107-DB | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9023210 | 059 | CARBON DRUM DIVERT | L15693 | - | - | REF | REQ | F | [5 empty] | 0 |  | ATOMAC | AMP3 | KV0007/P6 |  |  |  | 23
R14 | R14-CY-031A | R14-C-031 |  | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT | REF: REF; I.S: I.S; DI: DO |  |  |  | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004
R14 | R14-CY-031B | R14-C-031 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S | DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R14 | R14-ZSC-031 | R14-C-031 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM DIVERT | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-ZSO-031 | R14-C-031 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-CV-032 | R14-C-032 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023269 | 059 | CARBON DRUM ISOLATE | L15694 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
R14 | R14-CY-032 | R14-C-032 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R14 | R14-ZSC-032 | R14-C-032 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM ISOLATE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-ZSO-032 | R14-C-032 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-CV-033 | R14-C-033 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023270 | 059 | CARBON DRUM ISOLATE | L15695 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
R14 | R14-CY-033 | R14-C-033 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R14 | R14-ZSC-033 | R14-C-033 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM ISOLATE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-ZSO-033 | R14-C-033 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-CV-034 | R14-C-034 | FLD | 107-DB | BALL VALVE - ON/OFF - F.C. | 15-P-PT1A-0-9023210 | 059 | CARBON DRUM NITROGEN PURGE | L15696 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
R14 | R14-CY-034 | R14-C-034 | FLD | 107-DB | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM NITROGEN PURGE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R14 | R14-ZSC-034 | R14-C-034 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM NITROGEN PURGE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-ZSO-034 | R14-C-034 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM NITROGEN PURGE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R14 | R14-DIC-001 | R14-D-001 | PCS | 107-DB | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R14 | R14-DS-001 | R14-D-001 | MCC | 107-DB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R14 | R14-DY-001 | R14-D-001 | MCC | 107-DB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R14 | R14-DYC-001 | R14-D-001 | MCC | 107-DB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 059.0 | JACKET PUMP | 8798 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R14 | R14-FIT-001 | R14-F-001 | PKG | 107-DB | TRANSMITTER - FLOW | 15-N-SS1U-0-9023271 | 059 | N2 TO CARBON DRUM |  | - | - | REF | By request | C | Ref | I.S | AI |  |  |  | FG1 | KROHNE | H250/RR/M9S/ESK-EX |  | TI702-SP-5098 |  |  | 40
R14 | R14-HS-002 | R14-H-002 | FLD | 107-DB | SWITCH - HAND OP. | ADJ TO R14 | 059.0 | CRASH COOL | 6999 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | FG1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R14 | R14-HV-008 | R14-H-008 | FLD | 107-DB | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028795 | 059.0 | N2 PRESSURE SELECT | 7481 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R14 | R14-HZSC-008 | R14-H-008 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R14 | R14-HZSO-008 | R14-H-008 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R14 | R14-HV-009 | R14-H-009 | FLD | 107-DB | HAND VALVE | 25-P-PT1A-0-9023262 | 059.0 | AUX. INLET | 7405 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-HZSC-009 | R14-H-009 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-HZSO-009 | R14-H-009 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R14 | R14-HV-010 | R14-H-010 | FLD | 107-DB | HAND VALVE | 40-P-PT1A-0-9023865 | 059.0 | REAGENTS INLET | 7372 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R14 | R14-HZSC-010 | R14-H-010 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-HZSO-010 | R14-H-010 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-HV-012 | R14-H-012 | FLD | 107-DB | HAND VALVE | 25-P-PT1A-0-9023864 | 059.0 | SOLVENTS INLET | 7406 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-HZSC-012 | R14-H-012 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-HZSO-012 | R14-H-012 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R14 | R14-HV-013 | R14-H-013 | FLD | 107-DB | HAND VALVE | 40-P-PT1A-0-9023865 | 059.0 | SLURRIES INLET | 7453 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R14 | R14-HZSC-013 | R14-H-013 | FLD | 107-DB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-HZSO-013 | R14-H-013 | FLD | 107-DB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R14 | R14-II-002 | R14-I-002 | PCS | 107-DB | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R14 | R14-IT-002 | R14-I-002 | MCC | 107-DB | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 059.0 | AGITATOR CURRENT | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 13 | FG1 | [6 empty] | 01
R14 | R14-LAH-001 | R14-L-001 | PCS | 107-DB | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L6633; -: On/off; -: On/off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R14 | R14-LE-001 | R14-L-001 | FLD | 107-DB | ELEMENT - LEVEL | 80-P-PT1A-H-9023203 | 059.0 | HIGH LEVEL | L6633 | On/off | On/off | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R14 | R14-LSH-001 | R14-L-001 | CPR | 107-DB | SWITCH - LEVEL - HIGH | 80-P-PT1A-H-9023203 | 059.0 | HIGH LEVEL | 6633 | On/off | On/off | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | FG1 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R14 | R14-LG-002 | R14-L-002 | PKG | 107-DB | LEVEL GAUGE | AGITATOR SEAL POT | 059.0 | AGITATOR SEAL POT LEVEL | -: -; REF: REF; F: F |  |  | 0 | [7 empty] | 01
R14 | R14-PIC-001 | R14-P-001 | PCS | 107-DB | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-PIT-001 | R14-P-001 | FLD | 107-DB | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9023203 | 059.0 | PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R14 | R14-PI-002 | R14-P-002 | PCS | 107-DB | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6679; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R14 | R14-PIT-002 | R14-P-002 | FLD | 107-DB | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9023203 | 059.0 | PRESSURE | 6679 | -1 to 2.3 barg | +/-0.033barg | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R14 | R14-PAH-003 | R14-P-003 | PCS | 107-DB | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-PSH-003 | R14-P-003 | FLD | 107-DB | SWITCH - PRESSURE - DIAPHRAGM - HI | 80-P-PT1A-H-9023203 | 059.0 | HIGH PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 32 | FG1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R14 | R14-PI-004 | R14-P-004 | FLD | 107-DB | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-0-9023230 | 059.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R14 | R14-PI-007 | R14-P-007 | FLD | 107-DB | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-C-9029601 | 059.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R14 | R14-PI-008 | R14-P-008 | FLD | 107-DB | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-D-9023225 | 059.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R14 | R14-PI-009 | R14-P-009 | FLD | 107-DB | PRESSURE GAUGE | 40-P-PT1A-0-9023269 | 059 | CARBON DRUM INLET | L15721 | -1 TO 1 barg |  | REF | REQ | C | Ref | [6 empty] | WIKA | 233.30.063 | KP0006/P12 |  |  |  | 23
R14 | R14-PSV-012 | R14-P-012 | FLD | 107-DB | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9023255 | 059.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R14 | R14-PSV-013 | R14-P-013 | FLD | 107-DB | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023253 | 059.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R14 | R14-PSV-014 | R14-P-014 | FLD | 107-DB | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023254 | 059.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R14 | R14-PRV-015 | R14-P-015 | FLD | 107-DB | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028794 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R14 | R14-PI-016 | R14-P-016 | PKG | 107-DB | PRESSURE GAUGE | AGITATOR SEAL POT | 059.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R14 | R14-SE-001 | R14-S-001 | PKG | 107-DB | ELEMENT - SPEED | AGITATOR SHAFT | 059.0 | AGITATOR |  |  | - | REF | By request | C |  | I.S | DI |  |  | 33 | FG1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R14 | R14-SI-001A | R14-S-001 | PCS | 107-DB | INDICATOR - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-SI-001B | R14-S-001 | FLD | 107-DB | INDICATOR - SPEED | ADJ TO R14 AGITATOR | 059.0 | AGITATOR | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AO |  |  | 21 | FG1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R14 | R14-DS-002 | R14-S-002 | MCC | 107-DB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R14 | R14-DY-002 | R14-S-002 | MCC | 107-DB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R14 | R14-DYC-002 | R14-S-002 | MCC | 107-DB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 059.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R14 | R14-SC-002 | R14-S-002 | MCC | 107-DB | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 059.0 | AGITATOR | 8801 | 0 to 200 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | FG1 |  |  |  |  | SET Min 37 rpm & Max 186 rpm |  | 01
R14 | R14-SIC-002 | R14-S-002 | PCS | 107-DB | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TE-001 | R14-T-001 | PKG | 107-DB | ELEMENT - TEMPERATURE - RTD | WITH R14-CV-001 |  | TEMPERATURE #1 | PKG: L6887; -: -30 to 170degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R14 | R14-TI-001A | R14-T-001 | PCS | 107-DB | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6887; -: -30 to 170degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R14 | R14-TI-001B | R14-T-001 | FLD | 107-DB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R14 | 059.0 | TEMPERATURE #1 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R14 | R14-TT-001 | R14-T-001 | PKG | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | TEMPERATURE #1 | 6887 | -30 to 170 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R14 | R14-TE-002 | R14-T-002 | PKG | 107-DB | ELEMENT - TEMPERATURE - RTD | WITH R14-CV-001 |  | TEMPERATURE #2 | PKG: L6888; -: -30 to 170degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R14 | R14-TI-002A | R14-T-002 | PCS | 107-DB | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6888; -: -30 to 170degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R14 | R14-TI-002B | R14-T-002 | FLD | 107-DB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 059.0 | TEMPERATURE #2 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R14 | R14-TT-002 | R14-T-002 | PKG | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | TEMPERATURE #2 | L6887 | -30 to 170 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R14 | R14-TE-003 | R14-T-003 | PKG | 107-DB | ELEMENT - TEMPERATURE - RTD | R14/N2/80 |  | BAFFLE TEMPERATURE | PKG: L6889; -: -30 to 170degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R14 | R14-TI-003A | R14-T-003 | PCS | 107-DB | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6889; -: -30 to 170degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R14 | R14-TI-003B | R14-T-003 | FLD | 107-DB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 059.0 | BAFFLE TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R14 | R14-TT-003 | R14-T-003 | PKG | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | BAFFLE TEMPERATURE | 6889 | -30 to 170 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R14 | R14-TE-004 | R14-T-004 | FLD | 107-DB | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9023225 |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TI-004A | R14-T-004 | PCS | 107-DB | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TI-004B | R14-T-004 | FLD | 107-DB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 059.0 | JACKET INLET TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R14 | R14-TT-004 | R14-T-004 | FLD | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R14 | R14-TE-005 | R14-T-005 | FLD | 107-DB | ELEMENT - TEMPERATURE - RTD | 80-P-PT1A-H-9023203 |  | PC1 INLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TI-005 | R14-T-005 | PCS | 107-DB | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R14 | R14-TT-005 | R14-T-005 | FLD | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | PC1 INLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R14 | R14-TI-005A | R14-T-005A | [6 empty] | REQ: By request
R14 | R14-TE-006 | R14-T-006 | FLD | 107-DB | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023210 |  | VC1 OFF GAS TEMPERATURE | PKG: L6472; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R14 | R14-TI-006A | R14-T-006 | PCS | 107-DB | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6472; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R14 | R14-TI-006B | R14-T-006 | FLD | 107-DB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R14 | 059.0 | VC1 OFF GAS TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R14 | R14-TT-006 | R14-T-006 | FLD | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | VC1 OFF GAS TEMPERATURE | 6472 | -20 to 80 degC | +/-2degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R14 | R14-TE-007 | R14-T-007 | FLD | 107-DB | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9023217 |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TIC-007 | R14-T-007 | PCS | 107-DB | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R14 | R14-TT-007 | R14-T-007 | FLD | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R14 | R14-TE-008 | R14-T-008 | FLD | 107-DB | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9023214 |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TIC-008 | R14-T-008 | PCS | 107-DB | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TT-008 | R14-T-008 | FLD | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | PC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R14 | R14-TE-009 | R14-T-009 | FLD | 107-DB | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023202 |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TI-009A | R14-T-009 | PCS | 107-DB | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TI-009B | R14-T-009 | FLD | 107-DB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 059.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R14 | R14-TT-009 | R14-T-009 | FLD | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R14 | R14-TE-010 | R14-T-010 | FLD | 107-DB | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9023228 |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TI-010A | R14-T-010 | PCS | 107-DB | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R14 | R14-TI-010B | R14-T-010 | FLD | 107-DB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R14 | 059.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 01
R14 | R14-TT-010 | R14-T-010 | FLD | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R14 | R14-TE-011 | R14-T-011 | FLD | 107-DB | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023269 |  | CARBON DRUM INLET TEMPERATURE | PKG: L15697; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 23
R14 | R14-TI-011A | R14-T-011 | PCS | 107-DB | INDICATOR - TEMPERATURE |  |  | CARBON DRUM INLET TEMPERATURE | PKG: L15697; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 23
R14 | R14-TI-011B | R14-T-011 | FLD | 107-DB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE |  | CARBON DRUM INLET TEMPERATURE | L15697 | -20 to 80 degC | +/-2degC | SHE | 12 | C |  | I.S |  |  |  | 0 |  | ROSEMOUNT | [5 empty] | 23
R14 | R14-TT-011 | R14-T-011 | FLD | 107-DB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 059 | CARBON DRUM INLET TEMPERATURE | L15697 | -20 to 80 degC | +/-2degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P5 | TI702-SP-5012 |  |  | 23
R14 | R14-YA-001 | R14-Y-001 | PCS | 107-DB | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R14 | R14-YS-001 | R14-Y-001 | FUT | 107-DB | COMMON ALARM | R14 GAS SEAL ASSEMBLY | 059.0 | AGITATOR SEAL COMMON ALARM | PKG: 8703; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | FG1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R15 | R15-AG-001 | R15-A-001 | PKG | 107-DC | SPEED MOORE DISPLAY |  | 114.0 | AGITATOR | REF: REF; REQ: By request | [10 empty] | 34
R15 | R15-BD-001 | R15-B-001 | FLD | 107-DC | RUPTURE DISC | 150-P-PT1A-H-9023303 | 114.0 | BURSTING DISC | 8169 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | FG1 | BS&B | BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R15 | R15-YI-001 | R15-B-001 | PCS | 107-DC | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R15 | R15-CV-001 | R15-C-001 | PKG | 107-DC | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R15/K/100 | 114.0 | BOTTOM OUTLET VALVE | 8802 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R15 | R15-CY-001 | R15-C-001 | PKG | 107-DC | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | FG1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R15 | R15-ZSC-001 | R15-C-001 | PKG | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R15 | R15-ZSO-001 | R15-C-001 | PKG | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R15 | R15-CV-004 | R15-C-004 | FLD | 107-DC | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9023330 | 114.0 | NITROGEN SUPPLY | 8803 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R15 | R15-CV-005 | R15-C-005 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023311 | 114.0 | SCRUBBER 01 | 8198 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-CY-005 | R15-C-005 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-005 | R15-C-005 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-005 | R15-C-005 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-006 | R15-C-006 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-9023310 | 114.0 | SCRUBBER 02 | 8199 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-CY-006 | R15-C-006 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-006 | R15-C-006 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-006 | R15-C-006 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-007 | R15-C-007 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9023338 | 114.0 | PROCESS VACUUM | 8200 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-CY-007 | R15-C-007 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-007 | R15-C-007 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-007 | R15-C-007 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-008 | R15-C-008 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9023337 | 114.0 | HOUSE VACUUM | 8201 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-CY-008 | R15-C-008 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-008 | R15-C-008 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-008 | R15-C-008 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-009 | R15-C-009 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-C-9029524 | 114.0 | COLD HTF SUPPLY | 8234 | - | - | SHE | REQ | F | [5 empty] | 0 |  | WORCESTER | E52 | KV0017 |  |  |  | 01
R15 | R15-CY-009 | R15-C-009 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-009 | R15-C-009 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-009 | R15-C-009 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-010 | R15-C-010 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029204 | 114.0 | HOT HTF SUPPLY | 8235 | - | - | SHE | REQ | F | [5 empty] | 0 |  | WORCESTER | E52 | KV0017 |  |  |  | 01
R15 | R15-ZSC-010 | R15-C-010 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-010 | R15-C-010 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-011 | R15-C-011 | FLD | 107-DC | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9023323 | 114.0 | HOT HTF RTN | 8176 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R15 | R15-CV-012 | R15-C-012 | FLD | 107-DC | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9023356 | 114.0 | COLD HTF RTN | 8177 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R15 | R15-CV-013 | R15-C-013 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 50-HT-CS3A-D-9023325 | 114.0 | DUAL JACKET | 8236 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R15 | R15-CY-013 | R15-C-013 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-013 | R15-C-013 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-013 | R15-C-013 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-014 | R15-C-014 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9023359 | 114.0 | N2 TO BOTTOM OUTLET | 8202 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-CY-014 | R15-C-014 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-014 | R15-C-014 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-014 | R15-C-014 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-015 | R15-C-015 | FLD | 107-DC | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9023314 | 114.0 | PC1 TEMPERED HTF RTN | 8178 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R15 | R15-CV-016 | R15-C-016 | FLD | 107-DC | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9023317 | 114.0 | VC1 COLD HTF RTN | 8179 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R15 | R15-CV-018 | R15-C-018 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023305 | 114.0 | DISTILLATE VENT LINE | 8203 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-CY-018 | R15-C-018 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-018 | R15-C-018 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-018 | R15-C-018 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-019 | R15-C-019 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023823 | 114.0 | LIQUID INLET | 8204 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-CY-019 | R15-C-019 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-019 | R15-C-019 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-019 | R15-C-019 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-021 | R15-C-021 | FLD | 107-DC | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9023310 | 114.0 | +VE PRESSURE CONTROL | 8804 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R15 | R15-CV-022 | R15-C-022 | FLD | 107-DC | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9023337 | 114.0 | -VE PRESSURE CONTROL | 8805 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R15 | R15-CV-024 | R15-C-024 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-0-9023367 | 114.0 | SOLIDS INLET | 8205 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-CX-024 | R15-C-024 | SGS | 107-DC | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R15 | R15-CY-024 | R15-C-024 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED | 114.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-024 | R15-C-024 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-024 | R15-C-024 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-CV-025 | R15-C-025 | FLD | 107-DC | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023310 | 114.0 | SOLIDS ADDITION VENT | 8206 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-CX-025 | R15-C-025 | SGS | 107-DC | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R15 | R15-CY-025 | R15-C-025 | FLD | 107-DC | SOLENOID VALVE | RACK MOUNTED | 114.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R15 | R15-ZSC-025 | R15-C-025 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-ZSO-025 | R15-C-025 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 114.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-DIC-001 | R15-D-001 | PCS | 107-DC | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R15 | R15-DS-001 | R15-D-001 | MCC | 107-DC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R15 | R15-DY-001 | R15-D-001 | MCC | 107-DC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R15 | R15-DYC-001 | R15-D-001 | MCC | 107-DC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 114.0 | JACKET PUMP | 8806 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R15 | R15-FIAH-001 | R15-F-001 | PCS | 107-DC | FLOW INDICATOR - ALARM HIGH | R15 GAS SEAL ASSEMBLY | 114.0 | AGITATOR SEAL HIGH FLOW ALARM | REQ: By request | [10 empty] | 04
R15 | R15-FISH-002 | R15-F-001 | PKG | 107-DC | FLOW INDICATOR - SWITCH HIGH | R15 GAS SEAL ASSEMBLY | 114.0 | AGITATOR SEAL HIGH FLOW ALARM | REF: REF; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 0 | FG1 | PEPPERL + FUCHS | RC15-14-N3 |  | TI702-SP-5088 |  |  | 04
R15 | R15-FIAL-002 | R15-F-002 | PCS | 107-DC | FLOW INDICATOR - ALARM LOW | R15 GAS SEAL ASSEMBLY | 114.0 | AGITATOR SEAL LOW FLOW ALARM | REQ: By request | [10 empty] | 04
R15 | R15-FISL-003 | R15-F-002 | PKG | 107-DC | FLOW INDICATOR - SWITCH LOW | R15 GAS SEAL ASSEMBLY | 114.0 | AGITATOR SEAL LOW FLOW ALARM | PKG: 15065; REQ: By request; I.S: I.S; DI: DI |  |  |  | FG1 | KROHNE / PEPPERL + FUCHS | DK800 / RC10-14-N3 |  | TI702-SP-5087 | LOW RANGE FLOW |  | 04
R15 | R15-HS-002 | R15-H-002 | FLD | 107-DC | SWITCH - HAND OP. | ADJ TO R15 | 114.0 | CRASH COOL | 8227 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | FG1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R15 | R15-HV-008 | R15-H-008 | FLD | 107-DC | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028873 | 114.0 | N2 PRESSURE SELECT | 8233 | - | - | REF | REQ | F | [5 empty] | 0 |  | WORCESTER | SERIES 18 | KV0017 |  |  |  | 01
R15 | R15-HZSC-008 | R15-H-008 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R15 | R15-HZSO-008 | R15-H-008 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R15 | R15-HV-009 | R15-H-009 | FLD | 107-DC | HAND VALVE | 25-P-PT1A-0-9023362 | 114.0 | AUX. INLET | 8207 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-HZSC-009 | R15-H-009 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-HZSO-009 | R15-H-009 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R15 | R15-HV-010 | R15-H-010 | FLD | 107-DC | HAND VALVE | 40-P-PT1A-0-9023823 | 114.0 | REAGENTS INLET | 8208 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R15 | R15-HZSC-010 | R15-H-010 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-HZSO-010 | R15-H-010 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-HV-012 | R15-H-012 | FLD | 107-DC | HAND VALVE | 25-P-PT1A-0-9023899 | 114.0 | SOLVENTS INLET | 8209 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-HZSC-012 | R15-H-012 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-HZSO-012 | R15-H-012 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R15 | R15-HV-013 | R15-H-013 | FLD | 107-DC | HAND VALVE | 40-P-PT1A-0-9023823 | 114.0 | SLURRIES INLET | 8210 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R15 | R15-HZSC-013 | R15-H-013 | FLD | 107-DC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-HZSO-013 | R15-H-013 | FLD | 107-DC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R15 | R15-II-002 | R15-I-002 | PCS | 107-DC | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-IT-002 | R15-I-002 | MCC | 107-DC | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 114.0 | AGITATOR CURRENT | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 13 | FG1 | [6 empty] | 01
R15 | R15-LI-001 | R15-L-001 | PCS | 107-DC | INDICATOR - LEVEL |  |  | LEVEL | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 46
R15 | R15-LT-001 | R15-L-001 | FLD | 107-DC | TRANSMITTER - LEVEL | R15/N3/100 | 114.0 | LEVEL | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | VEGA | VEGAPULS 63 |  | TI702-SP-5009 |  |  | 46
R15 | R15-PIAL-015 | R15-P-001 | PCS | 107-DC | PRESSURE GAUGE - ALARM LOW | R15 GAS SEAL ASSEMBLY | 114.0 | AGITATOR SEAL LP ALARM | REF: SHE; REQ: By request | [10 empty] | 04
R15 | R15-PIC-001 | R15-P-001 | PCS | 107-DC | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-PISL-001 | R15-P-001 | PKG | 107-DC | PRESSURE GAUGE - SWITCH HIGH | R15 GAS SEAL ASSEMBLY | 114.0 | AGITATOR SEAL LP ALARM | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 | FG1 | TURCK | SI2-K08-Y1X |  | TI702-SP-5170 |  |  | 04
R15 | R15-PIT-001 | R15-P-001 | FLD | 107-DC | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-H-9023303 | 114.0 | PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R15 | R15-PI-002 | R15-P-002 | PCS | 107-DC | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L8258; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R15 | R15-PIT-002 | R15-P-002 | FLD | 107-DC | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-H-9023303 | 114.0 | PRESSURE | 8258 | -1 to 2.3 barg | +/-0.033barg | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R15 | R15-PAH-003 | R15-P-003 | [6 empty] | REQ: By request
R15 | R15-PSH-003 | R15-P-003 | FLD | 107-DC | SWITCH - PRESSURE - DIAPHRAGM - HI | 50-P-PT1A-H-9023303 | 114.0 | HIGH PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 32 | FG1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R15 | R15-PI-004 | R15-P-004 | FLD | 107-DC | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9023330 | 114.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R15 | R15-PI-007 | R15-P-007 | FLD | 107-DC | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029524 | 114.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R15 | R15-PI-008 | R15-P-008 | FLD | 107-DC | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9023325 | 114.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R15 | R15-PSV-012 | R15-P-012 | FLD | 107-DC | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9023355 | 114.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R15 | R15-PSV-013 | R15-P-013 | FLD | 107-DC | PRESSURE RELIEF VALVE | 25-HT0CS3A-C-9023353 | 114.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R15 | R15-PSV-014 | R15-P-014 | FLD | 107-DC | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023354 | 114.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R15 | R15-PRV-016 | R15-P-016 | PKG | 107-DC | CONTROL VALVE SELF ACTUATING | R15 GAS SEAL ASSEMBLY | 114.0 | N2 TO AGITATOR SEAL | -: Set @ 5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R15 | R15-SE-001 | R15-S-001 | PKG | 107-DC | ELEMENT - SPEED | AGITATOR SHAFT | 114.0 | AGITATOR |  |  | - | REF | By request | C |  | I.S | DI |  |  | 33 | FG1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R15 | R15-SI-001A | R15-S-001 | PCS | 107-DC | INDICATOR - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-SI-001B | R15-S-001 | FLD | 107-DC | INDICATOR - SPEED | ADJ TO R15 AGITATOR | 114.0 | AGITATOR | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AO |  |  | 21 | FG1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R15 | R15-DS-002 | R15-S-002 | MCC | 107-DC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R15 | R15-DY-002 | R15-S-002 | MCC | 107-DC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R15 | R15-DYC-002 | R15-S-002 | MCC | 107-DC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 114.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R15 | R15-SC-002 | R15-S-002 | MCC | 107-DC | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 114.0 | AGITATOR | 8811 | 0 to 120 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | FG1 |  |  |  |  | SET Min 24 rpm & Max 118 rpm |  | 01
R15 | R15-SIC-002 | R15-S-002 | PCS | 107-DC | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TE-001 | R15-T-001 | PKG | 107-DC | ELEMENT - TEMPERATURE - RTD | WITH R15-CV-001 |  | TEMPERATURE #1 | PKG: L8813; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R15 | R15-TI-001A | R15-T-001 | PCS | 107-DC | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L8813; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R15 | R15-TI-001B | R15-T-001 | FLD | 107-DC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R15 | 114.0 | TEMPERATURE #1 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R15 | R15-TT-001 | R15-T-001 | PKG | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | TEMPERATURE #1 | 8813 | -30 to 170 degC | +/-1degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R15 | R15-TE-002 | R15-T-002 | PKG | 107-DC | ELEMENT - TEMPERATURE - RTD | WITH R15-CV-001 |  | TEMPERATURE #2 | PKG: L8814; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R15 | R15-TI-002A | R15-T-002 | PCS | 107-DC | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L8814; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R15 | R15-TI-002B | R15-T-002 | FLD | 107-DC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 114.0 | TEMPERATURE #2 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R15 | R15-TT-002 | R15-T-002 | PKG | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | TEMPERATURE #2 | 8814 | -30 to 170 degC | +/-1degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R15 | R15-TE-003 | R15-T-003 | PKG | 107-DC | ELEMENT - TEMPERATURE - RTD | R15/N2/150 |  | BAFFLE TEMPERATURE | PKG: L8815; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R15 | R15-TI-003A | R15-T-003 | PCS | 107-DC | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L8815; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R15 | R15-TI-003B | R15-T-003 | FLD | 107-DC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 114.0 | BAFFLE TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R15 | R15-TT-003 | R15-T-003 | PKG | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | BAFFLE TEMPERATURE | 8815 | -30 to 170 degC | +/-1 degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R15 | R15-TE-004 | R15-T-004 | FLD | 107-DC | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023325 |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TI-004A | R15-T-004 | PCS | 107-DC | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TI-004B | R15-T-004 | FLD | 107-DC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 114.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BE324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R15 | R15-TT-004 | R15-T-004 | FLD | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R15 | R15-TE-005 | R15-T-005 | FLD | 107-DC | ELEMENT - TEMPERATURE - RTD | 150-RV-CS1A-0-9023332 |  | PC1 INLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TI-005 | R15-T-005 | PCS | 107-DC | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R15 | R15-TT-005 | R15-T-005 | FLD | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | PC1 INLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R15 | R15-TI-005A | R15-T-005A | [6 empty] | REQ: By request
R15 | R15-TE-006 | R15-T-006 | FLD | 107-DC | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9023310 |  | VC1 OFF-GAS TEMPERATURE | PKG: L8163; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R15 | R15-TI-006A | R15-T-006 | PCS | 107-DC | INDICATOR - TEMPERATURE |  |  | VC1 OFF-GAS TEMPERATURE | PKG: L8163; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R15 | R15-TI-006B | R15-T-006 | FLD | 107-DC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R15 | 114.0 | VC1 OFF-GAS TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R15 | R15-TT-006 | R15-T-006 | FLD | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | VC1 OFF-GAS TEMPERATURE | 8163 | -20 to 80 degC | +/-1 degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R15 | R15-TE-007 | R15-T-007 | FLD | 107-DC | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9023317 |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TIC-007 | R15-T-007 | PCS | 107-DC | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TT-007 | R15-T-007 | FLD | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R15 | R15-TE-008 | R15-T-008 | FLD | 107-DC | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9023314 |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TIC-008 | R15-T-008 | PCS | 107-DC | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TT-008 | R15-T-008 | FLD | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | PC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R15 | R15-TE-009 | R15-T-009 | FLD | 107-DC | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-C-9023302 |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TI-009A | R15-T-009 | PCS | 107-DC | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TI-009B | R15-T-009 | FLD | 107-DC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 114.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R15 | R15-TT-009 | R15-T-009 | FLD | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R15 | R15-TE-010 | R15-T-010 | FLD | 107-DC | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023324 |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TI-010A | R15-T-010 | PCS | 107-DC | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R15 | R15-TI-010B | R15-T-010 | FLD | 107-DC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R15 | 114.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R15 | R15-TT-010 | R15-T-010 | FLD | 107-DC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 114.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R15 | R15-YA-001 | R15-Y-001 | PCS | 107-DC | ALARM - COMMON | DELETED | 114.0 | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [5 empty] | DELETED |  | 04
R15 | R15-YS-001 | R15-Y-001 | PKG | 107-DC | COMMON ALARM | DELETED | 114.0 | AGITATOR SEAL COMMON ALARM | 8808 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | FG1 |  |  |  |  | DELETED |  | 04
R16 | R16-AG-001 | R16-A-001 | PKG | 107-DD | SPEED MOORE DISPLAY |  | 060.0 | AGITATOR | REF: REF; REQ: By request | [10 empty] | 34
R16 | R16-BD-001 | R16-B-001 | FLD | 107-DD | RUPTURE DISC | 100-P-PT1A-H-9023403 | 060.0 | BURSTING DISC | 6747 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | FG1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R16 | R16-YI-001 | R16-B-001 | PCS | 107-DD | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R16 | R16-CV-001 | R16-C-001 | PKG | 107-DD | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R16/K/100 | 060.0 | BOTTOM OUTLET VALVE | 8816 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R16 | R16-CY-001 | R16-C-001 | PKG | 107-DD | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | FG1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R16 | R16-ZSC-001 | R16-C-001 | PKG | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R16 | R16-ZSO-001 | R16-C-001 | PKG | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R16 | R16-CV-004 | R16-C-004 | FLD | 107-DD | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9023430 | 060.0 | NITROGEN SUPPLY | 6792 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R16 | R16-CV-005 | R16-C-005 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023411 | 060.0 | SCRUBBER 01 | 7217 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-CY-005 | R16-C-005 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-005 | R16-C-005 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-005 | R16-C-005 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-006 | R16-C-006 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023410 | 060.0 | SCRUBBER 02 | 7218 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-CY-006 | R16-C-006 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-006 | R16-C-006 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-006 | R16-C-006 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-007 | R16-C-007 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9023438 | 060.0 | PROCESS VACUUM | 7325 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-CY-007 | R16-C-007 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-007 | R16-C-007 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-007 | R16-C-007 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-008 | R16-C-008 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9023437 | 060.0 | HOUSE VACUUM | 7275 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-CY-008 | R16-C-008 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-008 | R16-C-008 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-008 | R16-C-008 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-009 | R16-C-009 | FLD | 107-DD | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-D-9029600 | 060.0 | COLD HTF SUPPLY | 7540 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R16 | R16-CY-009 | R16-C-009 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-009 | R16-C-009 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-009 | R16-C-009 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-010 | R16-C-010 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029254 | 060.0 | HOT HTF SUPPLY | 7516 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R16 | R16-ZSC-010 | R16-C-010 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-010 | R16-C-010 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-011 | R16-C-011 | FLD | 107-DD | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9023423 | 060.0 | HOT HTF RTN | 6380 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R16 | R16-CV-012 | R16-C-012 | FLD | 107-DD | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9023456 | 060.0 | COLD HTF RTN | 6392 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R16 | R16-CV-013 | R16-C-013 | FLD | 107-DD | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9023425 | 060.0 | DUAL JACKET | 7508 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R16 | R16-CY-013 | R16-C-013 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-013 | R16-C-013 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-013 | R16-C-013 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-014 | R16-C-014 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9023459 | 060.0 | N2 TO BOTTOM OUTLET | 7150 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-CY-014 | R16-C-014 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-014 | R16-C-014 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-014 | R16-C-014 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-015 | R16-C-015 | FLD | 107-DD | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-C-9023414 | 060.0 | PC1 TEMPERED HTF RTN | 6419 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R16 | R16-CV-016 | R16-C-016 | FLD | 107-DD | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9023417 | 060.0 | VC1 COLD HTF RTN | 6426 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R16 | R16-CV-018 | R16-C-018 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023405 | 060.0 | DISTILLATE VENT LINE | 7219 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-CY-018 | R16-C-018 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-018 | R16-C-018 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-018 | R16-C-018 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-019 | R16-C-019 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023863 | 060.0 | LIQUID INLET | 7245 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-CY-019 | R16-C-019 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-019 | R16-C-019 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-019 | R16-C-019 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-021 | R16-C-021 | FLD | 107-DD | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9023410 | 060.0 | +VE PRESSURE CONTROL | 6813 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R16 | R16-CV-022 | R16-C-022 | FLD | 107-DD | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9023437 | 060.0 | -VE PRESSURE CONTROL | 6834 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R16 | R16-CV-024 | R16-C-024 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9023467 | 060.0 | SOLIDS INLET | 7353 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-CX-024 | R16-C-024 | SGS | 107-DD | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R16 | R16-CY-024 | R16-C-024 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED | 060.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-024 | R16-C-024 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-024 | R16-C-024 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-025 | R16-C-025 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023410 | 060.0 | SOLIDS ADDITION VENT | 7301 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-CX-025 | R16-C-025 | SGS | 107-DD | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R16 | R16-CY-025 | R16-C-025 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED | 060.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R16 | R16-ZSC-025 | R16-C-025 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-ZSO-025 | R16-C-025 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 060.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-CV-030 | R16-C-030 | FLD | 107-DD | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9023410 | 060 | CARBON DRUM DIVERT | L15698 | - | - | REF | REQ | F | [5 empty] | 0 |  | ATOMAC | AMP3 | KV0007/P6 |  |  |  | 23
R16 | R16-CY-030A | R16-C-030 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S | DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R16 | R16-CY-030B | R16-C-030 |  | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT | I.S: I.S; DI: DO |  |  |  | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004
R16 | R16-ZSC-030 | R16-C-030 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM DIVERT | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-ZSO-030 | R16-C-030 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-CV-031 | R16-C-031 | FLD | 107-DD | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9023410 | 060 | CARBON DRUM DIVERT | L15699 | - | - | REF | REQ | F | [5 empty] | 0 |  | ATOMAC | AMP3 | KV0007/P6 |  |  |  | 23
R16 | R16-CY-031A | R16-C-031 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S | DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R16 | R16-CY-031B | R16-C-031 |  | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT | I.S: I.S; DI: DO |  |  |  | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004
R16 | R16-ZSC-031 | R16-C-031 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM DIVERT | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-ZSO-031 | R16-C-031 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-CV-032 | R16-C-032 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023469 | 060 | CARBON DRUM ISOLATE | L15700 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
R16 | R16-CY-032 | R16-C-032 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R16 | R16-ZSC-032 | R16-C-032 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM ISOLATE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-ZSO-032 | R16-C-032 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-CV-033 | R16-C-033 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023470 | 060 | CARBON DRUM ISOLATE | L15701 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
R16 | R16-CY-033 | R16-C-033 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R16 | R16-ZSC-033 | R16-C-033 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM ISOLATE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-ZSO-033 | R16-C-033 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-CV-034 | R16-C-034 | FLD | 107-DD | BALL VALVE - ON/OFF - F.C. | 15-P-PT1A-0-9023410 | 060 | CARBON DRUM NITROGEN PURGE | L15702 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
R16 | R16-CY-034 | R16-C-034 | FLD | 107-DD | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM NITROGEN PURGE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R16 | R16-ZSC-034 | R16-C-034 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM NITROGEN PURGE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-ZSO-034 | R16-C-034 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM NITROGEN PURGE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R16 | R16-DIC-001 | R16-D-001 | PCS | 107-DD | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R16 | R16-DS-001 | R16-D-001 | MCC | 107-DD | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R16 | R16-DY-001 | R16-D-001 | MCC | 107-DD | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R16 | R16-DYC-001 | R16-D-001 | MCC | 107-DD | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 060.0 | JACKET PUMP | 8817 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R16 | R16-FIT-001 | R16-FI01 | PKG | 107-DD | TRANSMITTER - FLOW | 15-N-SS1U-0-9023471 | 060 | N2 TO CARBON DRUM | L15722 | - | - | REF | By request | C | Ref | I.S | AI |  |  |  | FG1 | KROHNE | H250/RR/M9S/ESK-EX |  | TI702-SP-5098 |  |  | 40
R16 | R16-HS-002 | R16-H-002 | FLD | 107-DD | SWITCH - HAND OP. | ADJ TO R16 | 060.0 | CRASH COOL | 7000 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | FG1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R16 | R16-HV-008 | R16-H-008 | FLD | 107-DD | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028792 | 060.0 | N2 PRESSURE SELECT | 7482 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R16 | R16-HZSC-008 | R16-H-008 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R16 | R16-HZSO-008 | R16-H-008 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R16 | R16-HV-009 | R16-H-009 | FLD | 107-DD | HAND VALVE | 25-P-PT1A-0-9023462 | 060.0 | AUX. INLET | 7407 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-HZSC-009 | R16-H-009 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-HZSO-009 | R16-H-009 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R16 | R16-HV-010 | R16-H-010 | FLD | 107-DD | HAND VALVE | 40-P-PT1A-0-9023863 | 060.0 | REAGENTS INLET | 7373 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R16 | R16-HZSC-010 | R16-H-010 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-HZSO-010 | R16-H-010 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-HV-012 | R16-H-012 | FLD | 107-DD | HAND VALVE | 25-P-PT1A-0-9023862 | 060.0 | SOLVENTS INLET | 7408 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-HZSC-012 | R16-H-012 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-HZSO-012 | R16-H-012 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R16 | R16-HV-013 | R16-H-013 | FLD | 107-DD | HAND VALVE | 40-P-PT1A-0-9023863 | 060.0 | SLURRIES INLET | 7454 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R16 | R16-HZSC-013 | R16-H-013 | FLD | 107-DD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-HZSO-013 | R16-H-013 | FLD | 107-DD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R16 | R16-II-002 | R16-I-002 | PCS | 107-DD | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R16 | R16-IT-002 | R16-I-002 | MCC | 107-DD | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 060.0 | AGITATOR CURRENT | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 13 | FG1 | [6 empty] | 01
R16 | R16-LAH-001 | R16-L-001 | PCS | 107-DD | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L6634; -: on/off; -: on/off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R16 | R16-LE-001 | R16-L-001 | FLD | 107-DD | ELEMENT - LEVEL | 100-P-PT1A-H-9023403 | 060.0 | HIGH LEVEL | L6634 | on/off | on/off | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R16 | R16-LSH-001 | R16-L-001 | CPR | 107-DD | SWITCH - LEVEL - HIGH | 100-P-PT1A-H-9023403 | 060.0 | HIGH LEVEL | 6634 | on/off | on/off | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | FG1 | ENDRESS + HAUSER | FDL30-GAE5A70 | KL0014 | TI702-SP-5015 |  |  | 01
R16 | R16-LG-002 | R16-L-002 | PKG | 107-DD | LEVEL GAUGE | AGITATOR SEAL POT | 060.0 | AGITATOR SEAL POT LEVEL | -: -; REF: REF; REQ: By request; F: F |  |  | 0 | [7 empty] | 01
R16 | R16-PIC-001 | R16-P-001 | PCS | 107-DD | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-PIT-001 | R16-P-001 | FLD | 107-DD | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9023403 | 060.0 | PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R16 | R16-PI-002 | R16-P-002 | PCS | 107-DD | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6682; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R16 | R16-PIT-002 | R16-P-002 | FLD | 107-DD | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9023403 | 060.0 | PRESSURE | 6682 | -1 to 2.3 barg | +/-0.033 barg | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R16 | R16-PAH-003 | R16-P-003 | PCS | 107-DD | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-PSH-003 | R16-P-003 | FLD | 107-DD | SWITCH - PRESSURE - DIAPHRAGM - HI | 100-P-PT1A-H-9023403 | 060.0 | HIGH PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 32 | FG1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R16 | R16-PI-004 | R16-P-004 | FLD | 107-DD | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9023430 | 060.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R16 | R16-PI-007 | R16-P-007 | FLD | 107-DD | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029315 | 060.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R16 | R16-PI-008 | R16-P-008 | FLD | 107-DD | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9023425 | 060.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R16 | R16-PI-009 | R16-P-009 | FLD | 107-DD | PRESSURE GAUGE | 40-P-PT1A-0-9023469 | 060 | CARBON DRUM INLET | L15723 | -1 TO 1 barg |  | REF | REQ | C | Ref | [6 empty] | WIKA | 233.30.063 | KP0006/P12 |  |  |  | 23
R16 | R16-PSV-012 | R16-P-012 | FLD | 107-DD | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9023455 | 060.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R16 | R16-PSV-013 | R16-P-013 | FLD | 107-DD | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023453 | 060.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R16 | R16-PSV-014 | R16-P-014 | FLD | 107-DD | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023454 | 060.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R16 | R16-PRV-015 | R16-P-015 | FLD | 107-DD | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028791 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R16 | R16-PI-016 | R16-P-016 | PKG | 107-DD | PRESSURE GAUGE | AGITATOR SEAL POT | 060.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R16 | R16-SE-001 | R16-S-001 | PKG | 107-DD | ELEMENT - SPEED | AGITATOR SHAFT | 060.0 | AGITATOR |  |  | - | REF | By request | C |  | I.S | DI |  |  | 33 | FG1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R16 | R16-SI-001A | R16-S-001 | PCS | 107-DD | INDICATOR - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-SI-001B | R16-S-001 | FLD | 107-DD | INDICATOR - SPEED | ADJ TO R16 AGITATOR | 060.0 | AGITATOR | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AO |  |  | 21 | FG1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R16 | R16-DS-002 | R16-S-002 | MCC | 107-DD | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R16 | R16-DY-002 | R16-S-002 | MCC | 107-DD | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R16 | R16-DYC-002 | R16-S-002 | MCC | 107-DD | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 060.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R16 | R16-SC-002 | R16-S-002 | MCC | 107-DD | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 060.0 | AGITATOR | 6891 | 0 to 160 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | FG1 |  |  |  |  | SET Min 31rpm & Max 153 rpm |  | 01
R16 | R16-SIC-002 | R16-S-002 | PCS | 107-DD | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TE-001 | R16-T-001 | PKG | 107-DD | ELEMENT - TEMPERATURE - RTD | WITH R16-CV-001 |  | TEMPERATURE #1 | PKG: L6892; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R16 | R16-TI-001A | R16-T-001 | PCS | 107-DD | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6892; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R16 | R16-TI-001B | R16-T-001 | FLD | 107-DD | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R16 | 060.0 | TEMPERATURE #1 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R16 | R16-TT-001 | R16-T-001 | PKG | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | TEMPERATURE #1 | 6892 | -30 to 170 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R16 | R16-TE-002 | R16-T-002 | PKG | 107-DD | ELEMENT - TEMPERATURE - RTD | WITH R16-CV-001 |  | TEMPERATURE #2 | PKG: L6893; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R16 | R16-TI-002A | R16-T-002 | PCS | 107-DD | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6893; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R16 | R16-TI-002B | R16-T-002 | FLD | 107-DD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 060.0 | TEMPERATURE #2 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R16 | R16-TT-002 | R16-T-002 | PKG | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | TEMPERATURE #2 | 6893 | -30 to 170 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R16 | R16-TE-003 | R16-T-003 | PKG | 107-DD | ELEMENT - TEMPERATURE - RTD | R16/N2/100 |  | BAFFLE TEMPERATURE | PKG: L6894; -: -30 to 170 degC; -: +/-2degC; REF: GxP/SHE; REQ: 2 |  |  | 0 | [7 empty] | 01
R16 | R16-TI-003A | R16-T-003 | PCS | 107-DD | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TI-003B | R16-T-003 | FLD | 107-DD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 060.0 | BAFFLE TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R16 | R16-TT-003 | R16-T-003 | PKG | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | BAFFLE TEMPERATURE | 6894 | -30 to 170 degC | +/-2degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R16 | R16-TE-004 | R16-T-004 | FLD | 107-DD | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023425 |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TI-004A | R16-T-004 | PCS | 107-DD | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TI-004B | R16-T-004 | FLD | 107-DD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 060.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BE324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R16 | R16-TT-004 | R16-T-004 | FLD | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R16 | R16-TE-005 | R16-T-005 | FLD | 107-DD | ELEMENT - TEMPERATURE - RTD | 100-P-PT1A-H-9023403 |  | PC1 INLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TI-005 | R16-T-005 | PCS | 107-DD | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R16 | R16-TT-005 | R16-T-005 | FLD | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | PC1 INLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R16 | R16-TI-005A | R16-T-005A | [6 empty] | REQ: By request
R16 | R16-TE-006 | R16-T-006 | FLD | 107-DD | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023410 |  | VC1 OFF GAS TEMPERATURE | PKG: L6478; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R16 | R16-TI-006A | R16-T-006 | PCS | 107-DD | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6478; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R16 | R16-TI-006B | R16-T-006 | FLD | 107-DD | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R16 | 060.0 | VC1 OFF GAS TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R16 | R16-TT-006 | R16-T-006 | FLD | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | VC1 OFF GAS TEMPERATURE | 6478 | -20 to 80 degC | +/-2degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R16 | R16-TE-007 | R16-T-007 | FLD | 107-DD | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9023417 |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TIC-007 | R16-T-007 | PCS | 107-DD | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TT-007 | R16-T-007 | FLD | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R16 | R16-TE-008 | R16-T-008 | FLD | 107-DD | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-C-9023414 |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TIC-008 | R16-T-008 | PCS | 107-DD | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TT-008 | R16-T-008 | FLD | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | PC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R16 | R16-TE-009 | R16-T-009 | FLD | 107-DD | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023402 |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TI-009A | R16-T-009 | PCS | 107-DD | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TI-009B | R16-T-009 | FLD | 107-DD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 060.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R16 | R16-TT-009 | R16-T-009 | FLD | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R16 | R16-TE-010 | R16-T-010 | FLD | 107-DD | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023428 |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TI-010A | R16-T-010 | PCS | 107-DD | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R16 | R16-TI-010B | R16-T-010 | FLD | 107-DD | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R16 | 060.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R16 | R16-TT-010 | R16-T-010 | FLD | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R16 | R16-TE-011 | R16-T-011 | FLD | 107-DD | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023469 |  | CARBON DRUM INLET TEMPERATURE | PKG: L15703; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 23
R16 | R16-TI-011 | R16-T-011 | [6 empty] | PKG: L15703; -: -20 to 80 degC; -: +/-2degC; REF: SHE; REQ: 12
R16 | R16-TI-011A | R16-T-011 | PCS | 107-DD | INDICATOR - TEMPERATURE |  |  | CARBON DRUM INLET TEMPERATURE | -: -20 to 80 degC; -: +/- 1% |  |  | 0 | [7 empty] | 23
R16 | R16-TI-011B | R16-T-011 | FLD | 107-DD | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE |  | CARBON DRUM INLET TEMPERATURE | L15703 | 4 to 20 degC | +/-2degC | SHE | 12 | C |  | I.S |  |  |  | 0 |  | ROSEMOUNT | [5 empty] | 23
R16 | R16-TT-011 | R16-T-011 | FLD | 107-DD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 060 | CARBON DRUM INLET TEMPERATURE | L15703 | -20 to 80 degC | +/-2degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P5 | TI702-SP-5012 |  |  | 23
R16 | R16-YA-001 | R16-Y-001 | PCS | 107-DD | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R16 | R16-YS-001 | R16-Y-001 | FUT | 107-DD | COMMON ALARM | R16 GAS SEAL ASSEMBLY | 060.0 | AGITATOR SEAL COMMON ALARM | PKG: 8707; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | FG1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R17 | R17-AG-001 | R17-A-001 | PKG | 107-DE | SPEED MOORE DISPLAY |  | 115.0 | AGITATOR | REF: REF; REQ: By request | [10 empty] | 34
R17 | R17-BD-001 | R17-B-001 | FLD | 107-DE | RUPTURE DISC | 150-P-PT1A-H-9023503 | 115.0 | BURSTING DISC | 8170 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | FG1 | BS&B | BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R17 | R17-YI-001 | R17-B-001 | PCS | 107-DE | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R17 | R17-CV-001 | R17-C-001 | PKG | 107-DE | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R17/K/100 | 115.0 | BOTTOM OUTLET VALVE | 8820 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R17 | R17-CY-001 | R17-C-001 | PKG | 107-DE | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | FG1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R17 | R17-ZSC-001 | R17-C-001 | PKG | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R17 | R17-ZSO-001 | R17-C-001 | PKG | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R17 | R17-CV-004 | R17-C-004 | FLD | 107-DE | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9023530 | 115.0 | NITROGEN SUPPLY | 8821 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R17 | R17-CV-005 | R17-C-005 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023511 | 115.0 | SCRUBBER 01 | 8211 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-CY-005 | R17-C-005 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-005 | R17-C-005 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-005 | R17-C-005 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-006 | R17-C-006 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 40-SV-GR1A-0-9023512 | 115.0 | SCRUBBER 02 | 8212 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-CY-006 | R17-C-006 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-006 | R17-C-006 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-006 | R17-C-006 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-007 | R17-C-007 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9023538 | 115.0 | PROCESS VACUUM | 8213 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-CY-007 | R17-C-007 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-007 | R17-C-007 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-007 | R17-C-007 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-008 | R17-C-008 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9023564 | 115.0 | HOUSE VACUUM | 8214 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-CY-008 | R17-C-008 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-008 | R17-C-008 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-008 | R17-C-008 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-009 | R17-C-009 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-C-9029525 | 115.0 | COLD HTF SUPPLY | 8238 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R17 | R17-CY-009 | R17-C-009 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-009 | R17-C-009 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-009 | R17-C-009 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-010 | R17-C-010 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029203 | 115.0 | HOT HTF SUPPLY | 8239 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R17 | R17-ZSC-010 | R17-C-010 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-010 | R17-C-010 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-011 | R17-C-011 | FLD | 107-DE | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9023523 | 115.0 | HOT HTF RTN | 8180 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R17 | R17-CV-012 | R17-C-012 | FLD | 107-DE | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9023556 | 115.0 | COLD HTF RTN | 8181 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R17 | R17-CV-014 | R17-C-014 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9023559 | 115.0 | N2 TO BOTTOM OUTLET | 8215 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-CY-014 | R17-C-014 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-014 | R17-C-014 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-014 | R17-C-014 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-015 | R17-C-015 | FLD | 107-DE | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9023514 | 115.0 | PC1 TEMPERED HTF RTN | 8182 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R17 | R17-CV-016 | R17-C-016 | FLD | 107-DE | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9023517 | 115.0 | VC1 COLD HTF RTN | 8183 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R17 | R17-CV-018 | R17-C-018 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023505 | 115.0 | DISTILLATE VENT LINE | 8216 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-CY-018 | R17-C-018 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-018 | R17-C-018 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-018 | R17-C-018 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-019 | R17-C-019 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9023872 | 115.0 | LIQUID INLET | 8217 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-CY-019 | R17-C-019 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-019 | R17-C-019 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-019 | R17-C-019 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-021 | R17-C-021 | FLD | 107-DE | V-BALL VALVE - CONTROL - F.C. | 25-P-PT1A-0-9023510 | 115.0 | +VE PRESSURE CONTROL | 8822 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R17 | R17-CV-022 | R17-C-022 | FLD | 107-DE | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9023537 | 115.0 | -VE PRESSURE CONTROL | 8823 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R17 | R17-CV-024 | R17-C-024 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-0-9023567 | 115.0 | SOLIDS INLET | 8218 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-CX-024 | R17-C-024 | SGS | 107-DE | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R17 | R17-CY-024 | R17-C-024 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED | 115.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-024 | R17-C-024 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-024 | R17-C-024 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-CV-025 | R17-C-025 | FLD | 107-DE | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023566 | 115.0 | SOLIDS ADDITION VENT | 8219 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-CX-025 | R17-C-025 | SGS | 107-DE | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R17 | R17-CY-025 | R17-C-025 | FLD | 107-DE | SOLENOID VALVE | RACK MOUNTED | 115.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R17 | R17-ZSC-025 | R17-C-025 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-ZSO-025 | R17-C-025 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 115.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-DIC-001 | R17-D-001 | PCS | 107-DE | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R17 | R17-DS-001 | R17-D-001 | MCC | 107-DE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R17 | R17-DY-001 | R17-D-001 | MCC | 107-DE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R17 | R17-DYC-001 | R17-D-001 | MCC | 107-DE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 115.0 | JACKET PUMP | 8824 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R17 | R17-FIAH-001 | R17-F-001 | PCS | 107-DE | FLOW INDICATOR - ALARM HIGH | R17 GAS SEAL ASSEMBLY | 115.0 | AGITATOR SEAL HIGH FLOW ALARM | REQ: By request | [10 empty] | 04
R17 | R17-FI-002 | R17-F-002 | PKG | 107-DE | VA FLOW METER | R17 GAS SEAL ASSEMBLY | 115.0 | AGITATOR SEAL N2 FLOW | -: 0.08-0.8 Nl/min; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | KROHNE | DK 800 |  |  | LOW RANGE FLOW |  | 04
R17 | R17-FIAL-002 | R17-F-002 | [6 empty] | REF: REF; REQ: By request
R17 | R17-FISH-002 | R17-F-002 | PKG | 107-DE | FLOW INDICATOR - SWITCH HIGH | R17 GAS SEAL ASSEMBLY | 115.0 | AGITATOR SEAL HIGH FLOW ALARM | REQ: By request; F: C; I.S: I.S |  |  | 0 | FG1 | PEPPERL + FUCHS | RC15-14-N3 |  | TI702-SP-5088 |  |  | 04
R17 | R17-FISL-002 | R17-F-002 | [6 empty] | REQ: By request
R17 | R17-HS-002 | R17-H-002 | FLD | 107-DE | SWITCH - HAND OP. | ADJ TO R17 | 115.0 | CRASH COOL | 8228 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | FG1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R17 | R17-HV-008 | R17-H-008 | FLD | 107-DE | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028870 | 115.0 | N2 PRESSURE SELECT | 8237 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R17 | R17-HZSC-008 | R17-H-008 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R17 | R17-HZSO-008 | R17-H-008 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R17 | R17-HV-009 | R17-H-009 | FLD | 107-DE | HAND VALVE | 25-P-PT1A-0-9023562 | 115.0 | AUX. INLET | 8220 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-HZSC-009 | R17-H-009 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-HZSO-009 | R17-H-009 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R17 | R17-HV-010 | R17-H-010 | FLD | 107-DE | HAND VALVE | 40-P-PT1A-0-9023821 | 115.0 | REAGENTS INLET | 8221 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R17 | R17-HZSC-010 | R17-H-010 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-HZSO-010 | R17-H-010 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-HV-012 | R17-H-012 | FLD | 107-DE | HAND VALVE | 25-P-PT1A-0-9023872 | 115.0 | SOLVENTS INLET | 8222 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-HZSC-012 | R17-H-012 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-HZSO-012 | R17-H-012 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R17 | R17-HV-013 | R17-H-013 | FLD | 107-DE | HAND VALVE | 40-P-PT1A-0-9023821 | 115.0 | SLURRIES INLET | 8223 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R17 | R17-HZSC-013 | R17-H-013 | FLD | 107-DE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-HZSO-013 | R17-H-013 | FLD | 107-DE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R17 | R17-II-002 | R17-I-002 | PCS | 107-DE | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-IT-002 | R17-I-002 | MCC | 107-DE | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 115.0 | AGITATOR CURRENT | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 13 | FG1 | [6 empty] | 01
R17 | R17-LI-001 | R17-L-001 | PCS | 107-DE | INDICATOR - LEVEL |  |  | LEVEL | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-LT-001 | R17-L-001 | FLD | 107-DE | TRANSMITTER - LEVEL | R17/N4/100 | 115.0 | LEVEL | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | VEGA | VEGAPULS 63 | KL0028 | TI702-SP-5009 |  |  | 01
R17 | R17-PIC-001 | R17-P-001 | PCS | 107-DE | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-PIT-001 | R17-P-001 | FLD | 107-DE | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9023503 | 115.0 | PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | FOXBORO | 141GP (Note 2) | KP0001 | TI702-SP-5006 |  |  | 01
R17 | R17-PI-002 | R17-P-002 | PCS | 107-DE | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L8260; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R17 | R17-PIT-002 | R17-P-002 | FLD | 107-DE | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9023503 | 115.0 | PRESSURE | 8260 | -1 to 2.3 barg | +/-0.033barg | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R17 | R17-PAH-003 | R17-P-003 | PCS | 107-DE | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-PSH-003 | R17-P-003 | FLD | 107-DE | SWITCH - PRESSURE - DIAPHRAGM - HI | 150-P-PT1A-H-9023503 | 115.0 | HIGH PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 32 | FG1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R17 | R17-PI-004 | R17-P-004 | FLD | 107-DE | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9023530 | 115.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R17 | R17-PI-007 | R17-P-007 | FLD | 107-DE | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029525 | 115.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R17 | R17-PI-008 | R17-P-008 | FLD | 107-DE | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9023525 | 115.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R17 | R17-PSV-012 | R17-P-012 | FLD | 107-DE | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9023555 | 115.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R17 | R17-PSV-013 | R17-P-013 | FLD | 107-DE | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023553 | 115.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R17 | R17-PSV-014 | R17-P-014 | FLD | 107-DE | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023554 | 115.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R17 | R17-PIAL-015 | R17-P-015 | PCS | 107-DE | PRESSURE GAUGE - ALARM LOW | R17 GAS SEAL ASSEMBLY | 115.0 | AGITATOR SEAL LP ALARM | REQ: By request | [10 empty] | 04
R17 | R17-PISL-015 | R17-P-015 | PKG | 107-DE | PRESSURE GAUGE - SWITCH LOW | R17 GAS SEAL ASSEMBLY | 115.0 | AGITATOR SEAL LP ALARM | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 | [7 empty] | 04
R17 | R17-PRV-016 | R17-P-016 | PKG | 107-DE | CONTROL VALVE SELF ACTUATING | R17 GAS SEAL ASSEMBLY | 115.0 | N2 TO AGITATOR GAS SEAL | -: Set @ 5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R17 | R17-SE-001 | R17-S-001 | PKG | 107-DE | ELEMENT - SPEED | AGITATOR SHAFT | 115.0 | AGITATOR |  |  | - | REF | By request | C |  | I.S | DI |  |  | 33 | FG1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R17 | R17-SI-001A | R17-S-001 | PCS | 107-DE | INDICATOR - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-SI-001B | R17-S-001 | FLD | 107-DE | INDICATOR - SPEED | ADJ TO R17 AGITATOR | 115.0 | AGITATOR | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AO |  |  | 21 | FG1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R17 | R17-DS-002 | R17-S-002 | MCC | 107-DE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R17 | R17-DY-002 | R17-S-002 | MCC | 107-DE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R17 | R17-DYC-002 | R17-S-002 | MCC | 107-DE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 115.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R17 | R17-SC-002 | R17-S-002 | MCC | 107-DE | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 115.0 | AGITATOR | 8829 | 0 to 120 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | FG1 |  |  |  |  | SET Min 24 rpm & Max 118 rpm |  | 01
R17 | R17-SIC-002 | R17-S-002 | PCS | 107-DE | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TE-001 | R17-T-001 | PKG | 107-DE | ELEMENT - TEMPERATURE - RTD | WITH R17-CV-00 |  | TEMPERATURE #1 | PKG: L8831; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R17 | R17-TI-001A | R17-T-001 | PCS | 107-DE | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L8831; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R17 | R17-TI-001B | R17-T-001 | FLD | 107-DE | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R17 | 115.0 | TEMPERATURE #1 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R17 | R17-TT-001 | R17-T-001 | PKG | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | TEMPERATURE #1 | 8831 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R17 | R17-TE-002 | R17-T-002 | PKG | 107-DE | ELEMENT - TEMPERATURE - RTD | WITH R17-CV-00 |  | TEMPERATURE #2 | PKG: L8832; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R17 | R17-TI-002A | R17-T-002 | PCS | 107-DE | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L8832; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R17 | R17-TI-002B | R17-T-002 | FLD | 107-DE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 115.0 | TEMPERATURE #2 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R17 | R17-TT-002 | R17-T-002 | PKG | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | TEMPERATURE #2 | 8832 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R17 | R17-TE-003 | R17-T-003 | PKG | 107-DE | ELEMENT - TEMPERATURE - RTD | R17/N2/150 |  | BAFFLE TEMPERATURE | PKG: L8833; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R17 | R17-TI-003A | R17-T-003 | PCS | 107-DE | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L8833; -: 4 to 20 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R17 | R17-TI-003B | R17-T-003 | FLD | 107-DE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 115.0 | BAFFLE TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R17 | R17-TIC-003 | R17-T-003 | [6 empty] | PKG: L8833; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12
R17 | R17-TT-003 | R17-T-003 | PKG | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | BAFFLE TEMPERATURE | 8833 | -30 to 170 degC | +/-1 degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R17 | R17-TE-004 | R17-T-004 | FLD | 107-DE | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023525 |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TI-004A | R17-T-004 | PCS | 107-DE | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TI-004B | R17-T-004 | FLD | 107-DE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 115.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BE324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R17 | R17-TT-004 | R17-T-004 | FLD | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R17 | R17-TE-005 | R17-T-005 | FLD | 107-DE | ELEMENT - TEMPERATURE - RTD | 150-RV-PT1A-0-9023510 |  | PC1 INLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TI-005 | R17-T-005 | PCS | 107-DE | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R17 | R17-TT-005 | R17-T-005 | FLD | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | PC1 INLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R17 | R17-TI-005A | R17-T-005A | [6 empty] | REQ: By request
R17 | R17-TE-006 | R17-T-006 | FLD | 107-DE | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9023510 |  | VC1 OFF-GAS TEMPERATURE | PKG: L8166; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R17 | R17-TI-006A | R17-T-006 | PCS | 107-DE | INDICATOR - TEMPERATURE |  |  | VC1 OFF-GAS TEMPERATURE | PKG: L8166; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R17 | R17-TI-006B | R17-T-006 | FLD | 107-DE | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R17 | 115.0 | VC1 OFF-GAS TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R17 | R17-TT-006 | R17-T-006 | FLD | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | VC1 OFF-GAS TEMPERATURE | 8166 | -20 to 80 degC | +/-1 degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R17 | R17-TE-007 | R17-T-007 | FLD | 107-DE | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9023517 |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TIC-007 | R17-T-007 | PCS | 107-DE | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TT-007 | R17-T-007 | FLD | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R17 | R17-TE-008 | R17-T-008 | FLD | 107-DE | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9023514 |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TIC-008 | R17-T-008 | PCS | 107-DE | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TT-008 | R17-T-008 | FLD | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | PC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R17 | R17-TE-009 | R17-T-009 | FLD | 107-DE | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-C-9023502 |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TI-009A | R17-T-009 | PCS | 107-DE | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TI-009B | R17-T-009 | FLD | 107-DE | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 115.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R17 | R17-TT-009 | R17-T-009 | FLD | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R17 | R17-TE-010 | R17-T-010 | FLD | 107-DE | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023524 |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TI-010A | R17-T-010 | PCS | 107-DE | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R17 | R17-TI-010B | R17-T-010 | FLD | 107-DE | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R17 | 115.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R17 | R17-TT-010 | R17-T-010 | FLD | 107-DE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 115.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R17 | R17-YA-001 | R17-Y-001 | PCS | 107-DE | ALARM - COMMON | DELETED | 115.0 | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [5 empty] | DELETED |  | 04
R17 | R17-YS-001 | R17-Y-001 | PKG | 107-DE | COMMON ALARM | DELETED | 115.0 | AGITATOR SEAL COMMON ALARM | 8826 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | FG1 |  |  |  |  | DELETED |  | 04
R18 | R18-AG-001 | R18-A-001 | PKG | 107-DF | SPEED MOORE DISPLAY |  | 061.0 | AGITATOR | REF: REF; REQ: By request | [10 empty] | 34
R18 | R18-BD-001 | R18-B-001 | FLD | 107-DF | RUPTURE DISC | 150-P-PT1A-H-9023603 | 061.0 | BURSTING DISC | 6748 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | FG1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
R18 | R18-YI-001 | R18-B-001 | PCS | 107-DF | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R18 | R18-CV-001 | R18-C-001 | PKG | 107-DF | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R18/K/100 | 061.0 | BOTTOM OUTLET VALVE | 8834 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R18 | R18-CY-001 | R18-C-001 | PKG | 107-DF | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | FG1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R18 | R18-ZSC-001 | R18-C-001 | PKG | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R18 | R18-ZSO-001 | R18-C-001 | PKG | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R18 | R18-CV-004 | R18-C-004 | FLD | 107-DF | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9023630 | 061.0 | NITROGEN SUPPLY | 6793 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R18 | R18-CV-005 | R18-C-005 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023611 | 061.0 | SCRUBBER 01 | 7220 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-CY-005 | R18-C-005 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-005 | R18-C-005 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-005 | R18-C-005 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 01 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-006 | R18-C-006 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023610 | 061.0 | SCRUBBER 02 | 7221 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-CY-006 | R18-C-006 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-006 | R18-C-006 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-006 | R18-C-006 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-007 | R18-C-007 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9023638 | 061.0 | PROCESS VACUUM | 7326 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-CY-007 | R18-C-007 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED |  | PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-007 | R18-C-007 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-007 | R18-C-007 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-008 | R18-C-008 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9023637 | 061.0 | HOUSE VACUUM | 7276 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-CY-008 | R18-C-008 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-008 | R18-C-008 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-008 | R18-C-008 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-009 | R18-C-009 | FLD | 107-DF | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-D-9029508 | 061.0 | COLD HTF SUPPLY | 7541 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R18 | R18-CY-009 | R18-C-009 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-009 | R18-C-009 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-009 | R18-C-009 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-010 | R18-C-010 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029251 | 061.0 | HOT HTF SUPPLY | 7517 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R18 | R18-ZSC-010 | R18-C-010 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-010 | R18-C-010 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-011 | R18-C-011 | FLD | 107-DF | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9023623 | 061.0 | HOT HTF RTN | 6381 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R18 | R18-CV-012 | R18-C-012 | FLD | 107-DF | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9023656 | 061.0 | COLD HTF RTN | 6393 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R18 | R18-CV-013 | R18-C-013 | FLD | 107-DF | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9023625 | 061.0 | DUAL JACKET | 7509 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R18 | R18-CY-013 | R18-C-013 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-013 | R18-C-013 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-013 | R18-C-013 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-014 | R18-C-014 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9023659 | 061.0 | N2 TO BOTTOM OUTLET | 7151 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-CY-014 | R18-C-014 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-014 | R18-C-014 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-014 | R18-C-014 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-015 | R18-C-015 | FLD | 107-DF | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9023614 | 061.0 | PC1 TEMPERED HTF RTN | 6433 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R18 | R18-CV-016 | R18-C-016 | FLD | 107-DF | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9023617 | 061.0 | VC1 COLD HTF RTN | 6439 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R18 | R18-CV-018 | R18-C-018 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023605 | 061.0 | DISTILLATE VENT LINE | 7222 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-CY-018 | R18-C-018 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-018 | R18-C-018 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-018 | R18-C-018 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-019 | R18-C-019 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023861 | 061.0 | LIQUID INLET | 7246 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-CY-019 | R18-C-019 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-019 | R18-C-019 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-019 | R18-C-019 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-021 | R18-C-021 | FLD | 107-DF | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9023610 | 061.0 | +VE PRESSURE CONTROL | 6814 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R18 | R18-CV-022 | R18-C-022 | FLD | 107-DF | V-BALL VALVE - CONTROL - F.C. | 25-VP-PT1A-0-9023637 | 061.0 | -VE PRESSURE CONTROL | 6835 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R18 | R18-CV-024 | R18-C-024 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9023667 | 061.0 | SOLIDS INLET | 7354 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-CX-024 | R18-C-024 | SGS | 107-DF | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R18 | R18-CY-024 | R18-C-024 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED | 061.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-024 | R18-C-024 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-024 | R18-C-024 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-025 | R18-C-025 | FLD | 107-DF | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023610 | 061.0 | SOLIDS ADDITION VENT | 7302 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-CX-025 | R18-C-025 | SGS | 107-DF | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | FG1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R18 | R18-CY-025 | R18-C-025 | FLD | 107-DF | SOLENOID VALVE | RACK MOUNTED | 061.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R18 | R18-ZSC-025 | R18-C-025 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-ZSO-025 | R18-C-025 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 061.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-CV-030 | R18-C-030 | FLD | 107-GL | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9023610 | 061 | CARBON DRUM DIVERT | L15704 | - | - | REF | REQ | F | [5 empty] | 0 |  | ATOMAC | AMP3 | KV0007/P6 |  |  |  | 23
R18 | R18-CY-030A | R18-C-030 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S | DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R18 | R18-CY-030B | R18-C-030 |  | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT | I.S: I.S; DI: DO |  |  |  | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004
R18 | R18-ZSC-030 | R18-C-030 | FLD | 107-GL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM DIVERT | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-ZSO-030 | R18-C-030 | FLD | 107-GL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-CV-031 | R18-C-031 | FLD | 107-GL | BALL VALVE - 3 WAY F.L.P. | 50-P-PT1A-0-9023610 | 061 | CARBON DRUM DIVERT | L15705 | - | - | REF | REQ | F | [5 empty] | 0 |  | ATOMAC | AMP3 | KV0007/P6 |  |  |  | 23
R18 | R18-CY-031A | R18-C-031 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S | DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R18 | R18-CY-031B | R18-C-031 |  | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM DIVERT | I.S: I.S; DI: DO |  |  |  | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004
R18 | R18-ZSC-031 | R18-C-031 | FLD | 107-GL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM DIVERT | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-ZSO-031 | R18-C-031 | FLD | 107-GL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM DIVERT |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-CV-032 | R18-C-032 | FLD | 107-GL | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023671 | 061 | CARBON DRUM ISOLATE | L15706 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
R18 | R18-CY-032 | R18-C-032 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R18 | R18-ZSC-032 | R18-C-032 | FLD | 107-GL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM ISOLATE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-ZSO-032 | R18-C-032 | FLD | 107-GL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-CV-033 | R18-C-033 | FLD | 107-GL | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9023672 | 061 | CARBON DRUM ISOLATE | L15707 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
R18 | R18-CY-033 | R18-C-033 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R18 | R18-ZSC-033 | R18-C-033 | FLD | 107-GL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM ISOLATE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-ZSO-033 | R18-C-033 | FLD | 107-GL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM ISOLATE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-CV-034 | R18-C-034 | FLD | 107-GL | BALL VALVE - ON/OFF - F.C. | 15-P-PT1A-0-9023610 | 061 | CARBON DRUM NITROGEN PURGE | L15708 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | XLB 1A | KV0007/P6 |  |  |  | 23
R18 | R18-CY-034 | R18-C-034 | FLD | 107-GL | SOLENOID VALVE | RACK MOUNTED |  | CARBON DRUM NITROGEN PURGE |  | - | - | REF | REQ | F |  | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 23
R18 | R18-ZSC-034 | R18-C-034 | FLD | 107-GL | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CARBON DRUM NITROGEN PURGE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-ZSO-034 | R18-C-034 | FLD | 107-GL | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CARBON DRUM NITROGEN PURGE |  | - | - | REF | REQ | F |  | I.S |  | DI |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 23
R18 | R18-DIC-001 | R18-D-001 | PCS | 107-DF | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R18 | R18-DS-001 | R18-D-001 | MCC | 107-DF | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R18 | R18-DY-001 | R18-D-001 | MCC | 107-DF | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R18 | R18-DYC-001 | R18-D-001 | MCC | 107-DF | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 061.0 | JACKET PUMP | 8835 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R18 | R18-FI-001 | R18-F-001 | [6 empty] | REQ: By request
R18 | R18-FIT-001 | R18-FI01 | PKG | 107-GL | TRANSMITTER - FLOW | 15-N-SS1U-0-9023673 | 061 | N2 TO CARBON DRUM | L15724 | - | - | REF | REQ | C | Ref | I.S | AI |  |  |  | FG1 | KROHNE | H250/RR/M9S/ESK-EX |  | TI702-SP-5098 |  |  | 40
R18 | R18-HS-002 | R18-H-002 | FLD | 107-DF | SWITCH - HAND OP. | ADJ TO R18 | 061.0 | CRASH COOL | 7001 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | FG1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R18 | R18-HV-008 | R18-H-008 | FLD | 107-DF | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028789 | 061.0 | N2 PRESSURE SELECT | 7483 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R18 | R18-HZSC-008 | R18-H-008 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R18 | R18-HZSO-008 | R18-H-008 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R18 | R18-HV-009 | R18-H-009 | FLD | 107-DF | HAND VALVE | 25-P-PT1A-0-9023662 | 061.0 | AUX. INLET | 7409 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-HZSC-009 | R18-H-009 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-HZSO-009 | R18-H-009 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R18 | R18-HV-010 | R18-H-010 | FLD | 107-DF | HAND VALVE | 40-P-PT1A-0-9023861 | 061.0 | REAGENTS INLET | 7374 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R18 | R18-HZSC-010 | R18-H-010 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-HZSO-010 | R18-H-010 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-HV-012 | R18-H-012 | FLD | 107-DF | HAND VALVE | 25-P-PT1A-0-9023860 | 061.0 | SOLVENTS INLET | 7410 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-HZSC-012 | R18-H-012 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-HZSO-012 | R18-H-012 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | FG1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R18 | R18-HV-013 | R18-H-013 | FLD | 107-DF | HAND VALVE | 40-P-PT1A-0-9023861 | 061.0 | SLURRIES INLET | 7455 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R18 | R18-HZSC-013 | R18-H-013 | FLD | 107-DF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-HZSO-013 | R18-H-013 | FLD | 107-DF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R18 | R18-II-002 | R18-I-002 | PCS | 107-DF | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R18 | R18-IT-002 | R18-I-002 | MCC | 107-DF | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 061.0 | AGITATOR CURRENT | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 13 | FG1 | [6 empty] | 01
R18 | R18-LI-001 | R18-L-001 | PCS | 107-DF | INDICATOR - LEVEL |  |  | HIGH LEVEL | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-LT-001 | R18-L-001 | FLD | 107-DF | TRANSMITTER - LEVEL | R18/N3/100 | 061.0 | HIGH LEVEL | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | VEGA | VEGAPULS 63 | KL0028 | TI702-SP-5009 |  |  | 01
R18 | R18-LG-002 | R18-L-002 | PKG | 107-DF | LEVEL GAUGE | AGITATOR SEAL POT | 061.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
R18 | R18-PIC-001 | R18-P-001 | PCS | 107-DF | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R18 | R18-PIT-001 | R18-P-001 | FLD | 107-DF | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9023603 | 061.0 | PRESSURE | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R18 | R18-PI-002 | R18-P-002 | PCS | 107-DF | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6685; -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R18 | R18-PIT-002 | R18-P-002 | FLD | 107-DF | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9023603 | 061.0 | PRESSURE | 6685 | -1 to 2.3 barg | -1 to 0.033 barg | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R18 | R18-PAH-003 | R18-P-003 | PCS | 107-DF | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R18 | R18-PSH-003 | R18-P-003 | FLD | 107-DF | SWITCH - PRESSURE - DIAPHRAGM - HI | 150-P-PT1A-H-9023603 | 061.0 | HIGH PRESSURE | 6686 | set @ 2.2 barg | +/- 1% | SHE | REQ | C |  | I.S | DI |  |  | 32 | FG1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R18 | R18-PI-004 | R18-P-004 | FLD | 107-DF | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-0-9023630 | 061.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R18 | R18-PI-007 | R18-P-007 | FLD | 107-DF | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029508 | 061.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R18 | R18-PI-008 | R18-P-008 | FLD | 107-DF | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9023625 | 061.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R18 | R18-PI-009 | R18-P-009 | FLD | 107-GL | PRESSURE GAUGE | 40-P-PT1A-0-9023671 | 061 | CARBON DRUM INLET | L15725 | -1 TO 1 barg |  | REF | REQ | C | Ref | [6 empty] | WIKA | 233.30.063 | KP0006/P12 |  |  |  | 23
R18 | R18-PSV-012 | R18-P-012 | FLD | 107-DF | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9023655 | 061.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R18 | R18-PSV-013 | R18-P-013 | FLD | 107-DF | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023653 | 061.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R18 | R18-PSV-014 | R18-P-014 | FLD | 107-DF | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9023654 | 061.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R18 | R18-PRV-015 | R18-P-015 | FLD | 107-DF | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028788 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R18 | R18-PI-016 | R18-P-016 | PKG | 107-DF | PRESSURE GAUGE | AGITATOR SEAL POT | 061.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R18 | R18-SE-001 | R18-S-001 | PKG | 107-DF | ELEMENT - SPEED | AGITATOR SHAFT | 061.0 | AGITATOR | REF: REF; REQ: By request; F: C; I.S: I.S; DI: DI |  |  | 33 | FG1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R18 | R18-SI-001A | R18-S-001 | PCS | 107-DF | INDICATOR - SPEED |  |  | AGITATOR | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-SI-001B | R18-S-001 | FLD | 107-DF | INDICATOR - SPEED | ADJ TO R18 AGITATOR | 061.0 | AGITATOR | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AO |  |  | 21 | FG1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R18 | R18-DS-002 | R18-S-002 | MCC | 107-DF | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R18 | R18-DY-002 | R18-S-002 | MCC | 107-DF | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
R18 | R18-DYC-002 | R18-S-002 | MCC | 107-DF | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 061.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
R18 | R18-SC-002 | R18-S-002 | MCC | 107-DF | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 061.0 | AGITATOR | 6895 | 0 to 120 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | FG1 |  |  |  |  | SET Min 24 rpm & Max 118 rpm |  | 01
R18 | R18-SIC-002 | R18-S-002 | PCS | 107-DF | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R18 | R18-TE-001 | R18-T-001 | PKG | 107-DF | ELEMENT - TEMPERATURE - RTD | WITH R18-CV-001 |  | TEMPERATURE #1 | PKG: L6896; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R18 | R18-TI-001A | R18-T-001 | PCS | 107-DF | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6896; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R18 | R18-TI-001B | R18-T-001 | FLD | 107-DF | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R18 | 061.0 | TEMPERATURE #1 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R18 | R18-TT-001 | R18-T-001 | PKG | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | TEMPERATURE #1 | 6896 | -30 to 170 degC | +/-1 degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R18 | R18-TE-002 | R18-T-002 | PKG | 107-DF | ELEMENT - TEMPERATURE - RTD | WITH R18-CV-001 |  | TEMPERATURE #2 | PKG: L6896; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TI-002A | R18-T-002 | PCS | 107-DF | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6897; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R18 | R18-TI-002B | R18-T-002 | FLD | 107-DF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 061.0 | TEMPERATURE #2 | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | GA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R18 | R18-TT-002 | R18-T-002 | PKG | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | TEMPERATURE #2 | 6897 | -30 to 170 degC | +/-1 degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R18 | R18-TE-003 | R18-T-003 | PKG | 107-DF | ELEMENT - TEMPERATURE - RTD | R18/N6/100 |  | BAFFLE TEMPERATURE | PKG: L6898; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TI-003A | R18-T-003 | PCS | 107-DF | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6898; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R18 | R18-TI-003B | R18-T-003 | FLD | 107-DF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 061.0 | BAFFLE TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | GA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R18 | R18-TT-003 | R18-T-003 | PKG | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | BAFFLE TEMPERATURE | 6898 | -30 to 170 degC | +/-1 degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R18 | R18-TE-004 | R18-T-004 | FLD | 107-DF | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023625 |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TI-004A | R18-T-004 | PCS | 107-DF | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TI-004B | R18-T-004 | FLD | 107-DF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 061.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R18 | R18-TT-004 | R18-T-004 | FLD | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | JACKET INLET TEMP. | REF: SHE; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R18 | R18-TE-005 | R18-T-005 | FLD | 107-DF | ELEMENT - TEMPERATURE - RTD | 150-P-PT1A-H-9023603 |  | PC1 INLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TI-005 | R18-T-005 | PCS | 107-DF | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R18 | R18-TT-005 | R18-T-005 | FLD | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | PC1 INLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R18 | R18-TI-005A | R18-T-005A | [6 empty] | REQ: By request
R18 | R18-TE-006 | R18-T-006 | FLD | 107-DF | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9023610 |  | VC1 OFF GAS TEMPERATURE | PKG: L6484; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R18 | R18-TI-006A | R18-T-006 | PCS | 107-DF | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6484; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R18 | R18-TI-006B | R18-T-006 | FLD | 107-DF | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R18 | 061.0 | VC1 OFF GAS TEMPERATURE | REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R18 | R18-TT-006 | R18-T-006 | FLD | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | VC1 OFF GAS TEMPERATURE | 6484 | -20 to 80 degC | +/-1 degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R18 | R18-TE-007 | R18-T-007 | FLD | 107-DF | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9023617 |  | VC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TIC-007 | R18-T-007 | PCS | 107-DF | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R18 | R18-TT-007 | R18-T-007 | FLD | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R18 | R18-TE-008 | R18-T-008 | FLD | 107-DF | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9023614 |  | PC1 HTF RTN TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TIC-008 | R18-T-008 | PCS | 107-DF | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R18 | R18-TT-008 | R18-T-008 | FLD | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | PC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R18 | R18-TE-009 | R18-T-009 | FLD | 107-DF | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9023602 |  | DISTILLATE RTN TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TI-009A | R18-T-009 | PCS | 107-DF | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R18 | R18-TI-009B | R18-T-009 | FLD | 107-DF | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 061.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R18 | R18-TT-009 | R18-T-009 | FLD | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R18 | R18-TE-010 | R18-T-010 | FLD | 107-DF | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9023628 |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TI-010A | R18-T-010 | PCS | 107-DF | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
R18 | R18-TI-010B | R18-T-010 | FLD | 107-DF | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R18 | 061.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R18 | R18-TT-010 | R18-T-010 | FLD | 107-DF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061.0 | OUTLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R18 | R18-TE-011 | R18-T-011 | FLD | 107-GL | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023469 |  | CARBON DRUM INLET TEMPERATURE | PKG: L15709; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 23
R18 | R18-TI-011 | R18-T-011 | [6 empty] | PKG: L15709; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12
R18 | R18-TI-011A | R18-T-011 | PCS | 107-GL | INDICATOR - TEMPERATURE |  |  | CARBON DRUM INLET TEMPERATURE | -: -20 to 80 degC; -: +/- 1% |  |  | 0 | [7 empty] | 23
R18 | R18-TI-011B | R18-T-011 | FLD | 107-GL | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE |  | CARBON DRUM INLET TEMPERATURE | L15709 | -20 to 80 degC | +/-1 degC | SHE | 12 | C |  | I.S |  |  |  | 0 |  | ROSEMOUNT | [5 empty] | 23
R18 | R18-TT-011 | R18-T-011 | FLD | 107-GL | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 061 | CARBON DRUM INLET TEMPERATURE | L15709 | -20 to 80 degC | +/-1 degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P5 | TI702-SP-5012 |  |  | 23
R18 | R18-YA-001 | R18-Y-001 | PCS | 107-DF | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R18 | R18-YS-001 | R18-Y-001 | FUT | 107-DF | COMMON ALARM | R18 GAS SEAL ASSEMBLY | 061.0 | AGITATOR SEAL COMMON ALARM | PKG: 8708; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | FG1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R19 | R19-AG-001 | R19-A-001 | PKG | 107-EA | SPEED MOORE DISPLAY |  | 062.0 | AGITATOR | REF: REF; REQ: REQ | [10 empty] | 34
R19 | R19-BD-001 | R19-B-001 | FLD | 107-EA | RUPTURE DISC | 100-P-PT1A-H-9024103 | 062.0 | BURSTING DISC | 6749 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | C1 | BS&B | LCN / BAS + | KS0003/P2 | TI702-SP-5077 |  |  | 01
R19 | R19-YI-001 | R19-B-001 | PCS | 107-EA | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-CV-001 | R19-C-001 | PKG | 107-EA | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R19/K/100 | 062.0 | BOTTOM OUTLET VALVE | 8839 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R19 | R19-CY-001 | R19-C-001 | PKG | 107-EA | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | C1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R19 | R19-ZSC-001 | R19-C-001 | PKG | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R19 | R19-ZSO-001 | R19-C-001 | PKG | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R19 | R19-CV-004 | R19-C-004 | FLD | 107-EA | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9024130 | 062.0 | NITROGEN SUPPLY | 6794 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R19 | R19-CV-006 | R19-C-006 | FLD | 107-EA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024110 | 062.0 | SCRUBBER 02 | 7223 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-CY-006 | R19-C-006 | FLD | 107-EA | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R19 | R19-ZSC-006 | R19-C-006 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-006 | R19-C-006 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-CV-008 | R19-C-008 | FLD | 107-EA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9024137 | 062.0 | HOUSE VACUUM | 7327 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-CY-008 | R19-C-008 | FLD | 107-EA | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R19 | R19-ZSC-008 | R19-C-008 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-008 | R19-C-008 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-CV-009 | R19-C-009 | FLD | 107-EA | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-D-9029510 | 062.0 | COLD HTF SUPPLY | 7542 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R19 | R19-CY-009 | R19-C-009 | FLD | 107-EA | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R19 | R19-ZSC-009 | R19-C-009 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-009 | R19-C-009 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-CV-010 | R19-C-010 | FLD | 107-EA | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029253 | 062.0 | HOT HTF SUPPLY | 7518 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R19 | R19-ZSC-010 | R19-C-010 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-010 | R19-C-010 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-CV-011 | R19-C-011 | FLD | 107-EA | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9024123 | 062.0 | HOT HTF RTN | 6382 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R19 | R19-CV-012 | R19-C-012 | FLD | 107-EA | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9024156 | 062.0 | COLD HTF RTN | 6394 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R19 | R19-CV-013 | R19-C-013 | FLD | 107-EA | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9024125 | 062.0 | DUAL JACKET | 7510 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R19 | R19-CY-013 | R19-C-013 | FLD | 107-EA | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R19 | R19-ZSC-013 | R19-C-013 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-013 | R19-C-013 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-CV-014 | R19-C-014 | FLD | 107-EA | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9024159 | 062.0 | N2 TO BOTTOM OUTLET | 7152 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-CY-014 | R19-C-014 | FLD | 107-EA | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R19 | R19-ZSC-014 | R19-C-014 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-014 | R19-C-014 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-CV-015 | R19-C-015 | FLD | 107-EA | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-C-9024114 | 062.0 | PC1 TEMPERED HTF RTN | 6420 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R19 | R19-CV-016 | R19-C-016 | FLD | 107-EA | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9024117 | 062.0 | VC1 COLD HTF RTN | 6427 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R19 | R19-CV-018 | R19-C-018 | FLD | 107-EA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024105 | 062.0 | DISTILLATE VENT LINE | 7224 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-CY-018 | R19-C-018 | FLD | 107-EA | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R19 | R19-ZSC-018 | R19-C-018 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-018 | R19-C-018 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-CV-019 | R19-C-019 | FLD | 107-EA | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024882 | 062.0 | LIQUID INLET | 7247 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-CY-019 | R19-C-019 | FLD | 107-EA | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R19 | R19-ZSC-019 | R19-C-019 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-019 | R19-C-019 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-CV-021 | R19-C-021 | FLD | 107-EA | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9024110 | 062.0 | +VE PRESSURE CONTROL | 6844 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R19 | R19-CV-022 | R19-C-022 | FLD | 107-EA | V-BALL VALVE - CONTROL - F.C. | 50-VP-PT1A-0-9024137 | 062.0 | -VE PRESSURE CONTROL | 6846 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R19 | R19-CV-024 | R19-C-024 | FLD | 107-EA | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9024167 | 062.0 | SOLIDS INLET | 7355 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-CX-024 | R19-C-024 | SGS | 107-EA | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | C1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R19 | R19-CY-024 | R19-C-024 | FLD | 107-EA | SOLENOID VALVE | RACK MOUNTED | 062.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R19 | R19-ZSC-024 | R19-C-024 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-024 | R19-C-024 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-CV-025 | R19-C-025 | FLD | 107-EA | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9024110 | 062.0 | SOLIDS ADDITION VENT | 7303 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-CX-025 | R19-C-025 | SGS | 107-EA | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | C1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R19 | R19-CY-025 | R19-C-025 | FLD | 107-EA | SOLENOID VALVE | RACK MOUNTED | 062.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R19 | R19-ZSC-025 | R19-C-025 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-ZSO-025 | R19-C-025 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 062.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-DIC-001 | R19-D-001 | PCS | 107-EA | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-DS-001 | R19-D-001 | MCC | 107-EA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R19 | R19-DY-001 | R19-D-001 | MCC | 107-EA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R19 | R19-DYC-001 | R19-D-001 | MCC | 107-EA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 062.0 | JACKET PUMP | 8840 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R19 | R19-HS-002 | R19-H-002 | FLD | 107-EA | SWITCH - HAND OP. | ADJ TO R19 | 062.0 | CRASH COOL | 7002 | - | - | SIL | 6 | F | SOP | I.S | DI |  |  | 32 | C1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R19 | R19-HV-008 | R19-H-008 | FLD | 107-EA | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028815 | 062.0 | N2 PRESSURE SELECT | 7484 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R19 | R19-HZSC-008 | R19-H-008 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R19 | R19-HZSO-008 | R19-H-008 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R19 | R19-HV-009 | R19-H-009 | FLD | 107-EA | HAND VALVE | 25-P-PT1A-0-9024162 | 062.0 | AUX. INLET | 7412 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-HZSC-009 | R19-H-009 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-HZSO-009 | R19-H-009 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R19 | R19-HV-010 | R19-H-010 | FLD | 107-EA | HAND VALVE | 25-P-PT1A-0-9024882 | 062.0 | REAGENTS INLET | 7375 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R19 | R19-HZSC-010 | R19-H-010 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-HZSO-010 | R19-H-010 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-HV-012 | R19-H-012 | FLD | 107-EA | HAND VALVE | 25-P-PT1A-0-9024882 | 062.0 | SOLVENTS INLET | 7413 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-HZSC-012 | R19-H-012 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-HZSO-012 | R19-H-012 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R19 | R19-HV-013 | R19-H-013 | FLD | 107-EA | HAND VALVE | 40-P-PT1A-0-9024823 | 062.0 | SLURRIES INLET | 7456 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R19 | R19-HZSC-013 | R19-H-013 | FLD | 107-EA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-HZSO-013 | R19-H-013 | FLD | 107-EA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R19 | R19-II-002 | R19-I-002 | PCS | 107-EA | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-IT-002 | R19-I-002 | MCC | 107-EA | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 062.0 | AGITATOR CURRENT | 8838 | 0 to 10 amp | +/- 1% | REF | REQ | C |  | N.I.S | AI |  |  | 13 | C1 | [6 empty] | 01
R19 | R19-LAH-001 | R19-L-001 | PCS | 107-EA | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-LE-001 | R19-L-001 | FLD | 107-EA | ELEMENT - LEVEL | 100-P-PT1A-H-9024103 | 062.0 | HIGH LEVEL |  | Fixed | - | SHE | 12 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R19 | R19-LSH-001 | R19-L-001 | CPR | 107-EA | SWITCH - LEVEL - HIGH | 100-P-PT1A-H-9024103 | 062.0 | HIGH LEVEL | 6635 | - | - | SHE | 12 | F |  | N.I.S | DI |  |  | 35 | C1 | ENDRESS + HAUSER | FDL31-GYY9AC70 | KL0014 |  |  |  | 01
R19 | R19-LG-002 | R19-L-002 | PKG | 107-EA | LEVEL GAUGE | AGITATOR SEAL POT | 062.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
R19 | R19-PIC-001 | R19-P-001 | PCS | 107-EA | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-PIT-001 | R19-P-001 | FLD | 107-EA | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9024103 | 062.0 | PRESSURE | 7028 | -1 to 2.3 barg | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R19 | R19-PI-002 | R19-P-002 | PCS | 107-EA | INDICATOR - PRESSURE |  |  | PRESSURE | -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R19 | R19-PIT-002 | R19-P-002 | FLD | 107-EA | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9024103 | 062.0 | PRESSURE | 6688 | -1 to 2.3 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R19 | R19-PAH-003 | R19-P-003 | PCS | 107-EA | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-PSH-003 | R19-P-003 | FLD | 107-EA | SWITCH - PRESSURE - DIAPHRAGM - HI | 100-P-PT1A-H-9024103 | 062.0 | HIGH PRESSURE | 6689 | set @ 2.2 barg | +/- 1% | SHE | REQ | C |  | I.S | DI |  |  | 32 | C1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R19 | R19-PI-004 | R19-P-004 | FLD | 107-EA | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-09024130 | 062.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R19 | R19-PI-007 | R19-P-007 | FLD | 107-EA | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029510 | 062.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R19 | R19-PI-008 | R19-P-008 | FLD | 107-EA | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9024125 | 062.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R19 | R19-PSV-012 | R19-P-012 | FLD | 107-EA | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9024155 | 062.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R19 | R19-PSV-013 | R19-P-013 | FLD | 107-EA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9024153 | 062.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R19 | R19-PSV-014 | R19-P-014 | FLD | 107-EA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9024154 | 062.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R19 | R19-PRV-015 | R19-P-015 | FLD | 107-EA | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028814 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R19 | R19-PI-016 | R19-P-016 | PKG | 107-EA | PRESSURE GAUGE | AGITATOR SEAL POT | 062.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R19 | R19-SE-001 | R19-S-001 | PKG | 107-EA | ELEMENT - SPEED | AGITATOR SHAFT | 062.0 | AGITATOR | 6956 | 0 to 153 rpm | - | REF | REQ | C |  | I.S | DI |  |  | 33 | C1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R19 | R19-SI-001A | R19-S-001 | PCS | 107-EA | INDICATOR - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-SI-001B | R19-S-001 | FLD | 107-EA | INDICATOR - SPEED | ADJ TO R19 AGITATOR | 062.0 | AGITATOR |  | 0 to 200 rpm | +/- 1% | REF | REQ | C |  | I.S | AO |  |  | 21 | C1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R19 | R19-DS-002 | R19-S-002 | MCC | 107-EA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R19 | R19-DY-002 | R19-S-002 | MCC | 107-EA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R19 | R19-DYC-002 | R19-S-002 | MCC | 107-EA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 062.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R19 | R19-SC-002 | R19-S-002 | MCC | 107-EA | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 062.0 | AGITATOR | 8838 | 0 to 160 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | C1 |  |  |  |  | SET Min 31rpm & Max 153 rpm |  | 01
R19 | R19-SIC-002 | R19-S-002 | PCS | 107-EA | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TE-001 | R19-T-001 | PKG | 107-EA | ELEMENT - TEMPERATURE - RTD | WITH R19-CV-001 |  | TEMPERATURE #1 | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-001A | R19-T-001 | PCS | 107-EA | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-001B | R19-T-001 | FLD | 107-EA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R19 | 062.0 | TEMPERATURE #1 |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R19 | R19-TT-001 | R19-T-001 | PKG | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | TEMPERATURE #1 | 6921 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R19 | R19-TE-002 | R19-T-002 | PKG | 107-EA | ELEMENT - TEMPERATURE - RTD | WITH R19-CV-001 |  | TEMPERATURE #2 | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-002A | R19-T-002 | PCS | 107-EA | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-002B | R19-T-002 | FLD | 107-EA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 062.0 | TEMPERATURE #2 |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R19 | R19-TT-002 | R19-T-002 | PKG | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | TEMPERATURE #2 | 6922 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R19 | R19-TE-003 | R19-T-003 | PKG | 107-EA | ELEMENT - TEMPERATURE - RTD | R19/N2/100 |  | BAFFLE TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-003A | R19-T-003 | PCS | 107-EA | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-003B | R19-T-003 | FLD | 107-EA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 062.0 | BAFFLE TEMPERATURE |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R19 | R19-TT-003 | R19-T-003 | PKG | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | BAFFLE TEMPERATURE | 6923 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R19 | R19-TE-004 | R19-T-004 | FLD | 107-EA | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9024125 |  | JACKET INLET TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-004A | R19-T-004 | PCS | 107-EA | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-004B | R19-T-004 | FLD | 107-EA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 062.0 | JACKET INLET TEMP. |  | -30 to 170 degC | +/- 1% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R19 | R19-TT-004 | R19-T-004 | FLD | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | JACKET INLET TEMP. | 6924 | -30 to 170 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R19 | R19-TE-005 | R19-T-005 | FLD | 107-EA | ELEMENT - TEMPERATURE - RTD | 100-P-PT1A-H-9024103 |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TI-005 | R19-T-005 | PCS | 107-EA | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TT-005 | R19-T-005 | FLD | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | PC1 INLET TEMPERATURE | 6489 | -20 to 180 degC | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R19 | R19-TE-006 | R19-T-006 | FLD | 107-EA | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9024110 |  | VC1 OFF GAS TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-006A | R19-T-006 | PCS | 107-EA | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R19 | R19-TI-006B | R19-T-006 | FLD | 107-EA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R19 | 062.0 | VC1 OFF GAS TEMPERATURE |  | -20 to 80 degC | +/- 1% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R19 | R19-TT-006 | R19-T-006 | FLD | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | VC1 OFF GAS TEMPERATURE | 6490 | -20 to 80 degC | +/- 1% | SHE | 6 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R19 | R19-TE-007 | R19-T-007 | FLD | 107-EA | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9024117 |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TIC-007 | R19-T-007 | PCS | 107-EA | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TT-007 | R19-T-007 | FLD | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | VC1 HTF RTN TEMPERATURE | 6491 | -30 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R19 | R19-TE-008 | R19-T-008 | FLD | 107-EA | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-C-9024114 |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TIC-008 | R19-T-008 | PCS | 107-EA | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TT-008 | R19-T-008 | FLD | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | PC1 HTF RTN TEMPERATURE | 6492 | -20 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R19 | R19-TE-009 | R19-T-009 | FLD | 107-EA | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9024102 |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TI-009A | R19-T-009 | PCS | 107-EA | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TI-009B | R19-T-009 | FLD | 107-EA | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 062.0 | DISTILLATE RTN TEMP. |  | -20 to 80 degC | +/- 0.5% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R19 | R19-TT-009 | R19-T-009 | FLD | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | DISTILLATE RTN TEMP. | 6493 | -20 to 80 degC | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R19 | R19-TE-010 | R19-T-010 | FLD | 107-EA | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9024128 |  | OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TI-010A | R19-T-010 | PCS | 107-EA | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-TI-010B | R19-T-010 | FLD | 107-EA | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R19 | 062.0 | OUTLET TEMPERATURE |  | -30 to 170 degC | +/- 1% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R19 | R19-TT-010 | R19-T-010 | FLD | 107-EA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 062.0 | OUTLET TEMPERATURE | 6494 | -30 to 170 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R19 | R19-WE-001A | R19-W-001 | FLD | 107-EA | LOAD CELL - DUMMY | REACTOR R19 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 20kN |  |  |  |  | 01 | bar: PKG
R19 | R19-WE-001B | R19-W-001 | FLD | 107-EA | LOAD CELL - DUMMY | REACTOR R19 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 20kN |  |  |  |  | 01 | bar: PKG
R19 | R19-WE-001C | R19-W-001 | FLD | 107-EA | LOAD CELL - DUMMY | REACTOR R19 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 20kN |  |  |  |  | 01 | bar: PKG
R19 | R19-YA-001 | R19-Y-001 | PCS | 107-EA | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R19 | R19-YS-001 | R19-Y-001 | FUT | 107-EA | COMMON ALARM | R19 GAS SEAL ASSEMBLY | 062.0 | AGITATOR SEAL COMMON ALARM | PKG: 8810; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | C1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R20 | R20-AG-001 | R20-A-001 | PKG | 107-EB | SPEED MOORE DISPLAY |  | 063.0 | AGITATOR | REF: REF; REQ: REQ | [10 empty] | 34
R20 | R20-BD-001 | R20-B-001 | FLD | 107-EB | RUPTURE DISC | 80-P-PT1A-H-9024203 | 063.0 | BURSTING DISC | 6750 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | C1 | BS&B | LCN / BAS + | KS0003/P2 | TI702-SP-5077 |  |  | 01
R20 | R20-YI-001 | R20-B-001 | PCS | 107-EB | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-CV-001 | R20-C-001 | PKG | 107-EB | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R20/K/80 | 063.0 | BOTTOM OUTLET VALVE | 8843 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R20 | R20-CY-001 | R20-C-001 | PKG | 107-EB | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | C1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R20 | R20-ZSC-001 | R20-C-001 | PKG | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R20 | R20-ZSO-001 | R20-C-001 | PKG | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R20 | R20-CV-004 | R20-C-004 | FLD | 107-EB | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9024230 | 063.0 | NITROGEN SUPPLY | 6795 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R20 | R20-CV-006 | R20-C-006 | FLD | 107-EB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024210 | 063.0 | SCRUBBER 02 | 7225 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-CY-006 | R20-C-006 | FLD | 107-EB | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R20 | R20-ZSC-006 | R20-C-006 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-006 | R20-C-006 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-CV-008 | R20-C-008 | FLD | 107-EB | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9024237 | 063.0 | HOUSE VACUUM | 7278 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-CY-008 | R20-C-008 | FLD | 107-EB | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R20 | R20-ZSC-008 | R20-C-008 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-008 | R20-C-008 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-CV-009 | R20-C-009 | FLD | 107-EB | BALL VALVE - ON/OFF - F.O. | 50-HT-CS3A-D-9029607 | 063.0 | COLD HTF SUPPLY | 7502 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R20 | R20-CY-009 | R20-C-009 | FLD | 107-EB | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R20 | R20-ZSC-009 | R20-C-009 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-009 | R20-C-009 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-CV-010 | R20-C-010 | FLD | 107-EB | BALL VALVE - ON/OFF - F.C. | 50-HT-CS3A-D-9029261 | 063.0 | HOT HTF SUPPLY | 7497 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R20 | R20-ZSC-010 | R20-C-010 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-010 | R20-C-010 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-CV-011 | R20-C-011 | FLD | 107-EB | GLOBE VALVE - CONTROL - F.C. | 50-HT-CS3A-D-9024223 | 063.0 | HOT HTF RTN | 6366 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R20 | R20-CV-012 | R20-C-012 | FLD | 107-EB | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-D-9024256 | 063.0 | COLD HTF RTN | 6370 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R20 | R20-CV-013 | R20-C-013 | FLD | 107-EB | BALL VALVE - ON/OFF - F.O. | 40-HT-CS3A-D-9024225 | 063.0 | DUAL JACKET | 7489 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R20 | R20-CY-013 | R20-C-013 | FLD | 107-EB | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R20 | R20-ZSC-013 | R20-C-013 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-013 | R20-C-013 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-CV-014 | R20-C-014 | FLD | 107-EB | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9024259 | 063.0 | N2 TO BOTTOM OUTLET | 7153 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-CY-014 | R20-C-014 | FLD | 107-EB | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R20 | R20-ZSC-014 | R20-C-014 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-014 | R20-C-014 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-CV-015 | R20-C-015 | FLD | 107-EB | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9024214 | 063.0 | PC1 TEMPERED HTF RTN | 6409 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R20 | R20-CV-016 | R20-C-016 | FLD | 107-EB | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9024217 | 063.0 | VC1 COLD HTF RTN | 6414 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R20 | R20-CV-018 | R20-C-018 | FLD | 107-EB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024205 | 063.0 | DISTILLATE VENT LINE | 7226 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-CY-018 | R20-C-018 | FLD | 107-EB | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R20 | R20-ZSC-018 | R20-C-018 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-018 | R20-C-018 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-CV-019 | R20-C-019 | FLD | 107-EB | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024863 | 063.0 | LIQUID INLET | 7248 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-CY-019 | R20-C-019 | FLD | 107-EB | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R20 | R20-ZSC-019 | R20-C-019 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-019 | R20-C-019 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-CV-021 | R20-C-021 | FLD | 107-EB | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9024210 | 063.0 | +VE PRESSURE CONTROL | 6843 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R20 | R20-CV-022 | R20-C-022 | FLD | 107-EB | V-BALL VALVE - CONTROL - F.C. | 50-VP-PT1A-0-9024237 | 063.0 | -VE PRESSURE CONTROL | 6847 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R20 | R20-CV-024 | R20-C-024 | FLD | 107-EB | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9024267 | 063.0 | SOLIDS INLET | 7356 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-CX-024 | R20-C-024 | SGS | 107-EB | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | C1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R20 | R20-CY-024 | R20-C-024 | FLD | 107-EB | SOLENOID VALVE | RACK MOUNTED | 063.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R20 | R20-ZSC-024 | R20-C-024 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-024 | R20-C-024 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-CV-025 | R20-C-025 | FLD | 107-EB | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9024210 | 063.0 | SOLIDS ADDITION VENT | 7304 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-CX-025 | R20-C-025 | SGS | 107-EB | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | C1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R20 | R20-CY-025 | R20-C-025 | FLD | 107-EB | SOLENOID VALVE | RACK MOUNTED | 063.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R20 | R20-ZSC-025 | R20-C-025 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-ZSO-025 | R20-C-025 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 063.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-DIC-001 | R20-D-001 | PCS | 107-EB | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-DS-001 | R20-D-001 | MCC | 107-EB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R20 | R20-DY-001 | R20-D-001 | MCC | 107-EB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R20 | R20-DYC-001 | R20-D-001 | MCC | 107-EB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 063.0 | JACKET PUMP | 8844 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R20 | R20-HS-002 | R20-H-002 | FLD | 107-EB | SWITCH - HAND OP. | ADJ TO R20 | 063.0 | CRASH COOL | 7003 | - | - | SIL | 6 | F | SOP | I.S | DI |  |  | 32 | C1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R20 | R20-HV-008 | R20-H-008 | FLD | 107-EB | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028829 | 063.0 | N2 PRESSURE SELECT | 7485 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R20 | R20-HZSC-008 | R20-H-008 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R20 | R20-HZSO-008 | R20-H-008 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R20 | R20-HV-009 | R20-H-009 | FLD | 107-EB | HAND VALVE | 25-P-PT1A-0-9024262 | 063.0 | AUX. INLET | 7414 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-HZSC-009 | R20-H-009 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-HZSO-009 | R20-H-009 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R20 | R20-HV-010 | R20-H-010 | FLD | 107-EB | HAND VALVE | 40-P-PT1A-0-9024863 | 063.0 | REAGENTS INLET | 7376 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R20 | R20-HZSC-010 | R20-H-010 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-HZSO-010 | R20-H-010 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-HV-012 | R20-H-012 | FLD | 107-EB | HAND VALVE | 25-P-PT1A-0-9024862 | 063.0 | SOLVENTS INLET | 7415 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-HZSC-012 | R20-H-012 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-HZSO-012 | R20-H-012 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R20 | R20-HV-013 | R20-H-013 | FLD | 107-EB | HAND VALVE | 40-P-PT1A-0-9024863 | 063.0 | SLURRIES INLET | 7457 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R20 | R20-HZSC-013 | R20-H-013 | FLD | 107-EB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-HZSO-013 | R20-H-013 | FLD | 107-EB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R20 | R20-II-002 | R20-I-002 | PCS | 107-EB | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-IT-002 | R20-I-002 | MCC | 107-EB | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 063.0 | AGITATOR CURRENT | 8847 | 0 to 5 amp | +/- 1% | REF | REQ | C |  | N.I.S | AI |  |  | 13 | C1 | [6 empty] | 01
R20 | R20-LAH-001 | R20-L-001 | PCS | 107-EB | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-LE-001 | R20-L-001 | FLD | 107-EB | ELEMENT - LEVEL | 80-P-PT1A-H-9024203 | 063.0 | HIGH LEVEL |  | Fixed | - | SHE | 12 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R20 | R20-LSH-001 | R20-L-001 | CPR | 107-EB | SWITCH - LEVEL - HIGH | 80-P-PT1A-H-9024203 | 063.0 | HIGH LEVEL | 6636 | - | - | SHE | 12 | F |  | N.I.S | DI |  |  | 35 | C1 | ENDRESS + HAUSER | FDL31-GYY9AC70 | KL0014 |  |  |  | 01
R20 | R20-LG-002 | R20-L-002 | PKG | 107-EB | LEVEL GAUGE | AGITATOR SEAL POT | 063.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
R20 | R20-PIC-001 | R20-P-001 | PCS | 107-EB | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-PIT-001 | R20-P-001 | FLD | 107-EB | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9024203 | 063.0 | PRESSURE | 7029 | -1 to 2.3 barg | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R20 | R20-PI-002 | R20-P-002 | PCS | 107-EB | INDICATOR - PRESSURE |  |  | PRESSURE | -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R20 | R20-PIT-002 | R20-P-002 | FLD | 107-EB | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-PT1A-H-9024203 | 063.0 | PRESSURE | 6691 | -1 to 2.3 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R20 | R20-PAH-003 | R20-P-003 | PCS | 107-EB | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-PSH-003 | R20-P-003 | FLD | 107-EB | SWITCH - PRESSURE - DIAPHRAGM - HI | 80-P-PT1A-H-9024203 | 063.0 | HIGH PRESSURE | 6692 | set @ 2.2 barg | +/- 1% | SHE | REQ | C |  | I.S | DI |  |  | 32 | C1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R20 | R20-PI-004 | R20-P-004 | FLD | 107-EB | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9024230 | 063.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R20 | R20-PI-007 | R20-P-007 | FLD | 107-EB | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-C-9029607 | 063.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R20 | R20-PI-008 | R20-P-008 | FLD | 107-EB | PRESSURE GAUGE - DIAPHRAGM | 50-HT-CS3A-D-9024225 | 063.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R20 | R20-PSV-012 | R20-P-012 | FLD | 107-EB | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9024255 | 063.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R20 | R20-PSV-013 | R20-P-013 | FLD | 107-EB | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9024253 | 063.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R20 | R20-PSV-014 | R20-P-014 | FLD | 107-EB | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9024254 | 063.0 | PC1 HTF RELIEF | -: 9 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 45
R20 | R20-PRV-015 | R20-P-015 | FLD | 107-EB | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028828 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R20 | R20-PI-016 | R20-P-016 | PKG | 107-EB | PRESSURE GAUGE | AGITATOR SEAL POT | 063.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 25 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R20 | R20-SE-001 | R20-S-001 | PKG | 107-EB | ELEMENT - SPEED | AGITATOR SHAFT | 063.0 | AGITATOR | 6929 | 0 to 186 rpm | - | REF | REQ | C |  | I.S | DI |  |  | 33 | C1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R20 | R20-SI-001A | R20-S-001 | PCS | 107-EB | INDICATOR - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-SI-001B | R20-S-001 | FLD | 107-EB | INDICATOR - SPEED | ADJ TO R20 AGITATOR | 063.0 | AGITATOR |  | 0 to 200 rpm | +/- 1% | REF | REQ | C |  | I.S | AO |  |  | 21 | C1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R20 | R20-DS-002 | R20-S-002 | MCC | 107-EB | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R20 | R20-DY-002 | R20-S-002 | MCC | 107-EB | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R20 | R20-DYC-002 | R20-S-002 | MCC | 107-EB | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 063.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R20 | R20-SC-002 | R20-S-002 | MCC | 107-EB | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 063.0 | AGITATOR | 8847 | 0 to 200 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | C1 |  |  |  |  | SET Min 37 rpm & Max 186 rpm |  | 01
R20 | R20-SIC-002 | R20-S-002 | PCS | 107-EB | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TE-001 | R20-T-001 | PKG | 107-EB | ELEMENT - TEMPERATURE - RTD | WITH R20-CV-001 |  | TEMPERATURE #1 | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-001A | R20-T-001 | PCS | 107-EB | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-001B | R20-T-001 | FLD | 107-EB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ R20 | 063.0 | TEMPERATURE #1 |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R20 | R20-TT-001 | R20-T-001 | PKG | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | TEMPERATURE #1 | 6925 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R20 | R20-TE-002 | R20-T-002 | PKG | 107-EB | ELEMENT - TEMPERATURE - RTD | WITH R20-CV-001 |  | TEMPERATURE #2 | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-002A | R20-T-002 | PCS | 107-EB | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-002B | R20-T-002 | FLD | 107-EB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 063.0 | TEMPERATURE #2 |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R20 | R20-TT-002 | R20-T-002 | PKG | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | TEMPERATURE #2 | 6926 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R20 | R20-TE-003 | R20-T-003 | PKG | 107-EB | ELEMENT - TEMPERATURE - RTD | R20/N2/80 |  | BAFFLE TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-003A | R20-T-003 | PCS | 107-EB | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-003B | R20-T-003 | FLD | 107-EB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 063.0 | BAFFLE TEMPERATURE |  | -30 to 170 degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R20 | R20-TT-003 | R20-T-003 | PKG | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | BAFFLE TEMPERATURE | 6927 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R20 | R20-TE-004 | R20-T-004 | FLD | 107-EB | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9024225 |  | JACKET INLET TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-004A | R20-T-004 | PCS | 107-EB | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-004B | R20-T-004 | FLD | 107-EB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 063.0 | JACKET INLET TEMP. |  | -30 to 170 degC | +/- 1% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R20 | R20-TT-004 | R20-T-004 | FLD | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | JACKET INLET TEMP. | 6928 | -30 to 170 degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R20 | R20-TE-005 | R20-T-005 | FLD | 107-EB | ELEMENT - TEMPERATURE - RTD | 80-P-PT1A-H-9024203 |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TI-005 | R20-T-005 | PCS | 107-EB | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TT-005 | R20-T-005 | FLD | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | PC1 INLET TEMPERATURE | 6495 | -20 to 180 degC | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R20 | R20-TE-006 | R20-T-006 | FLD | 107-EB | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9024210 | 063.0 | VC1 OFF GAS TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-006A | R20-T-006 | PCS | 107-EB | INDICATOR - TEMPERATURE |  | 063.0 | VC1 OFF GAS TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R20 | R20-TI-006B | R20-T-006 | FLD | 107-EB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ R20 | 063.0 | VC1 OFF GAS TEMPERATURE |  | -20 to 80 degC | +/- 1% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R20 | R20-TT-006 | R20-T-006 | FLD | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | VC1 OFF GAS TEMPERATURE | 6496 | -20 to 80 degC | +/- 1% | SHE | 6 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R20 | R20-TE-007 | R20-T-007 | FLD | 107-EB | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9024217 |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TIC-007 | R20-T-007 | PCS | 107-EB | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TT-007 | R20-T-007 | FLD | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | VC1 HTF RTN TEMPERATURE | 6497 | -30 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R20 | R20-TE-008 | R20-T-008 | FLD | 107-EB | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9024214 |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TIC-008 | R20-T-008 | PCS | 107-EB | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TT-008 | R20-T-008 | FLD | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | PC1 HTF RTN TEMPERATURE | 6498 | -20 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R20 | R20-TE-009 | R20-T-009 | FLD | 107-EB | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9024202 |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TI-009A | R20-T-009 | PCS | 107-EB | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TI-009B | R20-T-009 | FLD | 107-EB | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 063.0 | DISTILLATE RTN TEMP. |  | -20 to 80 degC | +/- 0.5% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 34
R20 | R20-TT-009 | R20-T-009 | FLD | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | DISTILLATE RTN TEMP. | 6499 | -20 to 80 degC | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R20 | R20-TE-010 | R20-T-010 | FLD | 107-EB | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-D-9024228 |  | OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TI-010A | R20-T-010 | PCS | 107-EB | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-TI-010B | R20-T-010 | FLD | 107-EB | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ R20 | 063.0 | OUTLET TEMPERATURE |  | -30 to 170 degC | +/- 1% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R20 | R20-TT-010 | R20-T-010 | FLD | 107-EB | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 063.0 | OUTLET TEMPERATURE | 6500 | -30 to 170 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R20 | R20-WE-001A | R20-W-001 | FLD | 107-EB | LOAD CELL - DUMMY | REACTOR R20 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 5kN |  |  |  |  | 01 | bar: PKG
R20 | R20-WE-001B | R20-W-001 | FLD | 107-EB | LOAD CELL - DUMMY | REACTOR R20 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 5kN |  |  |  |  | 01 | bar: PKG
R20 | R20-WE-001C | R20-W-001 | FLD | 107-EB | LOAD CELL - DUMMY | REACTOR R20 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 5kN |  |  |  |  | 01 | bar: PKG
R20 | R20-YA-001 | R20-Y-001 | PCS | 107-EB | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R20 | R20-YS-001 | R20-Y-001 | FUT | 107-EB | COMMON ALARM | R20 GAS SEAL ASSEMBLY | 063.0 | AGITATOR SEAL COMMON ALARM | PKG: 8857; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | C1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R21 | R21-AG-001 | R21-A-001 | PKG | 107-EC | SPEED MOORE DISPLAY |  | 064.0 | AGITATOR | REF: REF; REQ: by request | [10 empty] | 34
R21 | R21-BD-001 | R21-B-001 | FLD | 107-EC | RUPTURE DISC | 150-P-PT1A-H-9024303 | 064.0 | BURSTING DISC | 6751 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | C1 | BS&B | LCN / BAS + | KS0003/P2 | TI702-SP-5077 |  |  | 01
R21 | R21-YI-001 | R21-B-001 | PCS | 107-EC | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R21 | R21-CV-001 | R21-C-001 | PKG | 107-EC | BOTTOM OUTLET VALVE - ON/OFF - F.C. | R21/K/100 | 064.0 | BOTTOM OUTLET VALVE | 8848 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R21 | R21-CY-001 | R21-C-001 | PKG | 107-EC | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | C1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R21 | R21-ZSC-001 | R21-C-001 | PKG | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R21 | R21-ZSO-001 | R21-C-001 | PKG | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R21 | R21-CV-004 | R21-C-004 | FLD | 107-EC | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-H-9024330 | 064.0 | NITROGEN SUPPLY | 6796 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R21 | R21-CV-006 | R21-C-006 | FLD | 107-EC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024310 | 064.0 | SCRUBBER 02 | 7227 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-CY-006 | R21-C-006 | FLD | 107-EC | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R21 | R21-ZSC-006 | R21-C-006 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-ZSO-006 | R21-C-006 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-CV-008 | R21-C-008 | FLD | 107-EC | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9024337 | 064.0 | HOUSE VACUUM | 7328 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-CY-008 | R21-C-008 | FLD | 107-EC | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R21 | R21-ZSC-008 | R21-C-008 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-ZSO-008 | R21-C-008 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-CV-009 | R21-C-009 | FLD | 107-EC | BALL VALVE - ON/OFF - F.O. | 80-HT-CS3A-D-9029509 | 064.0 | COLD HTF SUPPLY | 7543 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R21 | R21-CY-009 | R21-C-009 | FLD | 107-EC | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R21 | R21-ZSC-009 | R21-C-009 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-ZSO-009 | R21-C-009 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-CV-010 | R21-C-010 | FLD | 107-EC | BALL VALVE - ON/OFF - F.C. | 80-HT-CS3A-D-9029252 | 064.0 | HOT HTF SUPPLY | 7519 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R21 | R21-ZSC-010 | R21-C-010 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-ZSO-010 | R21-C-010 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-CV-011 | R21-C-011 | FLD | 107-EC | GLOBE VALVE - CONTROL - F.C. | 80-HT-CS3A-D-9024323 | 064.0 | HOT HTF RTN | 6383 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R21 | R21-CV-012 | R21-C-012 | FLD | 107-EC | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-D-9024356 | 064.0 | COLD HTF RTN | 6395 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R21 | R21-CV-014 | R21-C-014 | FLD | 107-EC | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9024359 | 064.0 | N2 TO BOTTOM OUTLET | 7154 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-CY-014 | R21-C-014 | FLD | 107-EC | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R21 | R21-ZSC-014 | R21-C-014 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-ZSO-014 | R21-C-014 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-CV-015 | R21-C-015 | FLD | 107-EC | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-CS3A-C-9024314 | 064.0 | PC1 TEMPERED HTF RTN | 6434 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R21 | R21-CV-016 | R21-C-016 | FLD | 107-EC | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9024317 | 064.0 | VC1 COLD HTF RTN | 6440 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R21 | R21-CV-018 | R21-C-018 | FLD | 107-EC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024305 | 064.0 | DISTILLATE VENT LINE | 7279 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-CY-018 | R21-C-018 | FLD | 107-EC | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R21 | R21-ZSC-018 | R21-C-018 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-ZSO-018 | R21-C-018 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-CV-019 | R21-C-019 | FLD | 107-EC | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024821 | 064.0 | LIQUID INLET | 7249 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-CY-019 | R21-C-019 | FLD | 107-EC | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R21 | R21-ZSC-019 | R21-C-019 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-ZSO-019 | R21-C-019 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-CV-021 | R21-C-021 | FLD | 107-EC | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9024310 | 064.0 | +VE PRESSURE CONTROL | 6842 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R21 | R21-CV-022 | R21-C-022 | FLD | 107-EC | V-BALL VALVE - CONTROL - F.C. | 50-VP-PT1A-0-9024337 | 064.0 | -VE PRESSURE CONTROL | 6848 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R21 | R21-CV-024 | R21-C-024 | FLD | 107-EC | BALL VALVE - ON/OFF - F.C. | 100-P-PT1A-H-9024367 | 064.0 | SOLIDS INLET | 7357 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-CX-024 | R21-C-024 | SGS | 107-EC | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | C1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R21 | R21-CY-024 | R21-C-024 | FLD | 107-EC | SOLENOID VALVE | RACK MOUNTED | 064.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R21 | R21-ZSC-024 | R21-C-024 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-ZSO-024 | R21-C-024 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-CV-025 | R21-C-025 | FLD | 107-EC | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9024310 | 064.0 | SOLIDS ADDITION VENT | 7305 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-CX-025 | R21-C-025 | SGS | 107-EC | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | C1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R21 | R21-CY-025 | R21-C-025 | FLD | 107-EC | SOLENOID VALVE | RACK MOUNTED | 064.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R21 | R21-ZSC-025 | R21-C-025 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-ZSO-025 | R21-C-025 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 064.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-DIC-001 | R21-D-001 | PCS | 107-EC | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R21 | R21-DS-001 | R21-D-001 | MCC | 107-EC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R21 | R21-DY-001 | R21-D-001 | MCC | 107-EC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R21 | R21-DYC-001 | R21-D-001 | MCC | 107-EC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 064.0 | JACKET PUMP | 8725 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R21 | R21-HS-002 | R21-H-002 | FLD | 107-EC | SWITCH - HAND OP. | ADJ TO R21 | 064.0 | CRASH COOL | 7004 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | C1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R21 | R21-HV-008 | R21-H-008 | FLD | 107-EC | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028812 | 064.0 | N2 PRESSURE SELECT | 7486 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R21 | R21-HZSC-008 | R21-H-008 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R21 | R21-HZSO-008 | R21-H-008 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R21 | R21-HV-009 | R21-H-009 | FLD | 107-EC | HAND VALVE | 25-P-PT1A-0-9024362 | 064.0 | AUX. INLET | 7416 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-HZSC-009 | R21-H-009 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-HZSO-009 | R21-H-009 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R21 | R21-HV-010 | R21-H-010 | FLD | 107-EC | HAND VALVE | 40-P-PT1A-0-9024821 | 064.0 | REAGENTS INLET | 7377 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | VALVE SIZE 15mm |  | 01
R21 | R21-HZSC-010 | R21-H-010 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-HZSO-010 | R21-H-010 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-HV-012 | R21-H-012 | FLD | 107-EC | HAND VALVE | 25-P-PT1A-0-9024899 | 064.0 | SOLVENTS INLET | 7417 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-HZSC-012 | R21-H-012 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-HZSO-012 | R21-H-012 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R21 | R21-HV-013 | R21-H-013 | FLD | 107-EC | HAND VALVE | 40-P-PT1A-0-9024821 | 064.0 | SLURRIES INLET | 7458 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R21 | R21-HZSC-013 | R21-H-013 | FLD | 107-EC | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-HZSO-013 | R21-H-013 | FLD | 107-EC | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R21 | R21-II-002 | R21-I-002 | PCS | 107-EC | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R21 | R21-IT-002 | R21-I-002 | MCC | 107-EC | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 064.0 | AGITATOR CURRENT | REF: REF; REQ: by request; F: C; I.S: N.I.S; DI: AI |  |  | 13 | C1 | [6 empty] | 01
R21 | R21-LI-001 | R21-L-001 | PCS | 107-EC | INDICATOR - LEVEL |  |  | LEVEL | PKG: L6659; REF: SHE; REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-LT-001 | R21-L-001 | FLD | 107-EC | TRANSMITTER - LEVEL | R21/N4/100 | 064.0 | LEVEL | 6659 |  |  | SHE | by request | C |  | I.S | AI |  |  | 11 | C1 | VEGA | VEGAPULS 63 | KL0028 | TI702-SP-5009 |  |  | 01
R21 | R21-LG-002 | R21-L-002 | PKG | 107-EC | LEVEL GAUGE | AGITATOR SEAL POT | 064.0 | AGITATOR SEAL POT LEVEL | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
R21 | R21-PIC-001 | R21-P-001 | PCS | 107-EC | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R21 | R21-PIT-001 | R21-P-001 | FLD | 107-EC | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9024303 | 064.0 | PRESSURE | 7030 |  |  | SHE | by request | C |  | I.S | AI |  |  | 11 | C1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
R21 | R21-PI-002 | R21-P-002 | PCS | 107-EC | INDICATOR - PRESSURE |  |  | PRESSURE | PKG: L6694; -: -1 to 2.3barg; -: +/-0.066barg; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R21 | R21-PIT-002 | R21-P-002 | FLD | 107-EC | TRANSMITTER - PRESSURE - DIAPHRAGM | 150-P-PT1A-H-9024303 | 064.0 | PRESSURE | 6694 | -1 to 2.3 barg | +/-0.033 barg | SHE | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R21 | R21-PAH-003 | R21-P-003 | PCS | 107-EC | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R21 | R21-PSH-003 | R21-P-003 | FLD | 107-EC | SWITCH - PRESSURE - DIAPHRAGM - HI | 150-P-PT1A-H-9024303 | 064.0 | HIGH PRESSURE | 6695 | set @ 2.2 barg | +/- 1% | SHE | REQ | C |  | I.S | DI |  |  | 32 | C1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R21 | R21-PI-004 | R21-P-004 | FLD | 107-EC | PRESSURE GAUGE - DIAPHRAGM | 25-N-PT1A-H-9024330 | 064.0 | N2 PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
R21 | R21-PI-007 | R21-P-007 | FLD | 107-EC | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-C-9029509 | 064.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R21 | R21-PI-008 | R21-P-008 | FLD | 107-EC | PRESSURE GAUGE - DIAPHRAGM | 80-HT-CS3A-D-9024325 | 064.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
R21 | R21-PSV-012 | R21-P-012 | FLD | 107-EC | PRESSURE RELIEF VALVE | 25-HT-CS3A-D-9024355 | 064.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R21 | R21-PSV-013 | R21-P-013 | FLD | 107-EC | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9024353 | 064.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R21 | R21-PSV-014 | R21-P-014 | FLD | 107-EC | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9024354 | 064.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R21 | R21-PRV-015 | R21-P-015 | FLD | 107-EC | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9028811 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 3.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1460 | KV0006 |  |  |  | 01
R21 | R21-PI-016 | R21-P-016 | PKG | 107-EC | PRESSURE GAUGE | AGITATOR SEAL POT | 064.0 | AGITATOR SEAL POT PRESSURE | -: 0 to 20 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R21 | R21-SE-001 | R21-S-001 | PKG | 107-EC | ELEMENT - SPEED | AGITATOR SHAFT | 064.0 | AGITATOR |  |  | - | REF | by request | C |  | I.S | DI |  |  | 33 | C1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R21 | R21-SI-001A | R21-S-001 | PCS | 107-EC | INDICATOR - SPEED |  |  | AGITATOR | REF: REF; REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-SI-001B | R21-S-001 | FLD | 107-EC | INDICATOR - SPEED | ADJ TO R21 AGITATOR | 064.0 | AGITATOR | REF: REF; REQ: by request; F: C; I.S: I.S; DI: AO |  |  | 21 | C1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R21 | R21-DS-002 | R21-S-002 | MCC | 107-EC | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R21 | R21-DY-002 | R21-S-002 | MCC | 107-EC | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R21 | R21-DYC-002 | R21-S-002 | MCC | 107-EC | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 064.0 | AGITATOR |  | - |  | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R21 | R21-SC-002 | R21-S-002 | MCC | 107-EC | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 064.0 | AGITATOR | 8850 | 0 to 120 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | C1 |  |  |  |  | SET Min 24 rpm & Max 118 rpm |  | 01
R21 | R21-SIC-002 | R21-S-002 | PCS | 107-EC | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R21 | R21-TE-001 | R21-T-001 | PKG | 107-EC | ELEMENT - TEMPERATURE - RTD | WITH R21-CV-001 |  | TEMPERATURE #1 | PKG: L6931; -: -30 to 170 degC; -: +/-1 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R21 | R21-TI-001A | R21-T-001 | PCS | 107-EC | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | PKG: L6931; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R21 | R21-TI-001B | R21-T-001 | FLD | 107-EC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R21 | 064.0 | TEMPERATURE #1 | REF: SHE; REQ: by request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R21 | R21-TT-001 | R21-T-001 | PKG | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | TEMPERATURE #1 | 6931 | -30 to 170 degC | +/-1 degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R21 | R21-TE-002 | R21-T-002 | PKG | 107-EC | ELEMENT - TEMPERATURE - RTD | WITH R21-CV-001 |  | TEMPERATURE #2 | PKG: L6932; -: -30 to 170 degC; -: +/-1 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R21 | R21-TI-002A | R21-T-002 | PCS | 107-EC | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | PKG: L6932; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R21 | R21-TI-002B | R21-T-002 | FLD | 107-EC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 064.0 | TEMPERATURE #2 | REF: SHE; REQ: by request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R21 | R21-TT-002 | R21-T-002 | PKG | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | TEMPERATURE #2 | 6932 | -30 to 170 degC | +/-1 degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R21 | R21-TE-003 | R21-T-003 | PKG | 107-EC | ELEMENT - TEMPERATURE - RTD | R21/N6/100 |  | BAFFLE TEMPERATURE | PKG: L6933; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R21 | R21-TI-003A | R21-T-003 | PCS | 107-EC | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | PKG: L6933; -: -30 to 170 degC; -: +/-2 degC; REF: GxP/SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R21 | R21-TI-003B | R21-T-003 | FLD | 107-EC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 064.0 | BAFFLE TEMPERATURE | REF: SHE; REQ: by request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R21 | R21-TT-003 | R21-T-003 | PKG | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | BAFFLE TEMPERATURE | 6933 | -30 to 170 degC | +/-1 degC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R21 | R21-TE-004 | R21-T-004 | FLD | 107-EC | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9024325 |  | JACKET INLET TEMP. | REF: SHE; REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-TI-004A | R21-T-004 | PCS | 107-EC | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE; REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-TI-004B | R21-T-004 | FLD | 107-EC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 064.0 | JACKET INLET TEMP. | REF: SHE; REQ: by request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R21 | R21-TT-004 | R21-T-004 | FLD | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | JACKET INLET TEMP. | REF: SHE; REQ: by request; F: C; I.S: I.S; DI: AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R21 | R21-TE-005 | R21-T-005 | FLD | 107-EC | ELEMENT - TEMPERATURE - RTD | 150-P-PT1A-H-9024303 |  | PC1 INLET TEMPERATURE | REF: REF; REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-TI-005 | R21-T-005 | PCS | 107-EC | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R21 | R21-TI-005 | R21-T-005 | [6 empty] | REQ: by request
R21 | R21-TT-005 | R21-T-005 | FLD | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | PC1 INLET TEMPERATURE | REF: REF; REQ: by request; F: C; I.S: I.S; DI: AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R21 | R21-TE-006 | R21-T-006 | FLD | 107-EC | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9024310 |  | VC1 OFF GAS TEMPERATURE | PKG: L6502; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R21 | R21-TI-006A | R21-T-006 | PCS | 107-EC | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | PKG: L6502; -: -20 to 80 degC; -: +/-1 degC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R21 | R21-TI-006B | R21-T-006 | FLD | 107-EC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R21 | 064.0 | VC1 OFF GAS TEMPERATURE | REF: SHE; REQ: by request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R21 | R21-TT-006 | R21-T-006 | FLD | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | VC1 OFF GAS TEMPERATURE | 6502 | -20 to 80 degC | +/-1 degC | SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R21 | R21-TE-007 | R21-T-007 | FLD | 107-EC | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9024317 |  | VC1 HTF RTN TEMPERATURE | REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-TIC-007 | R21-T-007 | PCS | 107-EC | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R21 | R21-TT-007 | R21-T-007 | FLD | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: by request; F: C; I.S: I.S; DI: AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R21 | R21-TE-008 | R21-T-008 | FLD | 107-EC | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-C-9024314 |  | PC1 HTF RTN TEMPERATURE | REF: REF; REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-TIC-008 | R21-T-008 | PCS | 107-EC | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R21 | R21-TT-008 | R21-T-008 | FLD | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | PC1 HTF RTN TEMPERATURE | REF: REF; REQ: by request; F: C; I.S: I.S; DI: AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R21 | R21-TE-009 | R21-T-009 | FLD | 107-EC | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-0-9024302 |  | DISTILLATE RTN TEMP. | REF: REF; REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-TI-009A | R21-T-009 | PCS | 107-EC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R21 | R21-TI-009B | R21-T-009 | FLD | 107-EC | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 064.0 | DISTILLATE RTN TEMP. |  | -20 to 80 degC | +/- 0.5% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5096 |  |  | 01
R21 | R21-TT-009 | R21-T-009 | FLD | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | DISTILLATE RTN TEMP. | REF: REF; REQ: by request; F: C; I.S: I.S; DI: AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5096 |  |  | 01
R21 | R21-TE-010 | R21-T-010 | FLD | 107-EC | ELEMENT - TEMPERATURE - RTD | 80-HT-CS3A-D-9024328 |  | OUTLET TEMPERATURE | REF: REF; REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-TI-010A | R21-T-010 | PCS | 107-EC | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | REF: REF; REQ: by request |  |  | 0 | [7 empty] | 01
R21 | R21-TI-010B | R21-T-010 | FLD | 107-EC | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R21 | 064.0 | OUTLET TEMPERATURE | REF: REF; REQ: by request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R21 | R21-TT-010 | R21-T-010 | FLD | 107-EC | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 064.0 | OUTLET TEMPERATURE | REF: REF; REQ: by request; F: C; I.S: I.S; DI: AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R21 | R21-WE-001A | R21-W-001 | FLD | 107-EC | LOAD CELL - DUMMY | REACTOR R21 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 50kN |  |  |  |  | 01 | bar: PKG
R21 | R21-WE-001B | R21-W-001 | FLD | 107-EC | LOAD CELL - DUMMY | REACTOR R21 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 50kN |  |  |  |  | 01 | bar: PKG
R21 | R21-WE-001C | R21-W-001 | FLD | 107-EC | LOAD CELL - DUMMY | REACTOR R21 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 50kN |  |  |  |  | 01 | bar: PKG
R21 | R21-YA-001 | R21-Y-001 | PCS | 107-EC | ALARM - COMMON |  |  | AGITATOR SEAL COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R21 | R21-YS-001 | R21-Y-001 | FUT | 107-EC | COMMON ALARM | R21 GAS SEAL ASSEMBLY | 064.0 | AGITATOR SEAL COMMON ALARM | PKG: 8871; -: -; -: -; I.S: I.S; DI: DI |  |  | 32 | C1 | N/A | N/A |  | TI702-SP-5097 | FUTURE(PCS I/O INSTALLED) |  | 01
R22 | R22-AG-001 | R22-A-001 | PKG | 107-ED | SPEED MOORE DISPLAY |  | 065.0 | AGITATOR | REF: REF; REQ: REQ | [10 empty] | 34
R22 | R22-BD-001 | R22-B-001 | FLD | 107-ED | RUPTURE DISC | 100-P-HS1A-H-9024403 | 065.0 | BURSTING DISC | 6752 | 5.7 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | C1 | BS&B | LCN / BAS + | KS0003/P5 | TI702-SP-5077 |  |  | 01
R22 | R22-YI-001 | R22-B-001 | PCS | 107-ED | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-CV-001 | R22-C-001 | PKG | 107-ED | BOTTOM OUTLET VALVE - ON/OFF - F.C. | 50-P-PT1A-H-9024420 | 065.0 | BOTTOM OUTLET VALVE | 8851 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R22 | R22-CY-001 | R22-C-001 | PKG | 107-ED | SOLENOID VALVE | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DO |  |  | 41 | C1 | RGS | EP000/ia |  | TI702-SP-5133 |  |  | 01
R22 | R22-ZSC-001 | R22-C-001 | PKG | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R22 | R22-ZSO-001 | R22-C-001 | PKG | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | BOTTOM OUTLET VALVE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5002 |  |  | 01
R22 | R22-CV-004 | R22-C-004 | FLD | 107-ED | V-BALL VALVE - CONTROL - F.C. | 25-N-HS1A-D-9024430 | 065.0 | NITROGEN SUPPLY | 6797 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R22 | R22-CV-006 | R22-C-006 | FLD | 107-ED | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024410 | 065.0 | SCRUBBER 02 | 7228 | - | - | GxP | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R22 | R22-CY-006 | R22-C-006 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-006 | R22-C-006 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-006 | R22-C-006 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SCRUBBER 02 | REF: GxP; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-008 | R22-C-008 | FLD | 107-ED | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9024437 | 065.0 | HOUSE VACUUM | 7329 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R22 | R22-CY-008 | R22-C-008 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED |  | HOUSE VACUUM | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-008 | R22-C-008 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-008 | R22-C-008 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOUSE VACUUM | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-009 | R22-C-009 | FLD | 107-ED | BALL VALVE - ON/OFF - F.O. | 80-HT-SS3A-D-9024471 | 065.0 | COLD HTF SUPPLY | 7113 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R22 | R22-CY-009 | R22-C-009 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-009 | R22-C-009 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-009 | R22-C-009 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COLD HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-010 | R22-C-010 | FLD | 107-ED | BALL VALVE - ON/OFF - F.C. | 80-HT-SS3A-D-9024470 | 065.0 | HOT HTF SUPPLY | 7112 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R22 | R22-ZSC-010 | R22-C-010 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-010 | R22-C-010 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF SUPPLY | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-011 | R22-C-011 | FLD | 107-ED | GLOBE VALVE - CONTROL - F.C. | 80-HT-SS3A-C-9024458 | 065.0 | HOT HTF RTN | 6371 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R22 | R22-CY-011 | R22-C-011 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED |  | HOT HTF RTN | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-011 | R22-C-011 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | HOT HTF RTN | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-011 | R22-C-011 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | HOT HTF RTN | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-012 | R22-C-012 | FLD | 107-ED | GLOBE VALVE - CONTROL - STAYPUT | 80-HT-SS3A-D-9024473 | 065.0 | COLD HTF RTN | 6372 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5008 |  |  | 01
R22 | R22-CV-013 | R22-C-013 | FLD | 107-ED | BALL VALVE - ON/OFF - F.O. | 50-HT-SS3A-C-9024425 | 065.0 | DUAL JACKET | 7111 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R22 | R22-CY-013 | R22-C-013 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED |  | DUAL JACKET | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-013 | R22-C-013 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-013 | R22-C-013 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DUAL JACKET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-014 | R22-C-014 | FLD | 107-ED | BALL VALVE - ON/OFF - F.C. | 25-N-HS1A-0-9024459 | 065.0 | N2 TO BOTTOM OUTLET | 7108 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R22 | R22-CY-014 | R22-C-014 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-014 | R22-C-014 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-014 | R22-C-014 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 TO BOTTOM OUTLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-015 | R22-C-015 | FLD | 107-ED | GLOBE VALVE - CONTROL - STAYPUT | 50-HT-CS3A-C-9024414 | 065.0 | PC1 TEMPERED HTF RTN | 6421 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R22 | R22-CV-016 | R22-C-016 | FLD | 107-ED | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9024417 | 065.0 | VC1 COLD HTF RTN | 6428 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 241-7 / 3767-1 POSITIONER | KV0001 | TI702-SP-5007 |  |  | 01
R22 | R22-CV-018 | R22-C-018 | FLD | 107-ED | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9024405 | 065.0 | DISTILLATE VENT LINE | 7280 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R22 | R22-CY-018 | R22-C-018 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED |  | DISTILLATE VENT LINE | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-018 | R22-C-018 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-018 | R22-C-018 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DISTILLATE VENT LINE | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-019 | R22-C-019 | FLD | 107-ED | BALL VALVE - ON/OFF - F.C. | 40-P-HS1A-D-9024411 | 065.0 | LIQUID INLET | 7109 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R22 | R22-CY-019 | R22-C-019 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-019 | R22-C-019 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-019 | R22-C-019 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | LIQUID INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-021 | R22-C-021 | FLD | 107-ED | V-BALL VALVE - CONTROL - F.C. | 50-P-PT1A-0-9024410 | 065.0 | +VE PRESSURE CONTROL | 6845 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R22 | R22-CV-022 | R22-C-022 | FLD | 107-ED | V-BALL VALVE - CONTROL - F.C. | 50-VP-PT1A-0-9024437 | 065.0 | -VE PRESSURE CONTROL | 6849 | 0 T0 100% | - |  | REQ | F |  | I.S | AO |  |  | 21 | C1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5008 |  |  | 01
R22 | R22-CV-024 | R22-C-024 | FLD | 107-ED | BALL VALVE - ON/OFF - F.C. | 100-P-HS1A-0-9024469 | 065.0 | SOLIDS INLET | 7358 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  |  |  | KV0017 |  |  |  | 01
R22 | R22-CX-024 | R22-C-024 | SGS | 107-ED | VALVE INTERLOCK FUNCTION |  |  | SOLIDS INLET | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | C1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R22 | R22-CY-024 | R22-C-024 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED | 065.0 | SOLIDS INLET |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-024 | R22-C-024 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-024 | R22-C-024 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLIDS INLET | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-025 | R22-C-025 | FLD | 107-ED | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9024410 | 065.0 | SOLIDS ADDITION VENT | 7306 | - | - | SHE | 12 | F | SIL |  |  |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R22 | R22-CX-025 | R22-C-025 | SGS | 107-ED | VALVE INTERLOCK FUNCTION |  |  | SOLIDS ADDITION VENT | REF: SHE; I.S: N.I.S; DI: DO |  |  | 42 | C1 |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R22 | R22-CY-025 | R22-C-025 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED | 065.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-025 | R22-C-025 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLIDS ADDITION VENT | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-025 | R22-C-025 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 065.0 | SOLIDS ADDITION VENT |  | - | - | SHE | 12 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-CV-028 | R22-C-028 | PKG | 107-ED | GLOBE VALVE - CONTROL - STAYPUT | R22-CC1 | 043.5 | CC1 LOW TEMP. N2 VENT | 8852 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | C1 | SAMSON | 3730-2 POSITIONER |  | TI702-SP-5008 |  |  | 01
R22 | R22-CV-029 | R22-C-029 | PKG | 107-ED | BALL VALVE - ON/OFF - F.C. | R22-CC1 | 043.5 | CC1 LIQUID N2 SUPPLY | 8853 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R22 | R22-CY-029 | R22-C-029 | FLD | 107-ED | SOLENOID VALVE | RACK MOUNTED |  | CC1 LIQUID N2 SUPPLY | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
R22 | R22-ZSC-029 | R22-C-029 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CC1 LIQUID N2 SUPPLY | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-ZSO-029 | R22-C-029 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CC1 LIQUID N2 SUPPLY | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-DIC-001 | R22-D-001 | PCS | 107-ED | INDICATING CONTR. - MOTOR DRIVE |  |  | JACKET PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-DS-001 | R22-D-001 | MCC | 107-ED | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R22 | R22-DY-001 | R22-D-001 | MCC | 107-ED | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | JACKET PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R22 | R22-DYC-001 | R22-D-001 | MCC | 107-ED | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 065.0 | JACKET PUMP | 8854 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R22 | R22-DIC-003 | R22-D-003 | PCS | 107-ED | INDICATING CONTR. - MOTOR DRIVE |  |  | R23-SS1 PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-DS-003 | R22-D-003 | MCC | 107-ED | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | R23-SS1 PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R22 | R22-DY-003 | R22-D-003 | MCC | 107-ED | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | R23-SS1 PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R22 | R22-DYC-003 | R22-D-003 | MCC | 107-ED | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 065.0 | R23-SS1 PUMP | 11133 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R22 | R22-DIC-004 | R22-D-004 | PCS | 107-ED | INDICATING CONTR. - MOTOR DRIVE |  |  | R23-SS1 HEATER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-DS-004 | R22-D-004 | MCC | 107-ED | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | R23-SS1 HEATER | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R22 | R22-DY-004 | R22-D-004 | MCC | 107-ED | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | R23-SS1 HEATER | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R22 | R22-DYC-004 | R22-D-004 | MCC | 107-ED | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 065.0 | R23-SS1 HEATER | 11134 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R22 | R22-FI-002 | R22-F-002 | PCS | 107-ED | INDICATOR - FLOW |  |  | HTF TO JACKET | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-FT-002 | R22-F-002 | PKG | 107-ED | TRANSMITTER - FLOW | R22-CC1 | 043.5 | HTF TO JACKET | 8856 | 0 to 24 m3/hr | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | ROSEMOUNT | 1151 |  | TI702-SP-5042 |  |  | 01
R22 | R22-FIAL-003 | R22-F-003 | FLD | 107-ED | FLOW INDICATOR - ALARM LOW | R22 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LOW FLOW ALARM | REQ: By request | [10 empty] | 52
R22 | R22-FISL-003 | R22-F-003 | FLD | 107-ED | FLOW INDICATOR - SWITCH LOW | R22 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LOW FLOW ALARM |  | 0 to 1 Nl/min N2 |  | REF | By request | C |  | I.S | DI |  |  | 0 | C1 | KROHNE / PEPPERL + FUCHS | DK 800 / RC15-14-N3 |  | TI702-SP-5088 | LOW RANGE FLOW |  | 52
R22 | R22-FIAH-004 | R22-F-004 | PCS | 107-ED | FLOW INDICATOR - ALARM HIGH | R22 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL HIGH FLOW ALARM | REQ: By request | [10 empty] | 52
R22 | R22-FISH-004 | R22-F-004 | FLD | 107-ED | FLOW INDICATOR - SWITCH HIGH | R22 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL HIGH FLOW ALARM |  | 1 to 10 Nl/min N2 |  | REF | By request | C |  | I.S | DI |  |  | 0 | C1 | KROHNE / PEPPERL + FUCHS | DK 800 / RC10-14-N3 |  | TI702-SP-5087 | HIGH RANGE FLOW |  | 52
R22 | R22-HS-002 | R22-H-002 | FLD | 107-ED | SWITCH - HAND OP. | ADJ TO R22 | 065.0 | CRASH COOL | 7005 | - | - | GxP | 6 | F | SOP | I.S | DI |  |  | 32 | C1 | TELEMECANIQUE | ZB2-BE102 | KB0003 | TI702-SP-5051 |  |  | 01
R22 | R22-HV-008 | R22-H-008 | FLD | 107-ED | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028826 | 065.0 | N2 PRESSURE SELECT | 8138 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R22 | R22-HZSC-008 | R22-H-008 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | N2 PRESSURE SELECT | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R22 | R22-HZSO-008 | R22-H-008 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | N2 PRESSURE SELECT | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 | 0.8 BARG N2 LINE OPEN |  | 01
R22 | R22-HV-009 | R22-H-009 | FLD | 107-ED | HAND VALVE | 25-P-PT1A-0-9024462 | 065.0 | AUX. INLET | 7418 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R22 | R22-HZSC-009 | R22-H-009 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | AUX. INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-HZSO-009 | R22-H-009 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | AUX. INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R22 | R22-HV-010 | R22-H-010 | FLD | 107-ED | HAND VALVE | 40-P-PT1A-0-9024861 | 065.0 | REAGENTS INLET | 8141 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R22 | R22-HZSC-010 | R22-H-010 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-HZSO-010 | R22-H-010 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | REAGENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-HV-012 | R22-H-012 | FLD | 107-ED | HAND VALVE | 25-P-PT1A-0-9024860 | 065.0 | SOLVENTS INLET | 7419 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R22 | R22-HZSC-012 | R22-H-012 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLVENTS INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-HZSO-012 | R22-H-012 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLVENTS INLET | [11 empty] | 0 | C1 |  |  |  |  | INSTALLED SPARE |  | 01 | bar: PKG
R22 | R22-HV-013 | R22-H-013 | FLD | 107-ED | HAND VALVE | 40-P-PT1A-0-9024861 | 065.0 | SLURRIES INLET | 7459 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R22 | R22-HZSC-013 | R22-H-013 | FLD | 107-ED | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-HZSO-013 | R22-H-013 | FLD | 107-ED | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SLURRIES INLET | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
R22 | R22-II-002 | R22-I-002 | PCS | 107-ED | INDICATOR - CURRENT |  |  | AGITATOR CURRENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-IT-002 | R22-I-002 | MCC | 107-ED | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 065.0 | AGITATOR CURRENT | 8858 | 0 to 5 amp | +/- 1% | REF | REQ | C |  | N.I.S | AI |  |  | 13 | C1 | [6 empty] | 01
R22 | R22-LAH-001 | R22-L-001 | PCS | 107-ED | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-LE-001 | R22-L-001 | FLD | 107-ED | ELEMENT - LEVEL | 100-P-HS1A-D-9024403 | 065.0 | HIGH LEVEL |  | Fixed | - | SHE | 12 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R22 | R22-LSH-001 | R22-L-001 | CPR | 107-ED | SWITCH - LEVEL - HIGH | 100-P-HS1A-D-9024403 | 065.0 | HIGH LEVEL | 6637 | - | - | SHE | 12 | F |  | N.I.S | DI |  |  | 35 | C1 | ENDRESS + HAUSER | FDL-GYY9AC70 | KL0014 |  |  |  | 01
R22 | R22-LI-022 | R22-L-022 | PKG | 107-ED | LEVEL GAUGE | R22-SS1 | 065.0 | R22-SS1 LEVEL | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
R22 | R22-PIC-001 | R22-P-001 | PCS | 107-ED | INDICATING CONTROLLER - PRESSURE |  |  | PRESSURE | REF: SHE; REQ: REQ |  |  | 0 | [7 empty] | 33
R22 | R22-PIT-001 | R22-P-001 | FLD | 107-ED | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9024403 | 065.0 | PRESSURE | 7031 | -1 to 6.0 barg | +/- 1% | SHE | REQ | C |  | I.S | AI |  |  | 11 | C1 | ROSEMOUNT | 3051S | KP0001/P1 | TI702-SP-5041 |  |  | 30
R22 | R22-PI-002 | R22-P-002 | PCS | 107-ED | INDICATOR - PRESSURE |  |  | PRESSURE | -: -1 to 2.3barg; -: +/-0.066barg; REF: SIL; REQ: 24 |  |  | 0 | [7 empty] | 01
R22 | R22-PIT-002 | R22-P-002 | FLD | 107-ED | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-P-PT1A-H-9024403 | 065.0 | PRESSURE | 6697 | -1 to 6.0 barg | +/- 1% | SIL | 12 | C | SIL | I.S |  | AI |  | 11 | SIS | ROSEMOUNT | 3051S | KP0001 | TI702-SP-5013 |  |  | 01
R22 | R22-PAH-003 | R22-P-003 | PCS | 107-ED | ALARM - PRESSURE - HIGH |  |  | HIGH PRESSURE | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-PSH-003 | R22-P-003 | FLD | 107-ED | SWITCH - PRESSURE - DIAPHRAGM - HI | 100-P-HS1A-0-9024403 | 065.0 | HIGH PRESSURE | 6698 | set @ 4.8 barg | +/- 1% | SHE | REQ | C |  | I.S | DI |  |  | 32 | C1 | DELTA CONTROLS LTD | WS210GDEH2X300AMK | KP0012 | TI702-SP-5070 |  |  | 01
R22 | R22-PI-004 | R22-P-004 | FLD | 107-ED | PRESSURE GAUGE - DIAPHRAGM | 25-N-HS1A-0-9024430 | 065.0 | N2 PRESSURE | -: - 1 to 9 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | NORTHDOWNS INST |  | KP0006/P8 |  |  |  | 01
R22 | R22-PI-007 | R22-P-007 | FLD | 107-ED | PRESSURE GAUGE - DIAPHRAGM | 80-HT-SS3A-C-9024470 | 065.0 | JP1 SUCTION PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/4 |  |  |  | 01
R22 | R22-PI-008 | R22-P-008 | FLD | 107-ED | PRESSURE GAUGE - DIAPHRAGM | 80-HT-SS3A-C-9024475 | 065.0 | JP1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/4 |  |  |  | 01
R22 | R22-PSV-012 | R22-P-012 | FLD | 107-ED | PRESSURE RELIEF VALVE | 25-HT-SS3A-C-9024455 | 065.0 | JACKET HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-S-B000 | KS0001 |  |  |  | 01
R22 | R22-PSV-013 | R22-P-013 | FLD | 107-ED | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9024453 | 065.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R22 | R22-PSV-014 | R22-P-014 | FLD | 107-ED | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9024454 | 065.0 | PC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R22 | R22-PSV-016 | R22-P-016 | PKG | 107-ED | PRESSURE RELIEF VALVE | 50-N-SS3A-C-9024466 | 043.5 | CC1 N2 VENT RELIEF | -: 17 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
R22 | R22-PSV-017 | R22-P-017 | PKG | 107-ED | PRESSURE RELIEF VALVE | R22-CC1 | 043.5 | CC1 LIQUID N2 RELIEF | -: 17 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
R22 | R22-PSV-018 | R22-P-018 | PKG | 107-ED | PRESSURE RELIEF VALVE | R22-CC1 | 043.5 | CC1 LIQUID N2 RELIEF | -: 17 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
R22 | R22-PSV-019 | R22-P-019 | FLD | 107-ED | PRESSURE RELIEF VALVE | 25-HT-SS3A-C-9024463 | 065.0 | CC1 RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-S-B000 | KS0001 |  |  |  | 01
R22 | R22-PRV-020 | R22-P-020 | DEL | 107-ED | CONTROL VALVE SELF ACTUATING | DELETED |  | DELETED | [11 empty] | 0 |  | ESME | R1460 | KV0006 |  | DELETED |  | 01
R22 | R22-PI-022 | R22-P-022 | DEL | 107-ED | PRESSURE GAUGE | DELETED |  | SEAL SUPPLY PRESSURE | [11 empty] | 0 | [5 empty] | DELETED |  | 01
R22 | R22-PI-023 | R22-P-023 | PKG | 107-ED | PRESSURE GAUGE | R22-SS1 | 065.0 | SEAL RETURN PRESSURE | -: 0 to 11 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R22 | R22-PRV-025 | R22-P-025 | PKG | 107-ED | CONTROL VALVE SELF ACTUATING | R22-SS1 | 065.0 | SEAL RETURN | -: 6.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R22 | R22-PSV-026 | R22-P-026 | PKG | 107-ED | PRESSURE RELIEF VALVE | R22-SS1 | 065.0 | R22-SS1 RELIEF | -: 10.0 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
R22 | R22-PRV-027 | R22-P-027 | FLD | 107-ED | CONTROL VALVE SELF ACTUATING | 15-N-SS3T-0-9024485 | 043.2 | N2 TO AGITATOR SEAL CONTROL PANEL | -: set @ 9.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | C1 | BURGMANN | Part of gas seal system |  |  |  |  | 52
R22 | R22-PRV-028 | R22-P-028 | FLD | 107-ED | CONTROL VALVE SELF ACTUATING | 25-CA-SS1U-0-9024483 | 042.0 | CA TO AGITATOR SEAL GAS BOOSTER | -: set @ 5.0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | C1 | BURGMANN | Part of gas seal system |  |  |  |  | 52
R22 | R22-PI-029 | R22-P-029 | FLD | 107-ED | PRESSURE GAUGE | R22 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL RECEIVER PRESSURE | -: SET @5BARG; REF: REF; REQ: By request; F: C |  |  | 0 | C1 | BURGMANN | Part of gas seal system |  |  |  |  | 52
R22 | R22-PIAL-030 | R22-P-030 | PCS | 107-ED | PRESSURE GAUGE - ALARM LOW | R22 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LP ALARM | -: SET @8BARG; REQ: By request; F: C |  |  |  | C1 | BURGMANN | Part of gas seal system |  |  |  |  | 52
R22 | R22-PISL-030 | R22-P-030 | FLD | 107-ED | PRESSURE GAUGE - SWITCH LOW | R22 GAS SEAL ASSEMBLY | 043.2 | AGITATOR SEAL LP ALARM |  | SET @8BARG |  | REF | By request | C |  | I.S | DI |  |  | 0 | C1 | PEPPERL + FUCHS | SJ2-N |  | TI702-SP-5099 |  |  | 52
R22 | R22-PRV-031 | R22-P-031 | FLD | 107-ED | CONTROL VALVE SELF ACTUATING | 15-N-SS3T-0-9024485 | 043.2 | N2 TO AGITATOR SEAL | -: set @ 8.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | C1 | BURGMANN | Part of gas seal system |  |  |  |  | 52
R22 | R22-RO-001 | R22-R-001 | DEL | 107-ED | RESTRICTION ORIFICE PLATE | DELETED |  | DELETED | [11 empty] | 0 | [5 empty] | DELETED |  | 01 | bar: -
R22 | R22-SE-001 | R22-S-001 | PKG | 107-ED | ELEMENT - SPEED | AGITATOR SHAFT | 065.0 | AGITATOR | 6935 | 0 to 215 rpm | - | REF | REQ | C |  | I.S | DI |  |  | 33 | C1 | PEPPERL + FUCHS | NCB8-18GM40-N0 |  | TI702-SP-5095 | 8 PULSE per REV |  | 34
R22 | R22-SI-001A | R22-S-001 | PCS | 107-ED | INDICATOR - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-SI-001B | R22-S-001 | FLD | 107-ED | INDICATOR - SPEED | ADJ TO R22 AGITATOR | 065.0 | AGITATOR |  | 0 to 220 rpm | +/- 1% | REF | REQ | C |  | I.S | AO |  |  | 21 | C1 | BEKA | BA324C-GRP | KX0017 | TI702-SP-5086 |  |  | 34
R22 | R22-DS-002 | R22-S-002 | MCC | 107-ED | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R22 | R22-DY-002 | R22-S-002 | MCC | 107-ED | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
R22 | R22-DYC-002 | R22-S-002 | MCC | 107-ED | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 065.0 | AGITATOR |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
R22 | R22-SC-002 | R22-S-002 | MCC | 107-ED | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 065.0 | AGITATOR | 8858 | 0 to 220 rpm | +/- 1% | REF | REQ | C |  | N.I.S | AO |  |  | 22 | C1 |  |  |  |  | SET Min 43 rpm & Max 215 rpm |  | 01
R22 | R22-SIC-002 | R22-S-002 | PCS | 107-ED | INDICATING CONTROLLER - SPEED |  |  | AGITATOR | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TE-001 | R22-T-001 | PKG | 107-ED | ELEMENT - TEMPERATURE - RTD | WITH R22-CV-001 |  | TEMPERATURE #1 | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-001A | R22-T-001 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #1 | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-001B | R22-T-001 | FLD | 107-ED | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R22 | 065.0 | TEMPERATURE #1 |  | -100 to 170degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R22 | R22-TT-001 | R22-T-001 | PKG | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | TEMPERATURE #1 | 6936 | -100 to 170degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R22 | R22-TE-002 | R22-T-002 | PKG | 107-ED | ELEMENT - TEMPERATURE - RTD | WITH R22-CV-001 |  | TEMPERATURE #2 | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-002A | R22-T-002 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | TEMPERATURE #2 | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-002B | R22-T-002 | FLD | 107-ED | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 065.0 | TEMPERATURE #2 |  | -100 to 170degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5038 |  |  | 34
R22 | R22-TT-002 | R22-T-002 | PKG | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | TEMPERATURE #2 | 6937 | -100 to 170degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | INOR | IPAQ-HX |  | TI702-SP-5038 |  |  | 01
R22 | R22-TE-003 | R22-T-003 | PKG | 107-ED | ELEMENT - TEMPERATURE - RTD | R22/N2/100 |  | BAFFLE TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-003A | R22-T-003 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | BAFFLE TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-003B | R22-T-003 | FLD | 107-ED | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 065.0 | BAFFLE TEMPERATURE |  | -100 to 170degC | +/- 0.5% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5011 |  |  | 34
R22 | R22-TT-003 | R22-T-003 | PKG | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | BAFFLE TEMPERATURE | 6938 | -100 to 170degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | ROSEMOUNT | 144H |  | TI702-SP-5011 |  |  | 01
R22 | R22-TE-004 | R22-T-004 | FLD | 107-ED | ELEMENT - TEMPERATURE - RTD | 80-HT-SS3A-C-9024425 |  | JACKET INLET TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-004A | R22-T-004 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | JACKET INLET TEMP. | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-004B | R22-T-004 | FLD | 107-ED | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 065.0 | JACKET INLET TEMP. |  | -100 to 170degC | +/- 1% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R22 | R22-TT-004 | R22-T-004 | FLD | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | JACKET INLET TEMP. | 6939 | -100 to 170degC | +/- 1% | SHE | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R22 | R22-TE-005 | R22-T-005 | FLD | 107-ED | ELEMENT - TEMPERATURE - RTD | 100-P-****-0-9024403 |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TI-005 | R22-T-005 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | PC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TT-005 | R22-T-005 | FLD | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | PC1 INLET TEMPERATURE | 6507 | -20 to 180 degC | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R22 | R22-TE-006 | R22-T-006 | FLD | 107-ED | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9024410 |  | VC1 OFF GAS TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-006A | R22-T-006 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | VC1 OFF GAS TEMPERATURE | REF: SHE |  |  | 0 | [7 empty] | 01
R22 | R22-TI-006B | R22-T-006 | FLD | 107-ED | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R22 | 065.0 | VC1 OFF GAS TEMPERATURE |  | -20 to 80 degC | +/- 1% | SHE | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R22 | R22-TT-006 | R22-T-006 | FLD | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | VC1 OFF GAS TEMPERATURE | 6508 | -20 to 80 degC | +/- 1% | SHE | 6 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R22 | R22-TE-007 | R22-T-007 | FLD | 107-ED | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9024417 |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TIC-007 | R22-T-007 | PCS | 107-ED | INDICATING CONTROLLER - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TT-007 | R22-T-007 | FLD | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | VC1 HTF RTN TEMPERATURE | 6509 | -30 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R22 | R22-TE-008 | R22-T-008 | FLD | 107-ED | ELEMENT - TEMPERATURE - RTD | 50-HT-CS3A-C-9024414 |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TIC-008 | R22-T-008 | PCS | 107-ED | INDICATING CONTROLLER - TEMPERATURE |  |  | PC1 HTF RTN TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TT-008 | R22-T-008 | FLD | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | PC1 HTF RTN TEMPERATURE | 6510 | -20 to 70 degC | +/- 1% | REF | REQ | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R22 | R22-TE-009 | R22-T-009 | FLD | 107-ED | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023402 |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TI-009A | R22-T-009 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | DISTILLATE RTN TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TI-009B | R22-T-009 | FLD | 107-ED | INDICATOR - TEMPERATURE | ADJ TO TT - VISIBLE | 065.0 | DISTILLATE RTN TEMP. |  | -20 to 80 degC | +/- 0.5% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R22 | R22-TT-009 | R22-T-009 | FLD | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | DISTILLATE RTN TEMP. | 6511 | -20 to 80 degC | +/- 0.5% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R22 | R22-TE-010 | R22-T-010 | FLD | 107-ED | ELEMENT - TEMPERATURE - RTD | 80-HT-SS3A-C-9024428 |  | OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TI-010A | R22-T-010 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | OUTLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TI-010B | R22-T-010 | FLD | 107-ED | INDICATOR - TEMPERATURE | 2ND FLOOR ADJ TO R22 | 065.0 | OUTLET TEMPERATURE |  | -100 to 170 deg | +/- 1% | REF | REQ | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5073 |  |  | 34
R22 | R22-TT-010 | R22-T-010 | FLD | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | OUTLET TEMPERATURE | 6512 | -100 to 170 deg | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5073 |  |  | 01
R22 | R22-TE-011 | R22-T-011 | FLD | 107-ED | ELEMENT - TEMPERATURE - RTD | 80-HT-SS3A-0-9024475 |  | CC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TI-011 | R22-T-011 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | CC1 INLET TEMPERATURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TT-011 | R22-T-011 | FLD | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 065.0 | CC1 INLET TEMPERATURE | 8158 | -100 to 170 deg | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
R22 | R22-TE-012 | R22-T-012 | PKG | 107-ED | ELEMENT - TEMPERATURE - RTD | 50-N-SS3A-C-9024466 |  | CC1 LOW TEMP. VENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TI-012 | R22-T-012 | PCS | 107-ED | INDICATOR - TEMPERATURE |  |  | CC1 LOW TEMP. VENT | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-TT-012 | R22-T-012 | PKG | 107-ED | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 043.5 | CC1 LOW TEMP. VENT | 8859 | -200 to 50 degC | +/- 1% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | MOORE INDUSTRIES | TRX/PRG / DM400X |  | TI702-SP-5040 |  |  | 01
R22 | R22-TI-013 | R22-T-013 | DEL | 107-ED | INDICATOR - TEMPERATURE | DELETED |  | R22-SS1 TEMPERATURE | -: 0 to 80 degC |  |  | 0 | [7 empty] | 01
R22 | R22-TC-014 | R22-T-014 | PKG | 107-ED | CONTROLLER - TEMPERATURE | R22-SS1 | 065.0 | R22-SS1 TEMP CONTROL | -: set @ 10 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R22 | R22-WE-001A | R22-W-001 | FLD | 107-ED | LOAD CELL - DUMMY | REACTOR R22 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 10kN |  |  |  |  | 01 | bar: PKG
R22 | R22-WE-001B | R22-W-001 | FLD | 107-ED | LOAD CELL - DUMMY | REACTOR R22 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 10kN |  |  |  |  | 01 | bar: PKG
R22 | R22-WE-001C | R22-W-001 | FLD | 107-ED | LOAD CELL - DUMMY | REACTOR R22 |  | WEIGHT(FUTURE) | [11 empty] | 0 |  | NOBEL | KIS 10kN |  |  |  |  | 01 | bar: PKG
R22 | R22-LSL-003 | R22-Y-001 | PKG | 107-ED | SWITCH - LEVEL - LOW | R22-SS1 | 065.0 | SEAL SYST COMMON ALARM |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R22 | R22-PSL-024 | R22-Y-001 | PKG | 107-ED | SWITCH - PRESSURE - LOW | R22-SS1 | 065.0 | SEAL SYST COMMON ALARM |  | set @ 5 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | [7 empty] | 01
R22 | R22-YA-001 | R22-Y-001 | PCS | 107-ED | ALARM - COMMON |  |  | SEAL SYST COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R22 | R22-YS-001 | R22-Y-001 | PKG | 107-ED | ALARM - COMMON | R22-SS1 | 065.0 | SEAL SYST COMMON ALARM | 8828 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | C1 | TAV ENGINEERING LTD / ROTOTHERM HNL | F71 / 300 SERIES |  | TI702-SP-5157 |  |  | 01
R23 | R23-AE-001A | R23-A-001A | FLD | 107-FA | ELEMENT - H2 DETECTOR | HYDROGENATOR ROOM | 066.0 | H2 LEAK HYDROG ROOM VENT | 8100 | 0 to 50% LEL | +/- 5% | SHE | 6 | C |  | I.S |  |  |  | 0 | [7 empty] | 01
R23 | R23-AI-001A | R23-A-001A | PCS | 107-FA | ELEMENT- H2 INDICATOR | PCS | 066.0 | H2 LEAK HYDROG ROOM VENT | PKG: 8100; -: 0 to 50% LEL; -: +/- 5%; REF: SHE; REQ: 6
R23 | R23-AT-001A | R23-A-001A | CPR | 107-FA | TRANSMITTER - H2 %LEL | MISC EQUIP. PANEL | 066.0 | H2 LEAK HYDROG ROOM VENT | 8100 | 0 to 50% LEL | +/- 5% | SHE | 6 | C |  | N.I.S |  | AI |  | 12 | SGS |  |  | KA0045 |  |  |  | 01
R23 | R23-AE-001B | R23-A-001B | FLD | 107-FA | ELEMENT - H2 DETECTOR | HYDROGENATOR ROOM | 066.0 | H2 LEAK HYDROG ROOM VENT | 6354 | 0 to 50% LEL | +/- 5% | SHE | 6 | C |  | I.S |  |  |  | 0 | [7 empty] | 01
R23 | R23-AI-001B | R23-A-001B | PCS | 107-FA | ELEMENT- H2 INDICATOR | PCS | 066.0 | H2 LEAK HYDROG ROOM VENT | PKG: 6354; -: 0 to 50% LEL; -: +/- 5%; REF: SHE; REQ: 6
R23 | R23-AT-001B | R23-A-001B | CPR | 107-FA | TRANSMITTER - H2 %LEL | MISC EQUIP. PANEL | 066.0 | H2 LEAK HYDROG ROOM VENT | 6354 | 0 to 50% LEL | +/- 5% | SHE | 6 | C |  | N.I.S |  | AI |  | 12 | SGS |  |  | KA0045 |  |  |  | 01
R23 | R23-AE-001C | R23-A-001C | FLD | 107-FA | ELEMENT - H2 DETECTOR | HYDROGENATOR ROOM | 066.0 | H2 LEAK HYDROG ROOM VENT | 6355 | 0 to 50% LEL | +/- 5% | SHE | 6 | C |  | I.S |  |  |  | 0 | [7 empty] | 01
R23 | R23-AI-001C | R23-A-001C | PCS | 107-FA | ELEMENT- H2 INDICATOR | PCS | 066.0 | H2 LEAK HYDROG ROOM VENT | PKG: 6355; -: 0 to 50% LEL; -: +/- 5%; REF: SHE; REQ: 6
R23 | R23-AT-001C | R23-A-001C | CPR | 107-FA | TRANSMITTER - H2 %LEL | MISC EQUIP. PANEL | 066.0 | H2 LEAK HYDROG ROOM VENT | 6355 | 0 to 50% LEL | +/- 5% | SHE | 6 | C |  | N.I.S |  | AI |  | 12 | SGS |  |  | KA0045 |  |  |  | 01
R23 | R23-BD-001 | R23-B-001 | FLD | 107-FA | RUPTURE DISC | 80-P-HS3A-H-9025130 | 066.0 | BURSTING DISC TO CT02 | 6753 | Set @ 20.0 barg | - |  | REQ | F |  | I.S | DI |  |  | 32 | HYD | BS&B | S-90 / BAS + | KS0003 | TI702-SP-5091 |  |  | 01
R23 | R23-YI-001 | R23-B-001 | PCS | 107-FA | ALARM - RUPTURE DISC FAIL | PCS | 066.0 | BURSTING DISC TO CT02 | PKG: 6753; -: -; -: -; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-BD-002 | R23-B-002 | FLD | 107-FA | RUPTURE DISC | 40-H-PT1A-0-9025178 | 066.0 | BURSTING DISC | 6760 | Set @ 6.0 barg | - |  | REQ | F |  | I.S | DI |  |  | 32 | HYD | BS&B | LCN / BAS + | KS0003 | TI702-SP-5091 |  |  | 01
R23 | R23-YI-002 | R23-B-002 | PCS | 107-FA | ALARM - RUPTURE DISC FAIL | PCS | 066.0 | BURSTING DISC | PKG: 6760; -: -; -: -; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-CV-001 | R23-C-001 | PKG | 107-FB | BALL VALVE - ON/OFF - F.C. | 15-N-SS3T-0-9025167 | 066.0 | N2 PURGE SUPPLY | 8860 | - | - |  | 6 | F | SIL |  |  |  |  | 0 | [7 empty] | 01
R23 | R23-CX-001 | R23-C-001 | SGS | 107-FB | VALVE INTERLOCK FUNCTION | SGS | 066.0 | N2 PURGE SUPPLY | 8860 | - | - |  | 6 |  |  | N.I.S | DO |  |  | 42 | HYD |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R23 | R23-CY-001 | R23-C-001 | FLD | 107-FB | SOLENOID VALVE | RACK MOUNTED | 066.0 | N2 PURGE SUPPLY | 8860 | - | - |  | 6 | F | SIL | I.S |  | DO |  | 41 | SIS | RGS | EP000/ia |  | TI702-SP-5102 |  |  | 01
R23 | R23-ZSC-001 | R23-C-001 | PKG | 107-FB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | N2 PURGE SUPPLY | 8860 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | RCS |  | TI702-SP-5018 |  |  | 01
R23 | R23-ZSO-001 | R23-C-001 | PKG | 107-FB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | N2 PURGE SUPPLY | 8860 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ5-18GM-N |  | TI702-SP-5018 |  |  | 01
R23 | R23-CV-002 | R23-C-002 | PKG | 107-FB | BALL VALVE - ON/OFF - F.C. | 15-H-SS3T-0-9025166 | 066.0 | H2 SUPPLY | 8861 | - | - |  | 6 | F | SIL |  |  |  |  | 0 | [7 empty] | 01
R23 | R23-CX-002 | R23-C-002 | SGS | 107-FB | VALVE INTERLOCK FUNCTION | SGS | 066.0 | H2 SUPPLY | 8861 | - | - |  | 6 |  |  | N.I.S | DO |  |  | 42 | HYD |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R23 | R23-CY-002 | R23-C-002 | FLD | 107-FB | SOLENOID VALVE | RACK MOUNTED | 066.0 | H2 SUPPLY | 8861 | - | - |  | 6 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-002 | R23-C-002 | PKG | 107-FB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | H2 SUPPLY | 8861 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-002 | R23-C-002 | PKG | 107-FB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | H2 SUPPLY | 8861 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-003 | R23-C-003 | FLD | 107-FA | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-0-9025146 | 066.0 | NITROGEN SUPPLY | 6798 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | HYD | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004 | TI702-SP-5022 |  |  | 01
R23 | R23-CV-004 | R23-C-004 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | 100-P-HS3A-H-9025160 | 066.0 | SOLIDS INLET | 7546 | - | - |  | 6 | F | SIL |  |  |  |  | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-CX-004 | R23-C-004 | SGS | 107-FA | VALVE INTERLOCK FUNCTION | SGS | 066.0 | SOLIDS INLET | 7546 | - | - |  | 6 |  |  | N.I.S | DO |  |  | 42 | HYD |  |  |  |  | CONTROL SIGNAL FROM PCS |  | 01
R23 | R23-CY-004 | R23-C-004 | FLD | 107-FA | SOLENOID VALVE | RACK MOUNTED | 066.0 | SOLIDS INLET | 7546 | - | - |  | 6 | F | SIL | I.S |  | DO |  | 41 | SIS | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-004 | R23-C-004 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | SOLIDS INLET | 7546 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-004 | R23-C-004 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | SOLIDS INLET | 7546 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-006 | R23-C-006 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | 40-P-HS3A-H-9025149 | 066.0 | LIQUID INLET | 7544 | - | - | GxP | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-CY-006 | R23-C-006 | FLD | 107-FA | SOLENOID VALVE | RACK MOUNTED | 066.0 | LIQUID INLET | 7544 | - | - | GxP | REQ |  |  | I.S | DO |  |  | 41 | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-006 | R23-C-006 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | LIQUID INLET | 7544 | - | - | GxP | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-006 | R23-C-006 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | LIQUID INLET | 7544 | - | - | GxP | 6 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-009 | R23-C-009 | FLD | 107-FA | BALL VALVE - ON/OFF - F.O. | 25-P-HS3A-0-9025172 | 066.0 | VENT LINE | 7545 | - | - | SHE | 6 | F | SIL |  |  |  |  | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-CY-009 | R23-C-009 | SIS | 107-FA | VALVE INTERLOCK FUNCTION | SIS | 066.0 | VENT LINE | 7545 | - | - | SHE | 6 |  |  | I.S |  |  |  |  | SIS | RGS | EP000/ia |  | TI702-SP-5102 |  |  | 01
R23 | R23-CY-009A | R23-C-009 | FLD | 107-FA | SOLENOID VALVE | VOID ADJ IJB 19549 | 066.0 | VENT LINE | 7545 | - | - | SHE | 6 |  |  | I.S | DO |  |  | 41 | HYD | RGS | EP000/ia |  | TI702-SP-5102 |  |  | 01
R23 | R23-CY-009B | R23-C-009 | FLD | 107-FA | SOLENOID VALVE | VOID ADJ IJB 19549 | 066.0 | VENT LINE | 7545 | - | - | SHE | 6 | F | SIL | I.S |  | DO |  | 41 | SIS | RGS | EP000/ia |  | TI702-SP-5102 |  |  | 01
R23 | R23-ZSC-009 | R23-C-009 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | VENT LINE | 7545 | - | - | REF | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-009 | R23-C-009 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | VENT LINE | 7545 | - | - | REF | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-010 | R23-C-010 | FLD | 107-FA | GLOBE VALVE - CONTROL - F.O. | 25-P-HS3A-0-9025172 | 066.0 | VENT LINE | 6768 | 0 T0 100% | - | SHE | 6 | F |  | I.S | AO |  |  | 21 | SIS | SAMSON | 3510 / 3730-2 POSITIONER | KV0001 | TI702-SP-5022 |  |  | 01
R23 | R23-CY-010 | R23-C-010 | FLD | 107-FA | SOLENOID VALVE | MTD. ON VALVE | 066.0 | VENT LINE | 6768 | - | - | SHE | 6 | F |  | I.S |  | DO |  | 41 | SIS | RGS | EP000/ia |  | TI702-SP-5102 |  |  | 01
R23 | R23-CV-011 | R23-C-011 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-H-9025100 | 066.0 | LIQUIDS SUPPLY | 7163 | - | - | SHE | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R23 | R23-CY-011 | R23-C-011 | FLD | 107-FA | SOLENOID VALVE | RACK MOUNTED | 066.0 | LIQUIDS SUPPLY | 7163 | - | - | SHE | REQ |  |  | I.S | DO |  |  | 41 | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-011 | R23-C-011 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | LIQUIDS SUPPLY | 7163 | - | - | SHE | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-011 | R23-C-011 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | LIQUIDS SUPPLY | 7163 | - | - | SHE | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-012 | R23-C-012 | FLD | 107-FA | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-C-9025110 | 066.0 | VC1 HTF RTN | 6443 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | HYD | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5022 |  |  | 01
R23 | R23-CV-013 | R23-C-013 | FLD | 107-FA | BOTTOM OUTLET VALVE - ON/OFF - F.C. | 25-P-HS3A-0-9025171 | 066.0 | BOTTOM OUTLET VALVE | 8862 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R23 | R23-CY-013 | R23-C-013 | FLD | 107-FA | SOLENOID VALVE | MTD. ON VALVE | 066.0 | BOTTOM OUTLET VALVE | 8862 | - | - |  | REQ |  |  | I.S | DO |  |  | 41 | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-013 | R23-C-013 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | BOTTOM OUTLET VALVE | 8862 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-013 | R23-C-013 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | BOTTOM OUTLET VALVE | 8862 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-015 | R23-C-015 | FLD | 107-FA | GLOBE VALVE - CONTROL - STAYPUT | 40-HT-CS3A-H-9025105 | 066.0 | TEMPERED HTF RETURN | 6444 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | HYD | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5022 |  |  | 01
R23 | R23-CV-016 | R23-C-016 | FLD | 107-FA | GLOBE VALVE - CONTROL - F.C. | 25-SLP-CS1A-H-9028036 | 023.0 | STEAM SUPPLY | 6765 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | HYD | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5022 |  |  | 01
R23 | R23-CV-017 | R23-C-017 | FLD | 107-FA | GLOBE VALVE - CONTROL - F.C. | 25-SLP-CS1A-H-9025170 | 023.0 | STEAM TO MIXER | 6766 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | HYD | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5022 |  |  | 01
R23 | R23-CV-018 | R23-C-018 | FLD | 107-FA | GLOBE VALVE - CONTROL - F.O. | 50-SLP-CS1A-H-9025102 | 066.0 | COOLING WATER BYPASS | 6770 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | HYD | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5022 |  |  | 01
R23 | R23-CV-020 | R23-C-020 | FLD | 107-FA | GLOBE VALVE - CONTROL - F.O. | 40-P-HS3A-0-9025113 | 066.0 | VC1 TO VENT | 6769 | 0 T0 100% | - | REF | 6 | F |  | I.S | AO |  |  | 21 | SIS | SAMSON | 241-7 / 3730-2 POSITIONER | KV0001 | TI702-SP-5022 |  |  | 01
R23 | R23-CY-020 | R23-C-020 | FLD | 107-FA | SOLENOID VALVE | MTD. ON VALVE | 066.0 | VC1 TO VENT | 6769 | - | - |  | 6 | F |  | I.S |  | DO |  | 41 | SIS | RGS | EP000/ia |  | TI702-SP-5102 |  |  | 01
R23 | R23-CV-021 | R23-C-021 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | 25-SLP-CS1A-H-9028036 | 023.0 | STEAM SUPPLY | 8139 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-CY-021 | R23-C-021 | FLD | 107-FA | SOLENOID VALVE | RACK MOUNTED | 023.0 | STEAM SUPPLY | 8139 | - | - |  | REQ |  |  | I.S | DO |  |  | 41 | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-021 | R23-C-021 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 023.0 | STEAM SUPPLY | 8139 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-021 | R23-C-021 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 023.0 | STEAM SUPPLY | 8139 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-022 | R23-C-022 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9025148 | 066.0 | N2 TO BOTTOM OUTLET | 7078 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R23 | R23-CY-022 | R23-C-022 | FLD | 107-FA | SOLENOID VALVE | RACK MOUNTED | 066.0 | N2 TO BOTTOM OUTLET | 7078 | - | - |  | REQ |  |  | I.S | DO |  |  | 41 | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-022 | R23-C-022 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | N2 TO BOTTOM OUTLET | 7078 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-022 | R23-C-022 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | N2 TO BOTTOM OUTLET | 7078 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-023 | R23-C-023 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | 25-N-HS3A-0-9025167 | 066.0 | NITROGEN PURGE | 7110 | - | - | SHE | 6 | F | SIL |  |  |  |  | 0 |  | PBM |  | KV0017/P |  |  |  | 01
R23 | R23-CY-023 | R23-C-023 | SIS | 107-FA | VALVE INTERLOCK FUNCTION | SIS | 066.0 | NITROGEN PURGE | 7110 | - | - | SHE | 6 |  |  | I.S |  |  |  |  | SIS | RGS | EP000/ia |  | TI702-SP-5102
R23 | R23-CY-023A | R23-C-023 | FLD | 107-FA | SOLENOID VALVE | VOID ADJ IJB19549 | 066.0 | NITROGEN PURGE | 7110 | - | - | SHE | 6 |  |  | I.S | DO |  |  | 41 | HYD | RGS | EP000/ia |  | TI702-SP-5102 |  |  | 01
R23 | R23-CY-023B | R23-C-023 | FLD | 107-FA | SOLENOID VALVE | VOID ADJ IJB19549 | 066.0 | NITROGEN PURGE | 7110 | - | - | SHE | 6 | F | SIL | I.S |  | DO |  | 41 | SIS | RGS | EP000/ia |  | TI702-SP-5102 |  |  | 01
R23 | R23-ZSC-023 | R23-C-023 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | NITROGEN PURGE | 7110 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-023 | R23-C-023 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | NITROGEN PURGE | 7110 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-026 | R23-C-026 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | 15-H-SS3T-0-9025166 | 066.0 | HYDROGEN SUPPLY | 8865 | - | - | REF | REQ | F |  | I.S |  |  |  | 0 |  | PBM | Note 2 | KV0017/P |  |  |  | 01
R23 | R23-CY-026 | R23-C-026 | FLD | 107-FA | SOLENOID VALVE | RACK MOUNTED | 066.0 | HYDROGEN SUPPLY | 8865 | - | - |  | REQ |  |  | I.S | DO |  |  | 41 | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-026 | R23-C-026 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | HYDROGEN SUPPLY | 8865 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-026 | R23-C-026 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | HYDROGEN SUPPLY | 8865 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-027 | R23-C-027 | FLD | 107-FA | GLOBE VALVE - CONTROL - F.C. | 15-H-SS3T-0-9025166 | 066.0 | HYDROGEN SUPPLY | 8872 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | HYD | SAMSON | 3510 / 3730-2 POSITIONER | KV0001/P | TI702-SP-5022 |  |  | 01
R23 | R23-CV-028 | R23-C-028 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | WITH REACTOR R23 | 066.0 | SAMPLE LINE | PKG: 8870; -: -; -: -; REF: SHE; REQ: REQ
R23 | R23-CY-028 | R23-C-028 | FLD | 107-FA | SOLENOID VALVE | RACK MOUNTED | 066.0 | SAMPLE LINE | 8870 | - | - | SHE | REQ |  |  | I.S |  |  |  |  | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-028 | R23-C-028 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | SAMPLE LINE | 8870 | - | - | SHE | 12 |  |  | I.S |  |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-028 | R23-C-028 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | SAMPLE LINE | 8870 | - | - | SHE | REQ |  |  | I.S |  |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-029 | R23-C-029 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | 15-N-SS1U-0-9025185 | 066.0 | SAMPLER LOW PRESS. N2 | PKG: 16014; -: -; -: -; REF: SHE; REQ: REQ
R23 | R23-CY-029 | R23-C-029 | FLD | 107-FA | SOLENOID VALVE | RACK MOUNTED | 066.0 | SAMPLER LOW PRESS. N2 | 16014 | - | - | SHE | 12 |  |  | I.S |  |  |  |  | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-029 | R23-C-029 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | SAMPLER LOW PRESS. N2 | 16014 | - | - | SHE | REQ |  |  | I.S |  |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-029 | R23-C-029 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | SAMPLER LOW PRESS. N2 | 16014 | - | - | SHE | REQ |  |  | I.S |  |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-030 | R23-C-030 | FLD | 107-FB | BALL VALVE - ON/OFF - F.C. | 25-N-SS3T-0-9025167 | 066.0 | SAMPLER HIGH PRESS. N2 | PKG: 16015; -: -; -: -; REF: REF; REQ: REQ
R23 | R23-CY-030 | R23-C-030 | FLD | 107-FB | SOLENOID VALVE | RACK MOUNTED | 066.0 | SAMPLER HIGH PRESS. N2 | PKG: 16015; -: -; -: -; REQ: REQ; I.S: I.S |  |  |  | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-030 | R23-C-030 | FLD | 107-FB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | SAMPLER HIGH PRESS. N2 | PKG: 16015; -: -; -: -; REQ: REQ; I.S: I.S |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-030 | R23-C-030 | FLD | 107-FB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | SAMPLER HIGH PRESS. N2 | PKG: 16015; -: -; -: -; REQ: REQ; I.S: I.S |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-031 | R23-C-031 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | 15-CWF-CS1B-AC-9025137 | 066.0 | R23-AG1 CW SUPPLY | PKG: 16016; -: -; -: -; REQ: REQ
R23 | R23-CV-031B | R23-C-031 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | [20 empty] | Retagged R23-CV32B |  |  | v14 | bar: PKG
R23 | R23-CY-031 | R23-C-031 | FLD | 107-FA | SOLENOID VALVE | RACK MOUNTED | 066.0 | R23-AG1 CW SUPPLY | PKG: 16016; -: -; -: -; REQ: REQ; I.S: I.S |  |  |  | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-031 | R23-C-031 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | R23-AG1 CW SUPPLY | PKG: 16016; -: -; -: -; REQ: REQ; I.S: I.S |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-031 | R23-C-031 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | R23-AG1 CW SUPPLY | PKG: 16016; -: -; -: -; REQ: REQ; I.S: I.S |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-CV-032 | R23-C-032 | FLD | 902-007-002-000-00159 | BALL VALVE - ON/OFF | 15-CA-SS1U-0-9028594 | 198 | R24-B01 PLANT AIR SUPPLY | PKG: 16017; -: -; -: -; REQ: REQ
| R23-CV-032B | R23-C-032 | FLD | 107-FA | BALL VALVE - ON/OFF - F.C. | R23 AGI CW SYSTEM | 066.0 | R23-ST1 CW RTN ISOLATION | bar: PKG
R23 | R23-CY-032 | R23-C-032 | FLD | 902-007-002-000-00159 | SOLENOID VALVE | RACK MOUNTED | 198 | R24-B01 PLANT AIR SUPPLY | PKG: 16017; -: -; -: -; REQ: REQ; I.S: I.S |  |  |  | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  | 01
R23 | R23-ZSC-032 | R23-C-032 | FLD | 902-007-002-000-00159 | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 198 | R24-B01 PLANT AIR SUPPLY | PKG: 16017; -: -; -: -; REQ: REQ; I.S: I.S |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-ZSO-032 | R23-C-032 | FLD | 902-007-002-000-00159 | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 198 | R24-B01 PLANT AIR SUPPLY | PKG: 16017; -: -; -: -; REQ: REQ; I.S: I.S |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
| R23-CV-033 | R23-C-033 | FLD | 902-007-002-000-00159 | BALL VALVE - ON/OFF - F.C. | 15-H-SS3T-0-9025166 | 066.0 | R23 HYDROGEN SUPPLY | REF: SHE; REQ: 24; F: F
R23 | R23-CY-033 | R23-C-033 | FLD | 902-007-002-000-00159 | SOLENOID VALVE | RACK MOUNTED | 066.0 | R23 HYDROGEN SUPPLY |  | - | - | SHE | 24 | F |  | I.S | DO |  |  |  | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  |  | v0.1
R23 | R23-ZSC-033 | R23-C-033 | FLD | 902-007-002-000-00159 | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | R23 HYDROGEN SUPPLY | -: -; -: -; REQ: REQ; I.S: I.S; DI: DI |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  |  | v0.1
R23 | R23-ZSO-033 | R23-C-033 | FLD | 902-007-002-000-00159 | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | R23 HYDROGEN SUPPLY | -: -; -: -; REQ: REQ; I.S: I.S; DI: DI |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  |  | v0.1
| R23-CV-034 | R23-C-034 | FLD | 902-007-002-000-00159 | BALL VALVE - ON/OFF - F.C. | 15-H-SS3T-0-9025166 | 198 | R24 HYDROGEN SUPPLY | REF: SHE; REQ: 24; F: F
R23 | R23-CY-034 | R23-C-034 | FLD | 902-007-002-000-00159 | SOLENOID VALVE | RACK MOUNTED | 198 | R24 HYDROGEN SUPPLY |  | - | - | SHE | 24 | F |  | I.S | DO |  |  |  | HYD | CROUZET | 81 519 _35 |  | TI702-SP-5019 |  |  |  | v0.1
R23 | R23-ZSC-034 | R23-C-034 | FLD | 902-007-002-000-00159 | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 198 | R24 HYDROGEN SUPPLY | -: -; -: -; REQ: REQ; I.S: I.S; DI: DI |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  |  | v0.1
R23 | R23-ZSO-034 | R23-C-034 | FLD | 902-007-002-000-00159 | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 198 | R24 HYDROGEN SUPPLY | -: -; -: -; REQ: REQ; I.S: I.S; DI: DI |  |  |  | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  |  | v0.1
R23 | R23-DIC-002 | R23-D-002 | PCS | 107-FA | INDICATING CONTR. - MOTOR DRIVE | PCS | 066.0 | JACKET PUMP | PKG: 8867; -: -; -: -; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-DS-002 | R23-D-002 | MCC | 107-FA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE | 066.0 | JACKET PUMP | 8867 | - | - |  | REQ |  |  | N.I.S | DI |  |  | 35 | HYD | [6 empty] | 01
R23 | R23-DY-002 | R23-D-002 | MCC | 107-FA | DRIVE - RUNNING | MOTOR CONTROL CENTRE | 066.0 | JACKET PUMP | 8867 | - | - |  | REQ |  |  | N.I.S | DI |  |  | 35 | HYD | [6 empty] | 01
R23 | R23-DYC-002 | R23-D-002 | MCC | 107-FA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 066.0 | JACKET PUMP | 8867 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | HYD | [6 empty] | 01
R23 | R23-DIC-003 | R23-D-003 | PCS | 107-FA | INDICATING CONTR. - MOTOR DRIVE | PCS | 066.0 | TRANSFER PUMP | PKG: 8868; -: -; -: -; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-DS-003 | R23-D-003 | MCC | 107-FA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE | 066.0 | TRANSFER PUMP | 8868 | - | - |  | REQ |  |  | N.I.S | DI |  |  | 35 | HYD | [6 empty] | 01
R23 | R23-DY-003 | R23-D-003 | MCC | 107-FA | DRIVE - RUNNING | MOTOR CONTROL CENTRE | 066.0 | TRANSFER PUMP | 8868 | - | - |  | REQ |  |  | N.I.S | DI |  |  | 35 | HYD | [6 empty] | 01
R23 | R23-DYC-003 | R23-D-003 | MCC | 107-FA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 066.0 | TRANSFER PUMP | 8868 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | HYD | [6 empty] | 01
R23 | R23-FIT-002 | R23-F-002 | FLD | 107-FA | TRANSMITTER - FLOW | 25-P-SS1C-0-9025161 | 066.0 | LIQUIDS SUPPLY | 6455 | 0 - 4 m3/hr | +/- 0.25% | SHE | REQ | C |  | N.I.S | DI |  |  | 36 | HYD | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
R23 | R23-FQIC-002 | R23-F-002 | PCS | 107-FA | INDICATING CONTROLLER - FLOW/TOTAL | PCS | 066.0 | LIQUIDS SUPPLY | PKG: 6455; -: 0 - 4 m3/hr; -: +/- 0.25%; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-FI-003 | R23-F-003 | FLD | 107-FA | INDICATOR - FLOW | 25-N-SS1U-0-9028722 | 043.3 | N2 VENT PURGE | PKG: N/A; -: 1 to 10 L/min; -: +/- 5%; REQ: REQ; F: C |  |  | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
R23 | R23-FIC-004 | R23-F-004 | PCS | 107-FA | INDICATING CONTROLLER - FLOW | PCS | 066.0 | HYDROGEN FLOW | PKG: 8869; -: 0.01 N l/pulse; -: +/- 0.5%; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-FIT-004A | R23-F-004 | FLD | 107-FA | TRANSMITTER - FLOW | 15-H-HS3A-9025121 | 066.0 | HYDROGEN FLOW | 8869 | 0.01 N l/pulse | +/- 0.5% | SHE | 5 YR | C |  | N.I.S | DI |  |  | 36 | HYD | ENDRESS + HAUSER | Note 1 | KF0002/P |  | INPUT TO FQI-004 |  | 01
R23 | R23-FIT-004B | R23-F-004 | FLD | 107-FA | TRANSMITTER - FLOW |  | 066.0 | HYDROGEN FLOW | 8869 | 0-1680 N l/min | +/- 0.5% | SHE | 5 YR | C |  | N.I.S. | AI |  |  | 13 | HYD | ENDRESS + HAUSER | Note 1 |  |  | INPUT TO FIC-004 |  | 01
R23 | R23-FQI-004 | R23-F-004 | PCS | 107-FA | INDICATOR - FLOW/TOTALISER | PCS | 066.0 | HYDROGEN FLOW | PKG: 8869; -: 0.01 N l/pulse; -: +/- 0.5%; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-FAL-005 | R23-F-005 | PCS | 107-FA | FLOW ALARM - LOW | PCS | 066.0 | R23-AG1 CW FLOW | PKG: 11906; -: -; -: -; REF: SHE; REQ: 12 | [10 empty] | 01
R23 | R23-FI-005 | R23-F-005 | FLD | 107-FA | INDICATOR - FLOW | 15-CWF-CS1B-AC-9025137 | 066.0 | R23-AG1 CW FLOW | 11906 | 0 to 400 L/hr | +/- 2% | REF | REQ | C | [7 empty] | RMC | GMTA123L | KF0027/P1 |  |  |  | 01
R23 | R23-FI-005A | R23-F-005 | FLD | 107-FA | INDICATOR - FLOW | 15-CWF-CS1B-AC-9025137 | 066.0 | R23-AG1 GEARBOX CW FLOW | 11906 | 0 to 630 L/hr | +/- 2% | SHE | 12 | C
R23 | R23-FI-005B | R23-F-005 | FLD | 107-FA | INDICATOR - FLOW | 15-CWF-CS1B-AC-9025137 | 066.0 | R23-AG1 DRIVE CW FLOW | 11906 | 0 to 630 L/hr | +/- 2% | SHE | 12 | C
R23 | R23-FI-005C | R23-F-005 | FLD | 107-FA | INDICATOR - FLOW | 15-CWF-CS1B-AC-9025137 | 066.0 | R23-AG1 HEAT TRAP CW FLOW | 11906 | 0 to 630 L/hr | +/- 2% | SHE | 12 | C
R23 | R23-FSL-005 | R23-F-005 | FLD | 107-FA | FLOW SWITCH - LOW | WITH FI-005 | 066.0 | R23-AG1 CW FLOW | 11906 | set @ 300 L/hr | +/- 5% | REF | REQ | F | [13 empty] | 01
R23 | R23-FSL-005A | R23-F-005 | FLD | 107-FA | FLOW SWITCH - LOW | WITH FI-005A | 066.0 | R23-AG1 GEARBOX CW FLOW | 11906 | set @ 400 L/hr | +/- 20 L/hr | SHE | 12 | F |  | I.S |  |  |  |  | HYD | KROHNE | H250 M40 |  | TI702-SP-5028
R23 | R23-FSL-005B | R23-F-005 | FLD | 107-FA | FLOW SWITCH - LOW | WITH FI-005B | 066.0 | R23-AG1 DRIVE CW FLOW | 11906 | set @ 150 L/hr | +/- 7.5 L/hr | SHE | 12 | F |  | I.S |  |  |  |  | HYD | KROHNE | H250 M40 |  | TI702-SP-5028
R23 | R23-FSL-005C | R23-F-005 | FLD | 107-FA | FLOW SWITCH - LOW | WITH FI-005C | 066.0 | R23-AG1 HEAT TRAP CW FLOW | 11906 | set @ 150 L/hr | +/- 7.5 L/hr | SHE | 12 | F |  | I.S |  |  |  |  | HYD | KROHNE | H250 M40 |  | TI702-SP-5028
R23 | R23-HV-001 | R23-H-001 | FLD | 107-FA | HAND VALVE - 3 WAY | 25-N-SS1U-0-9028720 | 066.0 | N2 PRESSURE SELECT | 8137 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-HZSC-001 | R23-H-001 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | N2 PRESSURE SELECT | 8137 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-001 | R23-H-001 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | N2 PRESSURE SELECT | 8137 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 | 0.8 BARG N2 LINE OPEN |  | 01
R23 | R23-HS-002 | R23-H-002 | LCP | 107-FA | SWITCH - PNEUMATIC | LOCAL PANEL | 066.0 | NITROGEN SUPPLY | 7487 | - | - | REF | REQ | F | [5 empty] | 0 |  | RGS | H125/46 |  |  |  |  | 01
R23 | R23-HV-002 | R23-H-002 | FLD | 107-FA | HAND VALVE - ACTUATED | 25-N-PT1A-0-9025146 | 066.0 | NITROGEN SUPPLY | 7487 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | OPERATED FROM LOCAL PANEL |  | 01
R23 | R23-HZSC-002 | R23-H-002 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | NITROGEN SUPPLY | 7487 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-002 | R23-H-002 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | NITROGEN SUPPLY | 7487 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HS-003 | R23-H-003 | FLD | 107-FA | SWITCH - HAND OP. | ADJ TO R23 | 066.0 | CRASH COOL | 8142 | - | - |  | 6 | F | SOP | I.S | DI |  |  | 32 | HYD | TELEMECANIQUE | ZB2-BE101 | KB0003 | TI702-SP-5103 |  |  | 01
R23 | R23-HS-005 | R23-H-005 | LCP | 107-FA | SWITCH - PNEUMATIC | LOCAL PANEL | 066.0 | N2 TO VENT | 7421 | - | - | REF | REQ | F | [5 empty] | 0 |  | RGS | H125/46 |  |  |  |  | 01
R23 | R23-HV-005 | R23-H-005 | FLD | 107-FA | HAND VALVE - ACTUATED | 25-P-SS1C-0-9025133 | 066.0 | N2 TO VENT | 7421 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  | OPERATED FROM LOCAL PANEL |  | 01
R23 | R23-HZSC-005 | R23-H-005 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | N2 TO VENT | 7421 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-005 | R23-H-005 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | N2 TO VENT | 7421 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HS-006 | R23-H-006 | LCP | 107-FA | SWITCH - PNEUMATIC | LOCAL PANEL | 066.0 | NITROGEN SUPPLY | 7422 | - | - | REF | REQ | F | [5 empty] | 0 |  | RGS | H125/46 |  |  |  |  | 01
R23 | R23-HV-006 | R23-H-006 | FLD | 107-FA | HAND VALVE - ACTUATED | 50-P-HS3A-H-9025181 | 066.0 | NITROGEN SUPPLY | 7422 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | OPERATED FROM LOCAL PANEL |  | 01
R23 | R23-HZSC-006 | R23-H-006 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | NITROGEN SUPPLY | 7422 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-006 | R23-H-006 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | NITROGEN SUPPLY | 7422 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HS-007 | R23-H-007 | LCP | 107-FA | SWITCH - PNEUMATIC | LOCAL PANEL | 066.0 | VC1 TO VENT | 8136 | - | - | REF | REQ | F | [5 empty] | 0 |  | RGS | H125/46 |  |  |  |  | 01
R23 | R23-HV-007 | R23-H-007 | FLD | 107-FA | HAND VALVE - ACTUATED | 40-P-HS3A-0-9025113 | 066.0 | VC1 TO VENT | 8136 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | OPERATED FROM LOCAL PANEL |  | 01
R23 | R23-HZSC-007 | R23-H-007 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | VC1 TO VENT | 8136 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-007 | R23-H-007 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | VC1 TO VENT | 8136 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-008 | R23-H-008 | FLD | 107-FA | HAND VALVE | 40-P-PT1A-H-9025100 | 066.0 | VENT | 7423 | - | - | SIL | 6 | F | SIL |  |  |  |  | 0 |  |  |  | KV0007 |  |  |  | 01
R23 | R23-HZSC-008 | R23-H-008 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | VENT | 7423 | - | - | SIL | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-008 | R23-H-008 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | VENT | 7423 | - | - | SIL | 6 | F | SIL | I.S |  | DI |  | 31 | SIS | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-009 | R23-H-009 | FLD | 107-FA | HAND VALVE | 50-SLP-CS1A-H-9025104 | 066.0 | HTF SUPPLY | 8134 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-HZSC-009 | R23-H-009 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | HTF SUPPLY | 8134 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-009 | R23-H-009 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | HTF SUPPLY | 8134 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-010 | R23-H-010 | FLD | 107-FA | HAND VALVE | 25-CLP-CS1A-H-9025147 | 066.0 | JACKET DRAIN | 8131 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-HZSC-010 | R23-H-010 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | JACKET DRAIN | 8131 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-010 | R23-H-010 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | JACKET DRAIN | 8131 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-011 | R23-H-011 | FLD | 107-FA | HAND VALVE | 40-P-PT1A-H-9025100 | 066.0 | DISTILLATE RTN | 7461 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R23 | R23-HZSC-011 | R23-H-011 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | DISTILLATE RTN | 7461 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-011 | R23-H-011 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | DISTILLATE RTN | 7461 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-012 | R23-H-012 | FLD | 107-FA | HAND VALVE | 25-P-PT1A-H-9025108 | 066.0 | DISTILLATE RTN | 7424 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R23 | R23-HZSC-012 | R23-H-012 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | DISTILLATE RTN | 7424 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-012 | R23-H-012 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | DISTILLATE RTN | 7424 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-013 | R23-H-013 | FLD | 107-FA | HAND VALVE | 25-P-PT1A-0-9025143 | 066.0 | TP1 RECIRC LINE | 7425 | - | - | REF | REQ | F | [5 empty] | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 01
R23 | R23-HZSC-013 | R23-H-013 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | TP1 RECIRC LINE | 7425 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-013 | R23-H-013 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | TP1 RECIRC LINE | 7425 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-014 | R23-H-014 | FLD | 107-FA | HAND VALVE | 25-P-HS3A-0-9025171 | 066.0 | BOTTOM OUTLET | 8135 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-HZSC-014 | R23-H-014 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | BOTTOM OUTLET | 8135 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-014 | R23-H-014 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | BOTTOM OUTLET | 8135 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-015 | R23-H-015 | FLD | 107-FA | HAND VALVE | 50-SLP-CS1A-H-9025102 | 066.0 | JACKET RTN | 8133 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-HZSC-015 | R23-H-015 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 066.0 | JACKET RTN | 8133 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-015 | R23-H-015 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 066.0 | JACKET RTN | 8133 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-016 | R23-H-016 | FLD | 107-FA | HAND VALVE | 25-SLP-CS1A-H-9028036 | 023.0 | STEAM SUPPLY | 8132 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
R23 | R23-HZSC-016 | R23-H-016 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 023.0 | STEAM SUPPLY | 8132 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HZSO-016 | R23-H-016 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 023.0 | STEAM SUPPLY | 8132 | - | - |  | REQ |  |  | I.S | DI |  |  | 31 | HYD | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
R23 | R23-HV-017 | R23-H-017 | PKG | 107-FA | HAND VALVE | WITH REACTOR R23 | 066.0 | SAMPLE VALVE | 8870 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
R23 | R23-HZSC-017 | R23-H-017 | FLD | 107-FA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SAMPLE VALVE | I.S: I.S; DI: DI |  |  | 31 | HYD | [6 empty] | 01
R23 | R23-HZSO-017 | R23-H-017 | FLD | 107-FA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SAMPLE VALVE | I.S: I.S; DI: DI |  |  | 31 | HYD | [6 empty] | 01
R23 | R23-II-002 | R23-I-002 | PCS | 107-FA | INDICATOR - CURRENT | PCS | 066.0 | AGITATOR CURRENT | PKG: 8875; -: 0 to 5 amp; -: +/- 1%; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-IT-002 | R23-I-002 | MCC | 107-FA | TRANSMITTER - CURRENT | MOTOR CONTROL CENTRE | 066.0 | AGITATOR CURRENT | 8875 | 0 to 5 amp | +/- 1% | REF | REQ | C |  | N.I.S | AI |  |  | 13 | HYD | [6 empty] | 01
R23 | R23-LAH-001 | R23-L-001 | PCS | 107-FA | ALARM - LEVEL - HIGH | PCS | 066.0 | HIGH LEVEL | PKG: 6638; -: On/Off; -: On/Off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
R23 | R23-LE-001 | R23-L-001 | FLD | 107-FA | ELEMENT - LEVEL | 80-P-HS3A-H-9025130 | 066.0 | HIGH LEVEL | 6638 | On/Off | On/Off | SHE | 24 | F |  | I.S |  |  |  | 0 | [7 empty] | 01
R23 | R23-LSH-001 | R23-L-001 | CPR | 107-FA | SWITCH - LEVEL - HIGH | 80-P-HS3A-H-9025130 | 066.0 | HIGH LEVEL | 6638 | On/Off | On/Off | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | HYD | ENDRESS + HAUSER | FDL31-GYY9AC70 | KL0014 |  |  |  | 01
R23 | R23-LSH-002 | R23-L-002 | FLD | 107-FA | SWITCH - LEVEL - HIGH | R23-TP1 SEAL POT | 066.0 | TP1 SEAL POT FAILURE | PKG: 8879; -: -; -: -; REF: SHE; REQ: REQ
R23 | R23-LSL-003 | R23-L-003 | FLD | 107-FA | SWITCH - LEVEL - LOW | R23-TP1 SEAL POT | 066.0 | TP1 SEAL POT FAILURE | PKG: 8879; -: On/Off; -: On/Off; REF: SHE; REQ: 24
R23 | R23-LI-004 | R23-L-004 | FLD | 107-FA | INDICATOR - LEVEL | R23-TP1 SEAL POT | 066.0 | TP1 SEAL POT FAILURE | PKG: N/A; -: -; -: -; REF: SHE; REQ: REQ
R23 | R23-LSHH-005 | R23-L-005 | FLD | 107-FA | SWITCH - LEVEL - HIGH |  | 066.0 | bar: PKG
R23 | R23-LSHH-005 | R23-L-005 | PKG | 107-FA | SWITCH - LEVEL - HI HI | R23 SEAL ASSEMBLY | 066.0 | SEAL SYSTEM COMMON ALARM |  | Fixed | - | REF | REQ | F |  | I.S. |  |  |  | 0 | [7 empty] | 01
R23 | R23-LSLL-005 | R23-L-005 | FLD | 107-FA | SWITCH - LEVEL - LOW |  | 066.0 | bar: PKG
| R23-LSLL-005 | R23-L-005 | PKG | 107-FA | SWITCH - LEVEL - LO LO | R23 SEAL ASSEMBLY | 066.0 | SEAL SYSTEM COMMON ALARM |  | Fixed | - | REF | REQ | F |  | I.S. |  |  |  | 0 | [7 empty] | 01
R23 | R23-LAL-006 | R23-L-006 | PCS | 107-FA | ALARM - LEVEL - LOW | R23 AGITATOR PRESS. ACC. | 066.0 | AGI SEAL ACCUMULATOR LEVEL | PKG: 16120; REF: SHE; REQ: 12
R23 | R23-LALL-006 | R23-L-006 | PCS | 107-FA | ALARM - LEVEL - LOW LOW | R23 AGITATOR PRESS. ACC. | 066.0 | AGI SEAL ACCUMULATOR LEVEL | PKG: 16120; REF: SHE; REQ: 12
R23 | R23-LI-006A | R23-L-006 | FLD | 107-FA | INDICATOR - LEVEL | R23 AGITATOR PRESS. ACC. | 066.0 | AGI SEAL ACCUMULATOR LEVEL | -: 0 to 100%; -: +/- 5%; REF: SHE; REQ: 12
R23 | R23-LI-006B | R23-L-006 | FLD | 107-FA | INDICATOR - LEVEL | R23 AGITATOR PRESS. ACC. | 066.0 | AGI SEAL ACCUMULATOR LEVEL | -: 0 to 100%; -: +/- 5%; REF: SHE; REQ: 12
R23 | R23-LT-006 | R23-L-006 | FLD | 107-FA | TRANSMITTER - LEVEL | R23 AGITATOR PRESS. ACC. | 066.0 | AGI SEAL ACCUMULATOR LEVEL | 16120 | 0 to 100% | +/- 5% | SHE | 12 |  |  | I.S |  |  |  |  | HYD | WIKA | T32 |  | TI702-SP-5025
R23 | R23-LSL-007 | R23-L-007 | FLD | 107-FA | SWITCH - LEVEL - LOW | R23-ST1 | 066.0 | LOW OPERATING LEVEL | PKG: 16021; REQ: REQ; F: F; I.S: I.S |  |  |  | HYD | ROSEMOUNT | 2120 |  | TI702-SP-5031
R23 | R23-LSH-008 | R23-L-008 | FLD | 107-FA | SWITCH - LEVEL - HIGH | R23-ST1 | 066.0 | HIGH OPERATING LEVEL | PKG: 16022; REQ: REQ; F: F; I.S: I.S |  |  |  | HYD | ROSEMOUNT | 2120 |  | TI702-SP-5031
R23 | R23-LAHH-009 | R23-L-009 | PCS | 107-FA | ALARM - LEVEL - HIGH HIGH | PCS | 066.0 | HIGH HIGH LEVEL | PKG: 16023; REQ: REQ; F: F
R23 | R23-LSHH-009 | R23-L-009 | FLD | 107-FA | SWITCH - LEVEL - HIGH HIGH | R23-ST1 | 066.0 | HIGH HIGH LEVEL | PKG: 16023; REQ: REQ; F: F; I.S: I.S |  |  |  | HYD | ROSEMOUNT | 2120 |  | TI702-SP-5031
R23 | R23-LAH-010 | R23-L-009 | PCS | 107-FA | ALARM - LEVEL - HIGH | PCS | 066.0 | HIGH LEVEL | REF: SHE; REQ: 24; F: F | [11 empty] | v0.1
R23 | R23-LSH-010 | R23-L-009 | FLD | 107-FA | SWITCH - LEVEL - HIGH | R23-CT02 | 066.0 | HIGH LEVEL | REF: SHE; REQ: 24; F: F; I.S: I.S; DI: DI |  |  |  | HYD | [7 empty] | v0.1
R23 | R23-PAL-001 | R23-P-001 | PCS | 107-FB | ALARM - PRESSURE - LOW | PCS | 066.0 | H2 LOW PRESSURE | PKG: 8873; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-PIT-001 | R23-P-001 | PKG | 107-FB | TRANSMITTER - PRESSURE DIAPHRAGM | GAS SUPPLY PACKAGE | 066.0 | H2 LOW PRESSURE | 8873 |  |  | REF | REQ | C |  | I.S | DI |  |  | 32 | HYD | ENDRESS + HAUSER | PMP635-G33Z9M2YYY9 | KP0001/4 | TI702-SP-5147 |  |  | 01
R23 | R23-PI-002 | R23-P-002 | PKG | 107-FB | PRESSURE GAUGE | WITH R23-PRV-013 | 066.0 | PRV-013 PRESSURE | PKG: N/A; REF: SHE; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R23 | R23-PI-004 | R23-P-004 | PKG | 107-FB | PRESSURE GAUGE | WITH R23-PRV-015 | 066.0 | PRV-015 PRESSURE | PKG: N/A; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R23 | R23-PIC-005 | R23-P-005 | PCS | 107-FA | INDICATING CONTROLLER - PRESSURE | PCS | 066.0 | STEAM PRESSURE | PKG: 6700; -: 0 to 10 barg; -: +/- 5%; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-PT-005 | R23-P-005 | FLD | 107-FA | TRANSMITTER - PRESSURE | 25-SLP-CS1A-H-9028036 | 066.0 | STEAM PRESSURE | 6700 | 0 to 10 barg | +/- 5% | REF | REQ | C |  | I.S | AI |  |  | 11 | HYD | FOXBORO | 141GP | KP0001 | TI702-SP-5023 |  |  | 01
R23 | R23-PIC-006 | R23-P-006 | PCS | 107-FA | INDICATING CONTROLLER - PRESSURE | PCS | 066.0 | PRESSURE | PKG: 6701; -: -1 to 18 barg; -: +/- 0.1 barg; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R23 | R23-PIT-006 | R23-P-006 | FLD | 107-FA | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-HS3A-H-9025130 | 066.0 | PRESSURE | 6701 | -1 to 18 barg | +/- 0.1 barg | SHE | 12 | C |  | I.S | AI |  |  | 11 | HYD | FOXBORO | 141GP (Note 2) | KP0001 | TI702-SP-5023 |  |  | 01
R23 | R23-PI-007 | R23-P-007 | FLD | 107-FA | PRESSURE GAUGE - DIAPHRAGM | 80-P-HS3A-H-9025130 | 066.0 | PRESSURE | N/A | -1 to 9 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27 | KP0006/2 |  |  |  | 01
R23 | R23-PI-008 | R23-P-008 | FLD | 107-FA | PRESSURE GAUGE - STEAM SYPHON | 25-SLP-CS1A-H-9025170 | 023.0 | STEAM TO MIXER PRESSURE | N/A | -1 to 9 barg | +/- 1% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
R23 | R23-PI-009 | R23-P-009 | FLD | 107-FA | PRESSURE GAUGE | 50-SLP-CS1A-H-9025102 | 066.0 | JP1 SUCTION PRESSURE | N/A | 0 to 2.5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 (Note 2) | KP0006/3 |  |  |  | 01
R23 | R23-PI-010 | R23-P-010 | FLD | 107-FA | PRESSURE GAUGE | 50-SLP-CS1A-H-9025180 | 066.0 | JP1 DISCHARGE PRESSURE | N/A | 0 to 6 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100 (Note 2) | KP0006/3 |  |  |  | 01
R23 | R23-PAL-011 | R23-P-011 | PCS | 107-FB | ALARM - PRESSURE - LOW | PCS | 066.0 | N2 PURGE LOW PRESSURE | PKG: 8874; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-PIT-011 | R23-P-011 | PKG | 107-FB | TRANSMITTER - PRESSURE -DIAPHRAGM | GAS SUPPLY PACKAGE | 066.0 | N2 PURGE LOW PRESSURE | 8874 |  | +/- 5% | REF | REQ | C |  | I.S | DI |  |  | 32 | HYD | ENDRESS + HAUSER | PMP635-G33Z9M2YYY1 | KP0001/4 | TI702-SP-5147 |  |  | 01
R23 | R23-PI-012 | R23-P-012 | FLD | 107-FA | PRESSURE GAUGE | R23-TP1 SEAL POT | 066.0 | R23-TP1 PRESSURE | PKG: N/A; -: 0 to 10 barg; -: +/- 5%; REF: SHE; REQ: REQ
R23 | R23-PRV-013 | R23-P-013 | PKG | 107-FB | CONTROL VALVE SELF ACTUATING | GAS SUPPLY PACKAGE | 066.0 | H2 SUPPLY | N/A | set @ 20 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
R23 | R23-PRV-015 | R23-P-015 | PKG | 107-FB | CONTROL VALVE SELF ACTUATING | GAS SUPPLY PACKAGE | 066.0 | H2 SYSTEM N2 PURGE | N/A | set @ 16 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
R23 | R23-PSV-016 | R23-P-016 | PKG | 107-FB | PRESSURE RELIEF VALVE | GAS SUPPLY PACKAGE | 066.0 | GAS SUPPLY RELIEF | PKG: N/A; -: set @ 25 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
R23 | R23-PI-017 | R23-P-017 | FLD | 107-FA | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-0-9025143 | 066.0 | TP1 DISCHARGE PRESSURE | N/A | 0 to 6 barg | +/- 1% | REF | REQ | C | [5 empty] | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
R23 | R23-PIC-018 | R23-P-018 | PCS | 107-FA | INDICATING CONTROLLER - PRESSURE | PCS | 066.0 | PRESSURE | PKG: 7134; -: -0.1 to 1 barg; -: +/- 0.066 barg; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R23 | R23-PSL-018 | R23-P-018 | FLD | 107-FA | SWITCH - PRESSURE - LOW | R23-TP1 SEAL POT | 066.0 | TP1 SEAL POT FAILURE | PKG: 7134; -: set @ 4.5 barg; -: +/- 0.5 barg; REQ: 24
R23 | R23-PT-018 | R23-P-018 | FLD | 107-FA | TRANSMITTER - PRESSURE - DIAPHRAGM | 80-P-HS3A-H-9025130 | 066.0 | PRESSURE | 7134 | -0.1 to 1 barg | +/- 0.066 barg | SHE | 12 | C |  | I.S | AI |  |  | 11 | HYD | ROSEMOUNT | 3051 TG (Note 3) | KP0001 | TI702-SP-5082 |  |  | 01
R23 | R23-PSV-019 | R23-P-019 | FLD | 107-FA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9025115 | 066.0 | VC1 HTF RELIEF | PKG: N/A; -: set @ 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R23 | R23-PSV-020 | R23-P-020 | FLD | 107-FA | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9025127 | 066.0 | CU1 HTF RELIEF | PKG: N/A; -: set @ 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
R23 | R23-PSV-021 | R23-P-021 | FLD | 107-FA | PRESSURE RELIEF VALVE | 25-SLP-CS1A-H-9025116 | 066.0 | JACKET HTF RELIEF | PKG: N/A; -: set @ 7.5 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 26113-S3-N000 | KS0001 |  |  |  | 01
R23 | R23-PRV-022 | R23-P-022 | FLD | 107-FA | CONTROL VALVE SELF ACTUATING | 50-CWR-CS1B-AC-9025107 | 066.0 | COOLING WATER BYPASS | N/A | set @ 2 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | BROADY | TYPE 8 | KS0001A |  |  |  | 01
R23 | R23-PRV-023 | R23-P-023 | FLD | 107-FA | CONTROL VALVE SELF ACTUATING | 25-SLP-CS1A-H-9028036 | 066.0 | STEAM TO JACKET | N/A | set @ 5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | Esme | R1480S | KV0006 |  |  |  | 01
R23 | R23-PRV-030 | R23-P-030 | FLD | 902-007-002-000-00159 | CONTROL VALVE SELF ACTUATING | R24-B01 PACKAGE | 198 | R24-B01 PLANT AIR SUPPLY | PKG: N/A; -: set @ 6 barg; -: +/- 5%; REF: REF; REQ: REQ
R23 | R23-PAL-031 | R23-P-031 | PCS | 107-FA | ALARM - PRESSURE - LOW | PCS | 066.0 | SGS AIR SUPPLY | PKG: 11132; -: set @ 4.5 barg; -: +/- 0.5 barg; REQ: 24 |  |  | 0 | [7 empty] | 01
R23 | R23-PSL-031 | R23-P-031 | FLD | 107-FA | SWITCH - PRESSURE - LOW | SIS AIR SUPPLY | 066.0 | SIS AIR SUPPLY | 11132 | set @ 4.5 barg | +/- 0.5 barg | REF | 24 | F |  | I.S |  | DI |  | 32 | SIS | PARKER | 43018 | KP0012/P | TI702-SP-5132 |  |  | 01
R23 | R23-PRV-032 | R23-P-032 | FLD | 107-FA | CONTROL VALVE SELF ACTUATING | SGS AIR SUPPLY | 066.0 | SGS AIR SUPPLY | N/A | set @ 5 barg | +/- 5% | REF | REQ | C | [5 empty] | 0 |  | PARKER | P3E-AA14WGB |  |  | GAS BOTTLE REGULATOR |  | 01
R23 | R23-PSV-033 | R23-P-033 | PKG | 107-FB | PRESSURE RELIEF VALVE | GAS SUPPLY PACKAGE | 066.0 | H2 SUPPLY N2 PURGE RELIEF | PKG: N/A; -: set @ 20 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
R23 | R23-PI-034 | R23-P-034 | PKG | 107-FA | PRESSURE GAUGE | R23 SEAL ASSEMBLY | 066.0 | SEAL SYSTEM COMMON ALARM | -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
R23 | R23-PSV-034 | R23-P-034 | PKG | 107-FA | PRESSURE RELIEF VALVE | SGS AIR SUPPLY | 066.0 | SGS AIR SUPPLY | PKG: N/A; -: set @ 8.5 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
R23 | R23-PI-035 | R23-P-035 | PKG | 107-FB | PRESSURE GAUGE | GAS SUPPLY PACKAGE | 066.0 | HYDROGEN SUPPLY | N/A | 0 to 400 barg | +/- 10% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
R23 | R23-PI-036 | R23-P-036 | PKG | 107-FB | PRESSURE GAUGE | GAS SUPPLY PACKAGE | 066.0 | HYDROGEN SUPPLY | N/A | 0 to 400 barg | +/- 10% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
R23 | R23-PI-037 | R23-P-037 | PKG | 107-FB | PRESSURE GAUGE | GAS SUPPLY PACKAGE | 066.0 | NITROGEN SUPPLY | N/A | 0 to 400 barg | +/- 10% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
R23 | R23-PI-038 | R23-P-038 | PKG | 107-FB | PRESSURE GAUGE | GAS SUPPLY PACKAGE | 066.0 | NITROGEN SUPPLY | N/A | 0 to 400 barg | +/- 10% | REF | REQ | C | [5 empty] | 0 | [7 empty] | 01
R23 | R23-PI-039 | R23-P-039 | PKG | 107-FA | PRESSURE GAUGE | WITH R23-PRV-013 | 066.0 | PRV-013 PRESSURE | PKG: N/A; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
R23 | R23-PI-040 | R23-P-040 | PKG | 107-FA | PRESSURE GAUGE | WITH R23-PRV-015 | 066.0 | PRV-015 PRESSURE | PKG: N/A; -: +/- 5%; REF: REF; REQ: REQ; F: C | [10 empty] | 01
R23 | R23-PI-041 | R23-P-041 | PKG | 107-FA | PRESSURE GAUGE | R23 SAMPLING SYSTEM | 066.0 | SAMPLE CHAMBER PRESSURE | PKG: N/A; -: 0 to 45 barg; -: +/- 0.25 barg; REQ: 12
R23 | R23-PI-042 | R23-P-042 | PCS | 107-FA | INDICATOR - PRESSURE | PCS | 066.0 | SAMPLE CHAMBER PRESSURE | PKG: 16024; -: 0 to 30 barg; -: +/- 0.1 barg; REF: SHE; REQ: 12
R23 | R23-PIT-042 | R23-P-042 | FLD | 107-FA | TRANSMITTER - PRESSURE -DIAPHRAGM | R23 SAMPLING SYSTEM | 066.0 | SAMPLE CHAMBER PRESSURE | 16024 | 0 to 30 barg | +/- 0.1 barg | SHE | 12 |  |  | I.S |  |  |  |  | HYD | ROSEMOUNT | 3051S2 |  | TI702-SP-5030
R23 | R23-PI-043 | R23-P-043 | FLD | 107-FA | PRESSURE GAUGE | 15-CA-SS1U-9028594 | 066.0 | PI FOR PRV-043 | PKG: N/A; REQ: REQ
R23 | R23-PRV-043 | R23-P-043 | FLD | 107-FA | CONTROL VALVE SELF ACTUATING | 15-CA-SS1U-0-9028594 | 066.0 | PLANT AIR SUPPLY | PKG: N/A
R23 | R23-PRV-044 | R23-P-044 | FLD | 107-FA | CONTROL VALVE SELF ACTUATING | 15-N-SS1U-0-9025185 | 043.3 | NITROGEN SUPPLY | PKG: N/A; -: set @ 0.1 barg |  |  |  |  | ESME | R1440/20
R23 | R23-PI-045 | R23-P-045 | FLD | 107-FA | PRESSURE GAUGE | PKG | 043.3 | NITROGEN SUPPLY | PKG: N/A; -: 0 to 1 barg; -: +/- 1%; REQ: REQ
R23 | R23-PSV-046 | R23-P-046 | FLD | 107-FA | PRESSURE RELIEF VALVE | 15-N-SS1U-0-9025185 | 043.3 | NITROGEN SUPPLY | PKG: N/A; -: set @
R23 | R23-PI-047 | R23-P-047 | FLD | 107-FA | PRESSURE GAUGE | R23 SAMPLER UTILITY PANEL | 066.0 | R23 SAMPLER UTILITY PANEL | PKG: N/A; -: -1 to 30 barg; -: +/- 0.25 barg; REQ: 12
R23 | R23-PI-048 | R23-P-048 | FLD | 107-FA | PRESSURE GAUGE | R23 AGITATOR PRESS. ACC. | 066.0 | AGI SEAL ACCUMULATOR PRESSURE | PKG: N/A; REQ: REQ
R23 | R23-PI-049 | R23-P-049 | FLD | 902-007-002-000-00159 | PRESSURE GAUGE | R24-B01 PACKAGE | 198 | R24-B01 PLANT AIR SUPPLY | PKG: N/A; -: 0 to 6 barg; REQ: REQ
R23 | R23-RO-001 | R23-R-001 | FLD | 107-FB | RESTRICTION ORIFICE PLATE | 15-H-SS3T-0-9025166 | 066.0 | H2 SUPPLY | PKG: N/A; -: <75 Nm3/hr; -: -; REQ: REQ; F: F |  |  | 0 |  | COULTON | N/A | KF0014 |  |  |  | 01
R23 | R23-RO-002 | R23-R-002 | FLD | 107-FA | RESTRICTION ORIFICE PLATE | R23-AG1 HEAT TRAP | 066.0 | R23-AG1 HEAT TRAP CW | PKG: N/A; -: 80 L/hr |  |  |  |  | SITE FABRICATED |  | SITE FAB/3 |  | 3mm orifice |  | 01
R23 | R23-DS-001 | R23-S-001 | MCC | 107-FA | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | AGITATOR | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | HYD | [6 empty] | 01
R23 | R23-DY-001 | R23-S-001 | MCC | 107-FA | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | AGITATOR | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | HYD | [6 empty] | 01
R23 | R23-DYC-001 | R23-S-001 | MCC | 107-FA | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 066.0 | AGITATOR | 8875 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | HYD | [6 empty] | 01
R23 | R23-SAL-001 | R23-S-001 | PCS | 107-FA | ALARM - SPEED - LOW |  |  | AGITATOR | REF: SHE |  |  | 0 | [7 empty] | 01
R23 | R23-SC-001 | R23-S-001 | MCC | 107-FA | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 066.0 | AGITATOR | 8875 | 0 to 1415 rpm | +/- 1% | SHE | 12 | C |  | N.I.S. | AO |  |  | 22 | HYD |  |  |  |  | SET Min @ 142 rpm |  | 01
R23 | R23-SIA-001 | R23-S-001 | [6 empty] | REF: SHE |  |  |  | HYD | PEPPERL + FUCHS | NJ1,5-18GM-N-D |  | TI702-SP-5137
R23 | R23-SIC-001 | R23-S-001 | PCS | 107-FA | INDICATING CONTROLLER - SPEED | PCS | 066.0 | AGITATOR | PKG: 8866; -: 0 to 640 rpm; -: +/- 1%; REF: SHE; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-ST-001 | R23-S-001 | FLD | 107-FA | TRANSMITTER - SPEED | R23 AGITATOR | 066.0 | AGITATOR | 8866 | 0 to 640 rpm | +/- 1% | SHE | REQ | C |  | I.S | AI |  |  | 11 | HYD | PEPPERL + FUCHS | MC |  | TI702-SP-5138 | 4 PULSES per REV |  | 01
R23 | R23-SX-001 | R23-S-001 | MCC | 107-FA | SET MINIMUM SPEED | MOTOR CONTROL CENTRE |  | AGITATOR | REF: SHE; I.S: N.I.S. | DO |  | 42 | SGS | [6 empty] | 01
R23 | R23-TE-001 | R23-T-001 | PKG | 107-FA | ELEMENT - TEMPERATURE - RTD | WITH R23-CV-013 | 066.0 | TEMPERATURE #1 | PKG: 8876; -: -30 to 170 degC; -: +/- 2DegC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R23 | R23-TI-001 | R23-T-001 | PCS | 107-FA | INDICATOR - TEMPERATURE | PCS | 066.0 | TEMPERATURE #1 | PKG: 8876; -: -30 to 170 degC; -: +/- 2DegC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R23 | R23-TT-001 | R23-T-001 | PKG | 107-FA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 066.0 | TEMPERATURE #1 | 8876 | -30 to 170 degC | +/- 2DegC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | HYD | INOR | IPAQ-HX |  | TI702-SP-5027 |  |  | 01
R23 | R23-TE-002 | R23-T-002 | PKG | 107-FA | ELEMENT - TEMPERATURE - RTD | WITH R23-CV-013 | 066.0 | TEMPERATURE #2 | PKG: 8877; -: -30 to 170 degC; -: +/- 2DegC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R23 | R23-TI-002 | R23-T-002 | PCS | 107-FA | INDICATOR - TEMPERATURE | PCS | 066.0 | TEMPERATURE #2 | PKG: 8877; -: -30 to 170 degC; -: +/- 2DegC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R23 | R23-TT-002 | R23-T-002 | PKG | 107-FA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 066.0 | TEMPERATURE #2 | 8877 | -30 to 170 degC | +/- 2DegC | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | HYD | INOR | IPAQ-HX |  | TI702-SP-5027 |  |  | 01
R23 | R23-TE-003 | R23-T-003 | FLD | 107-FA | ELEMENT - TEMPERATURE - RTD | R23/N2/25 | 066.0 | BAFFLE TEMPERATURE | PKG: 8878; -: -30 to 170 degC; -: +/- 2DegC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R23 | R23-TI-003 | R23-T-003 | PCS | 107-FA | INDICATOR - TEMPERATURE | PCS | 066.0 | BAFFLE TEMPERATURE | PKG: 8878; -: -30 to 170 degC; -: +/- 2DegC; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
R23 | R23-TT-003 | R23-T-003 | FLD | 107-FA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 066.0 | BAFFLE TEMPERATURE | 8878 | -30 to 170 degC | +/- 0.5% | GxP/SHE | 12 | C |  | I.S | AI |  |  | 11 | HYD | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5066 |  |  | 01
R23 | R23-TE-004 | R23-T-004 | FLD | 107-FA | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9025110 | 066.0 | VC1 HTF RTN | PKG: 6599; -: -30 to 170 degC; -: +/- 2DegC; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TIC-004 | R23-T-004 | PCS | 107-FA | INDICATING CONTROLLER - TEMPERATURE | PCS | 066.0 | VC1 HTF RTN | PKG: 6599; -: -30 to 170 degC; -: +/- 2DegC; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TT-004 | R23-T-004 | FLD | 107-FA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 066.0 | VC1 HTF RTN | 6599 | -30 to 170 degC | +/- 2DegC | REF | REQ | C |  | I.S | AI |  |  | 11 | HYD | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5066 |  |  | 01
R23 | R23-TE-005 | R23-T-005 | FLD | 107-FA | ELEMENT - TEMPERATURE - RTD | 50-SLP-CS1A-H-9025104 | 066.0 | JACKET SUPPLY TEMP. | PKG: 6600; -: -30 to 170 degC; -: +/- 2DegC; REF: SHE; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TI-005 | R23-T-005 | PCS | 107-FA | INDICATING CONTROLLER - TEMPERATURE | PCS | 066.0 | JACKET SUPPLY TEMP. | PKG: 6600; -: -30 to 170 degC; -: +/- 2DegC; REF: SHE; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TT-005 | R23-T-005 | FLD | 107-FA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 066.0 | JACKET SUPPLY TEMP. | 6600 | -30 to 170 degC | +/- 2DegC | SHE | REQ | C |  | I.S | AI |  |  | 11 | HYD | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5066 |  |  | 01
R23 | R23-TE-006 | R23-T-006 | FLD | 107-FA | ELEMENT - TEMPERATURE - RTD | 50-SLP-CS1A-H-9025102 | 066.0 | JACKET RTN TEMPERATURE | PKG: 6601; -: -30 to 170 degC; -: +/- 2DegC; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TI-006 | R23-T-006 | PCS | 107-FA | INDICATOR - TEMPERATURE | PCS | 066.0 | JACKET RTN TEMPERATURE | PKG: 6601; -: -30 to 170 degC; -: +/- 2DegC; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TT-006 | R23-T-006 | FLD | 107-FA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 066.0 | JACKET RTN TEMPERATURE | 6601 | -30 to 170 degC | +/- 2DegC | REF | REQ | C |  | I.S | AI |  |  | 11 | HYD | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5066 |  |  | 01
R23 | R23-TE-007 | R23-T-007 | FLD | 107-FA | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-H-9025105 | 066.0 | TEMPERED HTF RTN TEMP. | PKG: 6602; -: -30 to 170 degC; -: +/- 2DegC; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TIC-007 | R23-T-007 | PCS | 107-FA | INDICATING CONTROLLER - TEMPERATURE | PCS | 066.0 | TEMPERED HTF RTN TEMP. | PKG: 6602; -: -30 to 170 degC; -: +/- 2DegC; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TT-007 | R23-T-007 | FLD | 107-FA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 066.0 | TEMPERED HTF RTN TEMP. | 6602 | -30 to 170 degC | +/- 2DegC | REF | REQ | C |  | I.S | AI |  |  | 11 | HYD | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5066 |  |  | 01
R23 | R23-TE-008 | R23-T-008 | FLD | 107-FA | ELEMENT - TEMPERATURE - RTD | 50-CWF-CS1B-AC-9028112 | 066.0 | COOLING WATER TEMP. | PKG: 6603; -: 0 to 50 degC; -: +/- 2DegC; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TI-008 | R23-T-008 | PCS | 107-FA | INDICATOR - TEMPERATURE | PCS | 066.0 | COOLING WATER TEMP. | PKG: 6603; -: 0 to 50 degC; -: +/- 2DegC; REQ: REQ |  |  | 0 | [7 empty] | 01
R23 | R23-TT-008 | R23-T-008 | FLD | 107-FA | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 066.0 | COOLING WATER TEMP. | 6603 | 0 to 50 degC | +/- 2DegC | REF | REQ | C |  | I.S | AI |  |  | 11 | HYD | MOORE INDUSTRIES | TRX/PRG | KT0004 | TI702-SP-5024 |  |  | 01
R23 | R23-TE-009 | R23-T-009 | PKG | 107-FA | TEMPERATURE - ELEMENT | R23-AG1 | 066.0 | AGITATOR SEAL TEMPERATURE | 11907 | 0 to 100 degC | +/- 2DegC | SHE | 12 | C | [13 empty] | 01
R23 | R23-TI-009 | R23-T-009 | PCS | 107-FA | TEMPERATURE - INDICATOR | PCS | 066.0 | AGITATOR SEAL TEMPERATURE | PKG: 11907; -: 0 to 100 degC; -: +/- 2DegC; REF: SHE; REQ: 12 | [10 empty] | 01
R23 | R23-TT-009 | R23-T-009 | FLD | 107-FA | TEMPERATURE - TRANSMITTER | ADJ TO R23-AG1 | 066.0 | AGITATOR SEAL TEMPERATURE | 11907 | 0 to 100 degC | +/- 2DegC | SHE | 12 | C |  | I.S |  |  |  |  | HYD |  | RTD |  | TI702-SP-5068 |  |  | 26
R23 | R23-TI-010 | R23-T-010 | FLD | 107-FA | R23-TP1 SEAL POT TEMPERATURE | R23-TP1 SEAL POT | 66 | SEAL OIL TEMPERATURE | REF: SHE; REQ: REQ | [10 empty] | 55
R23 | R23-VI-001 | R23-V-001 | FLD | 107-FA | INDICATOR - VIBRATION | R23 | 066.0 | VIBRATION | PKG: 13066; REQ: REQ |  |  |  |  | BENTLEY NEVADA | [5 empty] | 01
R23 | R23-VIT-001 | R23-V-001 | FLD | 107-FA | TRANSMITTER - VIBRATION | R23 | 066.0 | VIBRATION | PKG: 13066; REQ: REQ |  |  |  |  | BENTLEY NEVADA | 3500 |  |  |  |  | 01
R23 | R23-VE-001A | R23-V-001A | FLD | 107-FA | SENSOR - PROXIMITY | Not shown on P&ID | 066.0 | VIBRATION | PKG: 13065; REQ: REQ |  |  |  |  | BENTLEY NEVADA | 14605-XXX-05-01-05 |  |  |  |  | 01
R23 | R23-VY-001A | R23-V-001A | FLD | 107-FA | PROXIMITOR | Not shown on P&ID | 066.0 | VIBRATION | PKG: 13064; REQ: REQ |  |  |  |  | BENTLEY NEVADA | 330180-X1-05 |  |  |  |  | 01
R23 | R23-VE-001B | R23-V-001B | FLD | 107-FA | SENSOR - PROXIMITY | Not shown on P&ID | 066.0 | VIBRATION | PKG: 13065; REQ: REQ |  |  |  |  | BENTLEY NEVADA | 14605-XXX-05-01-05 |  |  |  |  | 01
R23 | R23-VY-001B | R23-V-001B | FLD | 107-FA | PROXIMITOR | Not shown on P&ID | 066.0 | VIBRATION | PKG: 13064; REQ: REQ |  |  |  |  | BENTLEY NEVADA | 330180-X1-05 |  |  |  |  | 01
R23 | R23-VE-001C | R23-V-001C | FLD | 107-FA | SENSOR - SEISMIC | Not shown on P&ID | 066.0 | VIBRATION | [13 empty] | BENTLEY NEVADA | 330400 |  |  |  |  | 01 | bar: PKG
R23 | R23-VE-001D | R23-V-001D | FLD | 107-FA | SENSOR - SEISMIC | Not shown on P&ID | 066.0 | VIBRATION | [13 empty] | BENTLEY NEVADA | 330400 |  |  |  |  | 01 | bar: PKG
R23 | R23-LI-006 | R23-Y-001 | PKG | 107-FA | INDICATOR - LEVEL | R23 SEAL ASSEMBLY | 066.0 | SEAL SYSTEM COMMON ALARM | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
R23 | R23-YA-001 | R23-Y-001 | PCS | 107-FA | ALARM - COMMON |  |  | SEAL SYSTEM COMMON ALARM | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
R23 | R23-YS-001 | R23-Y-001 | PKG | 107-FA | COMMON ALARM | R23 SEAL ASSEMBLY | 066.0 | SEAL SYSTEM COMMON ALARM | 8849 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | HYD | N/A | N/A |  | TI702-SP-5158 |  |  | 01
R23 | R23-YA-005 | R23-Y-005 | PCS | 107-FA | ALARM - COMMON | PCS | 066.0 | TP1 SEAL POT FAILURE | REF: SHE; REQ: REQ; I.S: I.S |  |  | 0 | HYD | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
R23 | R23-YS-005 | R23-Y-005 | PKG | 107-FA | SWITCH - COMMON ALARM | R23-TP1 SEAL POT | 066.0 | TP1 SEAL POT FAILURE | 8879 | - | - | SHE | REQ | F |  | I.S. | DI |  |  | 32 | HYD | [6 empty] | 01
R24 | R24-AE-001 | R24-A-001 | FLD | 902-007-002-000-00159 | ELEMENT - O2 DETECTOR | 3rd FLR PLANT ROOM | 198.0 | O2 LEAK N2 CYLINDER STORE | -: 0 to 25% LEL; -: +/- 5%; REF: SHE; REQ: 12; F: C | [11 empty] | v0.1
R24 | R24-AI-001 | R24-A-001 | FLD | 902-007-002-000-00159 | ELEMENT - O2 INDICATOR | 3rd FLR PLANT ROOM | 198.0 | O2 LEAK N2 CYLINDER STORE | -: 0 to 25% LEL; -: +/- 5%; REF: SHE; REQ: 12; F: C | [11 empty] | v0.1
R24 | R24-AE-002A | R24-A-002 | FLD | 902-007-002-000-00220 | ELEMENT - H2 DETECTOR | HYDROGENATOR ROOM | 198.0 | H2 LEAK HYDROG ROOM VENT | -: 0 to 50% LEL; -: +/- 5%; REF: SHE; REQ: 6; F: C | [11 empty] | v0.1
R24 | R24-AI-002A | R24-A-002 | PCS | 902-007-002-000-00220 | ELEMENT- H2 INDICATOR | PCS | 198.0 | H2 LEAK HYDROG ROOM VENT | -: 0 to 50% LEL; -: +/- 5%; REF: SHE; REQ: 6; F: C | [11 empty] | v0.1
R24 | R24-AT-002A | R24-A-002 | CPR | 902-007-002-000-00220 | TRANSMITTER - H2 %LEL | MISC EQUIP. PANEL | 198.0 | H2 LEAK HYDROG ROOM VENT |  | 0 to 50% LEL | +/- 5% | SHE | 6 | C |  | I.S. | AI | [11 empty] | v0.1
R24 | R24-ASH-002A | R24-A-002 | CPR | 902-007-002-000-00220 | SWITCH - LEVEL - HIGH | MISC EQUIP. PANEL | 198.0 | H2 LEAK HYDROG ROOM VENT | -: set @ 10% LEL; -: +/- 1%; REF: SHE; REQ: 6; F: F | [11 empty] | v0.1
R24 | R24-AE-002B | R24-A-002 | FLD | 902-007-002-000-00220 | ELEMENT - H2 DETECTOR | HYDROGENATOR ROOM | 198.0 | H2 LEAK HYDROG ROOM VENT | -: 0 to 50% LEL; -: +/- 5%; REF: SHE; REQ: 6; F: C | [11 empty] | v0.1
R24 | R24-AI-002B | R24-A-002 | PCS | 902-007-002-000-00220 | ELEMENT- H2 INDICATOR | PCS | 198.0 | H2 LEAK HYDROG ROOM VENT | -: 0 to 50% LEL; -: +/- 5%; REF: SHE; REQ: 6; F: C | [11 empty] | v0.1
R24 | R24-AT-002B | R24-A-002 | CPR | 902-007-002-000-00220 | TRANSMITTER - H2 %LEL | MISC EQUIP. PANEL | 198.0 | H2 LEAK HYDROG ROOM VENT |  | 0 to 50% LEL | +/- 5% | SHE | 6 | C |  | I.S. | AI | [11 empty] | v0.1
R24 | R24-ASH-002B | R24-A-002 | CPR | 902-007-002-000-00220 | SWITCH - LEVEL - HIGH | MISC EQUIP. PANEL | 198.0 | H2 LEAK HYDROG ROOM VENT | -: set @ 10% LEL; -: +/- 1%; REF: SHE; REQ: 6; F: F | [11 empty] | v0.1
R24 | R24-AE-002C | R24-A-002 | FLD | 902-007-002-000-00220 | ELEMENT - H2 DETECTOR | HYDROGENATOR ROOM | 198.0 | H2 LEAK HYDROG ROOM VENT | -: 0 to 50% LEL; -: +/- 5%; REF: SHE; REQ: 6; F: C | [11 empty] | v0.1
R24 | R24-AI-002C | R24-A-002 | PCS | 902-007-002-000-00220 | ELEMENT- H2 INDICATOR | PCS | 198.0 | H2 LEAK HYDROG ROOM VENT | -: 0 to 50% LEL; -: +/- 5%; REF: SHE; REQ: 6; F: C | [11 empty] | v0.1
R24 | R24-AT-002C | R24-A-002 | CPR | 902-007-002-000-00220 | TRANSMITTER - H2 %LEL | MISC EQUIP. PANEL | 198.0 | H2 LEAK HYDROG ROOM VENT |  | 0 to 50% LEL | +/- 5% | SHE | 6 | C |  | I.S. | AI | [11 empty] | v0.1
R24 | R24-ASH-002C | R24-A-002 | CPR | 902-007-002-000-00220 | SWITCH - LEVEL - HIGH | MISC EQUIP. PANEL | 198.0 | H2 LEAK HYDROG ROOM VENT | -: set @ 10% LEL; -: +/- 1%; REF: SHE; REQ: 6; F: F | [11 empty] | v0.1
R24 | R24-ASH-002 | R24-A-002 | PCS | 902-007-002-000-00220 | ALARM - STATUS | PCS | 198.0 | H2 LEAK HYDROG ROOM VENT COMMON ALARM | REF: SHE; REQ: 6; F: F | [11 empty] | v0.1
R24 | R24-ASH-002 | R24-A-002 | CPR | 902-007-002-000-00220 | SWITCH - ALARM - COMMON | MISC EQUIP. PANEL | 198.0 | H2 LEAK HYDROG ROOM VENT COMMON ALARM | REF: SHE; REQ: 6; F: F; DI: DI | [11 empty] | v0.1
R24 | R24-CV-001 | R24-C-001 | FLD | 902-007-002-000-00219 | BALL VALVE - ON/OFF - F.C. | 10-H-E2E-0-9025835 | 198.0 | BT03 HYDROGEN SUPPLY | [20 empty] | v0.1 | bar: PKG
R24 | R24-CY-001 | R24-C-001 | CPR | 902-007-002-000-00219 | SOLENOID VALVE | PLC CONTROL PANEL | 198.0 | BT03 HYDROGEN SUPPLY | I.S: I.S |  | DO | [9 empty] | v0.1
R24 | R24-ZSC-001 | R24-C-001 | FLD | 902-007-002-000-00219 | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 198.0 | BT03 HYDROGEN SUPPLY | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-ZSO-001 | R24-C-001 | FLD | 902-007-002-000-00219 | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 198.0 | BT03 HYDROGEN SUPPLY | I.S: I.S |  | DI | [9 empty] | v0.1
R24 |  | R24-C-002 | [26 empty] | v0.3 | bar: PKG
R24 | R24-CV-003 | R24-C-003 | FLD | 902-007-002-000-00219 | CONTROL VALVE | 10-H-E2E-0-9025849 | 198.0 | BT03 OUTLET ISOLATION VALVE | REF: SHE; REQ: 24; F: F | [11 empty] | v0.3
R24 | R24-CY-003 | R24-C-003 | FLD | 902-007-002-000-00219 | SOLENOID VALVE | 10-H-E2E-0-9025849 | 198.0 | BT03 OUTLET ISOLATION VALVE | REF: SHE; REQ: 24; F: F; I.S: I.S |  | DO | [9 empty] | v0.1
R24 | R24-CV-004 | R24-C-004 | FLD | 902-007-002-000-00221 | BALL VALVE - ON/OFF - F.C. | 10-H-E2E-0-9025887 | 198.0 | BT04 INLET VALVE | REF: SHE; REQ: 24; F: F | [11 empty] | v0.3
R24 | R24-CY-004 | R24-C-004 | CPR | 902-007-002-000-00221 | SOLENOID VALVE | PLC CONTROL PANEL | 198.0 | BT04 INLET VALVE | REF: SHE; REQ: 24; F: F; I.S: I.S |  | DO | [9 empty] | v0.1
R24 | R24-ZSC-004 | R24-C-004 | FLD | 902-007-002-000-00221 | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 198.0 | BT04 INLET VALVE | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-ZSO-004 | R24-C-004 | FLD | 902-007-002-000-00221 | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 198.0 | BT04 INLET VALVE | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-CV-005 | R24-C-005 | FLD | 902-007-002-000-00221 | BALL VALVE - ON/OFF - F.C. | 25-P-A2E-0-9025888 | 198.0 | BT04 OUTLET VALVE | [20 empty] | v0.3 | bar: PKG
R24 | R24-CY-005 | R24-C-005 | CPR | 902-007-002-000-00221 | SOLENOID VALVE | PLC CONTROL PANEL | 198.0 | BT04 OUTLET VALVE | I.S: I.S |  | DO | [9 empty] | v0.1
R24 | R24-ZSC-005 | R24-C-005 | FLD | 902-007-002-000-00221 | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 198.0 | BT04 OUTLET VALVE | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-ZSO-005 | R24-C-005 | FLD | 902-007-002-000-00221 | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 198.0 | BT04 OUTLET VALVE | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-CV-006 | R24-C-006 | FLD | 902-007-002-000-00219 | CONTROL VALVE | 10-P-E2E-0-9025845 | 198.0 | MP01 FEED VALVE | REF: SHE; REQ: 24; F: F | [11 empty] | v0.3
R24 | R24-CY-006 | R24-C-006 | CPR | 902-007-002-000-00219 | BALL VALVE - ON/OFF - F.C. | PLC CONTROL PANEL | 198.0 | MP01 FEED VALVE | REF: SHE; REQ: 24; F: F; I.S: I.S |  | DO | [9 empty] | v0.1
R24 | R24-ZSC-006 | R24-C-006 | FLD | 902-007-002-000-00219 | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 198.0 | MP01 FEED VALVE | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-ZSO-006 | R24-C-006 | FLD | 902-007-002-000-00219 | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 198.0 | MP01 FEED VALVE | I.S: I.S |  | DI | [9 empty] | v0.1
R24 |  | R24-C-007 | [26 empty] | v0.3 | bar: PKG
R24 | R24-CV-008 | R24-C-008 | FLD | 902-007-002-000-00221 | CONTROL VALVE | 10-P-E2E-0-9025891 | 198.0 | SE01 VENT ISOLATION VALVE | REF: SHE; REQ: 24; F: F | [11 empty] | v0.3
R24 | R24-CY-008 | R24-C-008 | FLD | 902-007-002-000-00221 | SOLENOID VALVE | 10-P-E2E-0-9025891 | 198.0 | SE01 VENT ISOLATION VALVE | REF: SHE; REQ: 24; F: F; I.S: I.S |  | DO | [9 empty] | v0.1
R24 |  | R24-C-009 | [26 empty] | v0.3 | bar: PKG
R24 | R24-CV-010 | R24-C-010 | FLD | 902-007-002-000-00219 | BALL VALVE - ON/OFF - F.C. | 10-N-E2E-0-9025830 | 198.0 | BT03 NITROGEN SUPPLY | [20 empty] | v0.3 | bar: PKG
R24 | R24-CY-010 | R24-C-010 | CPR | 902-007-002-000-00219 | SOLENOID VALVE | PLC CONTROL PANEL | 198.0 | BT03 NITROGEN SUPPLY | I.S: I.S |  | DO | [9 empty] | v0.1
R24 | R24-ZSC-010 | R24-C-010 | FLD | 902-007-002-000-00219 | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 198.0 | BT03 NITROGEN SUPPLY | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-ZSO-010 | R24-C-010 | FLD | 902-007-002-000-00219 | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 198.0 | BT03 NITROGEN SUPPLY | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-CV-012 | R24-C-012 | FLD | 902-007-002-000-00219 | BALL VALVE - ON/OFF - F.C. | 10-P-E2E-0-9025844 | 198.0 | BT01 OUTLET VALVE | [20 empty] | v0.3 | bar: PKG
R24 | R24-CY-012 | R24-C-012 | CPR | 902-007-002-000-00219 | SOLENOID VALVE | PLC CONTROL PANEL | 198.0 | BT01 OUTLET VALVE | I.S: I.S |  | DO | [9 empty] | v0.1
R24 | R24-ZSC-012 | R24-C-012 | FLD | 902-007-002-000-00219 | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 198.0 | BT01 OUTLET VALVE | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-ZSO-012 | R24-C-012 | FLD | 902-007-002-000-00219 | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 198.0 | BT01 OUTLET VALVE | I.S: I.S |  | DI | [9 empty] | v0.1
R24 |  | R24-C-013 | [26 empty] | v0.3 | bar: PKG
R24 | R24-FIC-001 | R24-F-001 | PLC | 902-007-002-000-00219 | FLOW INIDICATOR |  | 198.0 | MP01 FLOWRATE | -: 0 to 40 l/hr; -: +/- 2% | [11 empty] | v0.1
R24 | R24-FT-001 | R24-F-001 | FLD | 902-007-002-000-00219 | TRANSMITTER - FLOW | 10-P-E2E-0-9025845 | 198.0 | MP01 FLOWRATE | -: 0 to 40 l/hr; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 |  | R24-F-002 | [26 empty] | v0.1 | bar: PKG
R24 | R24-FI-003 | R24-F-003 | PLC | 902-007-002-000-00219 | FLOW INIDICATOR |  | 198.0 | HYDROGEN FLOWRATE | -: 0 to 30 N.l/min; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-FIC-003 | R24-F-003 | FLD | 902-007-002-000-00219 | INDICATING CONTROLLER - FLOW | 10-H-E2E-0-9025849 | 198.0 | HYDROGEN FLOWRATE | -: 0 to 30 N.l/min; -: +/- 5%; REF: SHE; REQ: 24 |  |  |  |  | Bronkhorst Flexi-flow Compact | [6 empty] | v0.1
R24 | R24-FT-003 | R24-F-003 | FLD | 902-007-002-000-00219 | TRANSMITTER - FLOW | 10-H-E2E-0-9025849 | 198.0 | HYDROGEN FLOWRATE | -: 0 to 30 N.l/min; -: +/- 5%; REF: SHE; REQ: 24; I.S: I.S |  | Comms |  |  | Bronkhorst Flexi-flow Compact | [6 empty] | v0.1
R24 | R24-FCV-003 | R24-F-003 | FLD | 902-007-002-000-00219 | CONTROL VALVE | 10-H-E2E-0-9025849 | 198.0 | HYDROGEN FLOWRATE | -: 0 to 30 N.l/min; -: +/- 5%; REF: SHE; REQ: 24; I.S: I.S |  | Comms |  |  | Bronkhorst Flexi-flow Compact | [6 empty] | v0.1
R24 | R24-FI-004 | R24-F-004 | PLC | 902-007-002-000-00221 | FLOW INIDICATOR |  | 198.0 | PRODUCT TANK INLET FLOW | -: 0 to 40 l/hr; -: +/- 2%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-FIC-004 | R24-F-004 | FLD | 902-007-002-000-00221 | INDICATING CONTROLLER - FLOW | 10-H-E2E-0-9025887 | 198.0 | PRODUCT TANK INLET FLOW | -: 0 to 40 l/hr; -: +/- 2%; REF: SHE; REQ: 24 |  |  |  |  | Bronkhorst Flow Controller | [6 empty] | v0.1
R24 | R24-FT-004 | R24-F-004 | FLD | 902-007-002-000-00221 | TRANSMITTER - FLOW | 10-H-E2E-0-9025887 | 198.0 | PRODUCT TANK INLET FLOW | -: 0 to 40 l/hr; -: +/- 2%; REF: SHE; REQ: 24; I.S: I.S |  | Comms |  |  | Bronkhorst Flow Controller | [6 empty] | v0.1
R24 | R24-FCV-004 | R24-F-004 | FLD | 902-007-002-000-00221 | CONTROL VALVE | 10-H-E2E-0-9025887 | 198.0 | PRODUCT TANK INLET FLOW | -: 0 to 40 l/hr; -: +/- 2%; REF: SHE; REQ: 24; I.S: I.S |  | Comms |  |  | Bronkhorst Flow Controller | [6 empty] | v0.1
R24 | R24-FI-005 | R24-F-005 | PLC | 902-007-002-000-00219 | FLOW INIDICATOR |  | 198.0 | N2 SWEEP TO BT01 | -: 0 to 40 N.l/min; -: +/- 5% | [11 empty] | v0.1
R24 | R24-FIC-005 | R24-F-005 | FLD | 902-007-002-000-00219 | INDICATING CONTROLLER - FLOW | 15-N-A3E-0-9025837 | 198.0 | N2 SWEEP TO BT01 | -: 0 to 40 N.l/min; -: +/- 5% |  |  |  |  | Bronkhorst Flow Controller | [6 empty] | v0.1
R24 | R24-FT-005 | R24-F-005 | FLD | 902-007-002-000-00219 | TRANSMITTER - FLOW | 15-N-A3E-0-9025837 | 198.0 | N2 SWEEP TO BT01 | -: 0 to 40 N.l/min; -: +/- 5%; I.S: I.S |  | Comms |  |  | Bronkhorst Flow Controller | [6 empty] | v0.1
R24 | R24-FCV-005 | R24-F-005 | FLD | 902-007-002-000-00219 | CONTROL VALVE | 15-N-A3E-0-9025837 | 198.0 | N2 SWEEP TO BT01 | -: 0 to 40 N.l/min; -: +/- 5%; I.S: I.S |  | Comms |  |  | Bronkhorst Flow Controller | [6 empty] | v0.1
R24 |  | R24-F-006 | [26 empty] | v0.3 | bar: PKG
R24 | R24-FI-007 | R24-F-007 | PLC | 902-007-002-000-00221 | FLOW INIDICATOR |  | 198.0 | N2 SWEEP TO BT04 | -: 0 to 40 N.l/min; -: +/- 5% | [11 empty] | v0.1
R24 | R24-FIC-007 | R24-F-007 | FLD | 902-007-002-000-00221 | INDICATING CONTROLLER - FLOW | 15-N-A3E-0-9025838 | 198.0 | N2 SWEEP TO BT04 | -: 0 to 40 N.l/min; -: +/- 5% |  |  |  |  | Bronkhorst Flow Controller | [6 empty] | v0.1
R24 | R24-FT-007 | R24-F-007 | FLD | 902-007-002-000-00221 | TRANSMITTER - FLOW | 15-N-A3E-0-9025838 | 198.0 | N2 SWEEP TO BT04 | -: 0 to 40 N.l/min; -: +/- 5%; I.S: I.S |  | Comms |  |  | Bronkhorst Flow Controller | [6 empty] | v0.1
R24 | R24-FCV-007 | R24-F-007 | FLD | 902-007-002-000-00221 | CONTROL VALVE | 15-N-A3E-0-9025838 | 198.0 | N2 SWEEP TO BT04 | -: 0 to 40 N.l/min; -: +/- 5%; I.S: I.S |  | Comms |  |  | Bronkhorst Flow Controller | [6 empty] | v0.1
R24 | R24-FI-008 | R24-F-008 | FLD | 902-007-002-000-00159 | INDICATOR - FLOW | 15-N-A1E-0-9025831 | 198.0 | N2 SWEEP TO RELIEF VENT | -: 0 to 10 N.l/min; -: +/- 5%; REF: SHE; REQ: 24; F: F | [11 empty] | v0.1
R24 | R24-FAL-008 | R24-F-008 | PCS | 902-007-002-000-00159 | FLOW INDICATOR - SWITCH LOW | 15-N-A1E-0-9025831 | 198.0 | N2 SWEEP TO RELIEF VENT |  | Set at 5 N l/min | +/- 5% | SHE | 24 | F |  |  | DI | [11 empty] | v0.1
R24 | R24-FI-009 | R24-F-009 | FLD | 902-007-002-000-00159 | INDICATOR - FLOW | 15-N-A1E-0-9025833 | 198.0 | N2 SWEEP TO PROCESS VENT | -: 0 to 10 N.l/min; -: +/- 5%; REF: SHE; REQ: 24; F: F | [11 empty] | v0.1
R24 | R24-FAL-009 | R24-F-009 | PCS | 902-007-002-000-00159 | FLOW INDICATOR - SWITCH LOW | 15-N-A1E-0-9025833 | 198.0 | N2 SWEEP TO PROCESS VENT |  | Set at 5 N l/min | +/- 5% | SHE | 24 | F |  |  | DI | [11 empty] | v0.1
R24 | R24-HS-001 | R24-H-001 | FLD | 902-007-002-000-00220 | SWITCH - PROCESS STOP | R24 SKID | 198.0 | ESD PUSH BUTTON | REF: SHE; REQ: 24; F: F | [11 empty] | v0.1
R24 | R24-HS-001A | R24-H-001 | PLC | 902-007-002-000-00220 | ALARM - STATUS | PLC | 198.0 | R24 PROCESS STOP | I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-HS-001B | R24-H-001 | FLD | 902-007-002-000-00220 | ALARM - STATUS | R24 SKID | 198.0 | TCU CRASH COOL VFC | REF: SHE; REQ: 24; F: F | [11 empty] | v0.1
R24 | R24-LI-001 | R24-L-001 | PLC | 902-007-002-000-00219 | INDICATOR - LEVEL |  | 198.0 | BT01 LEVEL |  | 0 to 300 ltrs | +/- 2% | SHE | 24 | C |  | I.S |  |  | AI | [9 empty] | v0.1
R24 | R24-LIT-001 | R24-L-001 | FLD | 902-007-002-000-00219 | TRANSMITTER - LEVEL | BT01 | 198.0 | BT01 LEVEL | -: 0 to 300 ltrs; -: +/- 2%; REF: SHE; REQ: 24; F: C | [11 empty] | v0.1
R24 |  | R24-L-002 | [26 empty] | v0.1 | bar: PKG
R24 | R24-LIC-003 | R24-L-003 | PLC | 902-007-002-000-00221 | INDICATING CONTROLLER - LEVEL | R24-SE01 | 198.0 | SE01 LEVEL |  | 0 to 20 ltrs | +/- 2% | SHE | 24 | C |  | I.S |  |  | AI | [9 empty] | v0.1
R24 | R24-LIT-003 | R24-L-003 | FLD | 902-007-002-000-00221 | TRANSMITTER - LEVEL | R24-SE01 | 198.0 | SE01 LEVEL | -: 0 to 20 ltrs; -: +/- 2%; REF: SHE; REQ: 24; F: C |  |  |  |  | Emerson 5300 GWRT | [6 empty] | v0.1
R24 | R24-LIC-004 | R24-L-004 | PLC | 902-007-002-000-00221 | INDICATOR - LEVEL |  | 198.0 | BT04 LEVEL |  | 0 to 300 ltrs | +/- 2% | SHE | 24 | C |  | I.S |  |  | AI | [9 empty] | v0.1
R24 | R24-LIT-004 | R24-L-004 | FLD | 902-007-002-000-00221 | TRANSMITTER - LEVEL | BT04 | 198.0 | BT04 LEVEL | -: 0 to 300 ltrs; -: +/- 2%; REF: SHE; REQ: 24; F: C | [11 empty] | v0.1
R24 | R24-LAL-005 | R24-L-005 | PLC | 902-007-002-000-00221 | SWITCH - LEVEL - LOW |  | 198.0 | SE01 LEVEL LOW | REF: SHE; REQ: 24; F: F | [11 empty] | v0.1
R24 | R24-LSL-005 | R24-L-005 | FLD | 902-007-002-000-00221 | SWITCH - LEVEL - LOW | R24-SE01 | 198.0 | SE01 LEVEL LOW | REF: SHE; REQ: 24; F: F; I.S: I.S |  | DI | [9 empty] | v0.1
R24 | R24-LAH-006 | R24-L-006 | PLC | 902-007-002-000-00221 | SWITCH - LEVEL - HIGH |  | 198.0 | SE01 LEVEL HIGH | REF: SHE; REQ: 24; F: F | [11 empty] | v0.1
R24 | R24-LSH-006 | R24-L-006 | FLD | 902-007-002-000-00221 | SWITCH - LEVEL - HIGH | R24-SE01 | 198.0 | SE01 LEVEL HIGH | REF: SHE; REQ: 24; F: F; I.S: I.S |  | DI | [9 empty] | v0.1
R24 |  | R24-L-007 |  |  |  |  | 198.0 | [21 empty] | v0.3 | bar: PKG
R24 | R24-PI-001 | R24-P-001 | PLC | 902-007-002-000-00219 | INDICATOR - PRESSURE |  | 198.0 | BT03 PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PIT-001 | R24-P-001 | FLD | 902-007-002-000-00219 | TRANSMITTER - PRESSURE | BT03 | 198.0 | BT03 PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PI-002 | R24-P-002 | PLC | 902-007-002-000-00220 | INDICATOR - PRESSURE |  | 198.0 | CR01 INLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PT-002 | R24-P-002 | FLD | 902-007-002-000-00220 | TRANSMITTER - PRESSURE | 10-H-E2E-D-9025850 | 198.0 | CR01 INLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PI-003 | R24-P-003 | PLC | 902-007-002-000-00219 | INDICATOR - PRESSURE |  | 198.0 | METERING PUMP OUTLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PT-003 | R24-P-003 | PLC | 902-007-002-000-00219 | TRANSMITTER - PRESSURE | 10-P-E2E-0-9025845 | 198.0 | METERING PUMP OUTLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PI-004 | R24-P-004 | PLC | 902-007-002-000-00220 | INDICATOR - PRESSURE |  | 198.0 | CR01 PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PIT-004 | R24-P-004 | FLD | 902-007-002-000-00220 | TRANSMITTER - PRESSURE | R24-CR01 | 198.0 | CR01 PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PI-005 | R24-P-005 | PLC | 902-007-002-000-00220 | INDICATOR - PRESSURE |  | 198.0 | CR01 OUTLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PT-005 | R24-P-005 | FLD | 902-007-002-000-00220 | TRANSMITTER - PRESSURE | 10-P-E2E-D-9025861 | 198.0 | CR01 OUTLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PI-006 | R24-P-006 | PLC | 902-007-002-000-00220 | INDICATOR - PRESSURE |  | 198.0 | CR02 PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PIT-006 | R24-P-006 | FLD | 902-007-002-000-00220 | TRANSMITTER - PRESSURE | R24-CR02 | 198.0 | CR02 PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PI-007 | R24-P-007 | PLC | 902-007-002-000-00220 | INDICATOR - PRESSURE |  | 198.0 | CR02 OUTLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PT-007 | R24-P-007 | FLD | 902-007-002-000-00220 | TRANSMITTER - PRESSURE | 10-P-E2E-D-9025863 | 198.0 | CR02 OUTLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PI-008 | R24-P-008 | PLC | 902-007-002-000-00220 | INDICATOR - PRESSURE |  | 198.0 | CR03 PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PIT-008 | R24-P-008 | FLD | 902-007-002-000-00220 | TRANSMITTER - PRESSURE | R24-CR03 | 198.0 | CR03 PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PI-009 | R24-P-009 | PLC | 902-007-002-000-00220 | INDICATOR - PRESSURE |  | 198.0 | CR03 OUTLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [8 empty] | PIT Position is 'Reactor Outlet' - Check |  |  | v0.1
R24 | R24-PT-009 | R24-P-009 | FLD | 902-007-002-000-00220 | TRANSMITTER - PRESSURE | 10-P-E2E-D-9025864 | 198.0 | CR03 OUTLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PDI-010 | R24-P-010 | PLC | 902-007-002-000-00221 | INDICATOR - PRESSURE |  | 198.0 | FILTER DIFFERENTIAL PRESSURE | -: 0 to 1000 mbarg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PDIT-010 | R24-P-010 | FLD | 902-007-002-000-00221 | TRANSMITTER - PRESSURE | 10-P-E2E-D-9025860 | 198.0 | FILTER DIFFERENTIAL PRESSURE | -: 0 to 1000 mbarg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 |  | R24-P-011 | [23 empty] | PSV Deleted |  |  | v0.4 | bar: PKG
R24 |  | R24-P-012 | [26 empty] | v0.1 | bar: PKG
R24 | R24-PSV-013 | R24-P-013 | FLD | 902-007-002-000-00219 | PRESSURE SAFETY VALVE | xx-RV-E1E-0-9025847 | 198.0 | BT03 PRESSURE SAFETY VALVE | -: set @ 80.0 barg; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-PI-014 | R24-P-014 | PLC | 902-007-002-000-00221 | INDICATOR - PRESSURE |  | 198.0 | BT04 PRESSURE | -: 0 to 6.0 barg; -: +/- 2%; REF: SHE; REQ: 12; F: C | [11 empty] | v0.1
R24 | R24-PIT-014 | R24-P-014 | FLD | 902-007-002-000-00221 | TRANSMITTER - PRESSURE | R24-BT04 | 198.0 | BT04 PRESSURE |  | 0 to 6.0 barg | +/- 2% | SHE | 12 | C |  | I.S |  |  | AI | [9 empty] | v0.1
R24 | R24-PSV-015 | R24-P-015 | FLD | 902-007-002-000-00219 | PRESSURE SAFETY VALVE | R24-MP01 | 198.0 | MP01 PRESSURE SAFETY VALVE | -: set @ 80.0 barg; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 |  | R24-P-016 | [26 empty] | v0.1 | bar: PKG
R24 |  | R24-P-017 | [26 empty] | v0.1 | bar: PKG
R24 | R24-PSV-018 | R24-P-018 | FLD | 902-007-002-000-00221 | PRESSURE SAFETY VALVE | 15-SV-A2E-0-9025889 | 198.0 | BT04 PRESSURE SAFETY VALVE | -: set @ 2.0 barg; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-PSV-019 | R24-P-019 | PLC | 902-007-002-000-00221 | PRESSURE SAFETY VALVE | xx-P-E2E-0-9025893 | 198.0 | SE01 PRESSURE SAFETY VALVE | -: set @ 80.0 barg; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-PI-020 | R24-P-020 | PLC | 902-007-002-000-00219 | INDICATOR - PRESSURE |  | 198.0 | BT01 PRESSURE | -: 0 to 6.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PIT-020 | R24-P-020 | FLD | 902-007-002-000-00219 | TRANSMITTER - PRESSURE | BT01 | 198.0 | BT01 PRESSURE | -: 0 to 6.0 barg; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 |  | R24-P-021 | [26 empty] | v0.1 | bar: PKG
R24 | R24-PSV-022 | R24-P-022 | FLD | 902-007-002-000-00220 | PRESSURE SAFETY VALVE | xx-P-E2E-D-9025854 | 198.0 | CR01 PRESSURE SAFETY VALVE | -: set @ 80.0 barg; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-PSV-023 | R24-P-023 | FLD | 902-007-002-000-00220 | PRESSURE SAFETY VALVE | xx-P-E2E-D-9025856 | 198.0 | CR02 PRESSURE SAFETY VALVE | -: set @ 80.0 barg; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-PSV-024 | R24-P-024 | FLD | 902-007-002-000-00220 | PRESSURE SAFETY VALVE | xx-P-E2E-D-9025858 | 198.0 | CR03 PRESSURE SAFETY VALVE | -: set @ 80.0 barg; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-PSV-025 | R24-P-025 | FLD | 902-007-002-000-00221 | PRESSURE SAFETY VALVE | xx-P-E2E-D-9025895 | 198.0 | CU01 PRESSURE SAFETY VALVE | -: set @ 80.0 barg; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 |  | R24-P-026 | [26 empty] | v0.1 | bar: PKG
R24 | R24-PI-027 | R24-P-027 | PLC | 902-007-002-000-00221 | INDICATOR - PRESSURE |  | 198.0 | SE01 PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; REF: SHE; REQ: 12; F: C | [11 empty] | v0.1
R24 | R24-PT-027 | R24-P-027 | FLD | 902-007-002-000-00221 | TRANSMITTER - PRESSURE | 10-P-E2E-0-9025891 | 198.0 | SE01 PRESSURE |  | 0 to 80.0 barg | +/- 2% | SHE | 12 | C |  | I.S |  |  | AI | [9 empty] | v0.1
R24 | R24-PSH-027 | R24-P-027 | CPR | 902-007-002-000-00221 | SWITCH - PRESSURE - HIGH | PLC CONTROL PANEL | 198.0 | SE01 PRESSURE | -: set @ 6.0 barg; -: +/- 5%; REF: SHE; REQ: 12; F: F | [11 empty] | v0.1
R24 | R24-PAH-027 | R24-P-027 | CPR | 902-007-002-000-00221 | SWITCH - PRESSURE - HIGH | PLC CONTROL PANEL | 198.0 | SE01 PRESSURE | REF: SHE; REQ: 12; F: F | [11 empty] | v0.4
R24 | R24-PI-028 | R24-P-028 | PLC | 902-007-002-000-00221 | INDICATOR - PRESSURE |  | 198.0 | SYSTEM BACK PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; REF: SHE; REQ: 12 | [11 empty] | v0.1
R24 | R24-PIC-028 | R24-P-028 | PLC | 902-007-002-000-00221 | INDICATING CONTROLLER - PRESSURE | 10-P-E2E-0-9025891 | 198.0 | SYSTEM BACK PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; REF: SHE; REQ: 12 | [11 empty] | v0.1
R24 | R24-PT-028 | R24-P-028 | FLD | 902-007-002-000-00221 | TRANSMITTER - PRESSURE | 10-P-E2E-0-9025891 | 198.0 | SYSTEM BACK PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; REF: SHE; REQ: 12; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-PC-028 | R24-P-028 | PLC | 902-007-002-000-00221 | CONTROL VALVE | 10-P-E2E-0-9025891 | 198.0 | SYSTEM BACK PRESSURE | -: 0 to 80.0 barg; -: +/- 2%; REF: SHE; REQ: 12; I.S: I.S |  | AO | [9 empty] | v0.1
R24 | R24-PSV-029 | R24-P-029 | FLD | 902-007-002-000-00221 | PRESSURE SAFETY VALVE | xx-RV-A2E-0-9025878 | 198.0 | PROCESS VENT RELIEF | -: set @ 0.5 barg; -: +/- 5%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-PI-030 | R24-P-030 | PLC | 902-007-002-000-00221 | PRESSURE INIDICATOR |  |  | SE01 OUTLET PRESSURE REDUCER | [20 empty] | v0.4 | bar: PKG
R24 | R24-PIC-030 | R24-P-030 | FLD | 902-007-002-000-00221 | INDICATING CONTROLLER - PRESSURE | 10-H-E2E-0-9025887 | 198.0 | SE01 OUTLET PRESSURE REDUCER | -: set @ 4.0 barg; -: +/- 5% |  |  |  |  | Bronkhorst Pressure Controller | [6 empty] | v0.4
R24 | R24-PT-030 | R24-P-030 | FLD | 902-007-002-000-00221 | TRANSMITTER - PRESSURE | 10-H-E2E-0-9025887 | 198.0 | SE01 OUTLET PRESSURE REDUCER | -: 0 to 80.0 barg; -: +/- 2%; I.S: I.S. |  | Comms |  |  | Bronkhorst Pressure Controller | [6 empty] | v0.4
R24 | R24-PCV-030 | R24-P-030 | FLD | 902-007-002-000-00221 | CONTROL VALVE | 10-H-E2E-0-9025887 | 198.0 | SE01 OUTLET PRESSURE REDUCER | I.S: I.S. |  | Comms |  |  | Bronkhorst Pressure Controller | [6 empty] | v0.4
R24 | R24-PI-032 | R24-P-032 | FLD | 902-007-002-000-00159 | PRESSURE GAUGE - DIAPHRAGM | R24-B01 | 198.0 | B01 HYDROGEN INLET PRESSURE | -: 0 to 30.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PI-033 | R24-P-033 | FLD | 902-007-002-000-00159 | PRESSURE GAUGE - DIAPHRAGM | R24-B01 | 198.0 | B01 OUTLET AIR PILOT PRESSURE | -: 0 to 6.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PI-034 | R24-P-034 | FLD | 902-007-002-000-00159 | PRESSURE GAUGE - DIAPHRAGM | R24-B01 | 198.0 | B01 OUTLET PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PI-035 | R24-P-035 | FLD | 902-007-002-000-00159 | PRESSURE GAUGE - DIAPHRAGM | R24-B01 | 198.0 | B01 COMPRESSED AIR CONTROL PRESSURE INDICATOR | -: 0 to 6.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PRV-036 | R24-P-036 | FLD | 902-007-002-000-00159 | PRESSURE REDUCING VALVE | R24-B01 | 198.0 | B01 COMPRESSED AIR CONTROL PRESSURE | -: set @ 5.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PRV-037 | R24-P-037 | FLD | 902-007-002-000-00159 | PRESSURE REDUCING VALVE | R24-B01 | 198.0 | B01 OUTLET AIR PILOT CONTROL PRESSURE | -: set @ x.x barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PRV-038 | R24-P-038 | FLD | 902-007-002-000-00159 | PRESSURE SAFETY VALVE | R24-B01 | 198.0 | B01 PRESSURE SAFETY VALVE | -: set @ 77.0 barg; -: +/- 10% | [11 empty] | v0.1
R24 | R24-PI-039 | R24-P-039 | FLD | 902-007-002-000-00159 | PRESSURE GAUGE - DIAPHRAGM | 10-N-E2E-0-9025830 | 198.0 | NITROGEN CYLINDER PRESSURE | -: 0 to 300.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PI-040 | R24-P-040 | FLD | 902-007-002-000-00159 | PRESSURE GAUGE - DIAPHRAGM | 10-N-E2E-0-9025830 | 198.0 | NITROGEN SUPPLY PRESSURE 1 | -: 0 to 100.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PI-041 | R24-P-041 | PCS | 902-007-002-000-00159 | INDICATOR - PRESSURE | 10-N-E2E-0-9025830 | 198.0 | NITROGEN SUPPLY PRESSURE 2 | -: 0 to 100.0 barg; -: +/- 2%; REF: SHE; REQ: 24; F: C | [11 empty] | v0.1
R24 | R24-PIT-041 | R24-P-041 | FLD | 902-007-002-000-00159 | TRANSMITTER - PRESSURE | 10-N-E2E-0-9025830 | 198.0 | NITROGEN SUPPLY PRESSURE 2 |  | 0 to 100.0 barg | +/- 2% | SHE | 24 | C |  |  | AI | [11 empty] | v0.1
R24 | R24-PRV-042 | R24-P-042 | FLD | 902-007-002-000-00159 | PRESSURE REDUCING VALVE | 10-N-E2E-0-9025830 | 198.0 | NITROGEN PRESSURE | -: 0 to 80.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 | R24-PSV-043 | R24-P-043 | FLD | 902-007-002-000-00159 | PRESSURE SAFETY VALVE | 10-N-E2E-0-9025830 | 198.0 | HP NITROGEN PRESSURE SAFETY VALVE | -: set @ 77.0 barg; -: +/- 10%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-PRV-044 | R24-P-044 | FLD | 902-007-002-000-00221 | PRESSURE REDUCING VALVE | 10-N-A3E-0-9025885 | 198.0 | NITROGEN PRESSURE | -: set @ 0.3 barg; -: +/- 2% | [11 empty] | v0.1
R24 |  | R24-P-045 | [26 empty] | v0.1 | bar: PKG
R24 | R24-PSV-046 | R24-P-046 | FLD | 902-007-002-000-00221 | PRESSURE SAFETY VALVE | 25-P-E2E-0-9025899 | 198.0 | SE01 CIP SUPPLY RELIEF VALVE | -: set @ 8 barg; -: +/- 10%; REF: SHE; REQ: 24 | [11 empty] | v0.1
R24 | R24-PI-047 | R24-P-047 | FLD | 902-007-002-000-00221 | PRESSURE GAUGE - DIAPHRAGM | 10-N-A3E-0-9025885 | 198.0 | NITROGEN SAMPLER SUPPLY PRESSURE | -: 0 to 2.0 barg; -: +/- 2% | [11 empty] | v0.1
R24 |  | R24-P-048 | [26 empty] | v0.3 | bar: PKG
R24 | R24-PI-049 | R24-P-049 | PLC | 902-007-002-000-00221 | PRESSURE INIDICATOR |  | 198.0 | BT04 BACK PRESSURE | -: 0 to 2.0 barg; -: +/- 2% | [11 empty] | v0.3
R24 | R24-PIC-049 | R24-P-049 | FLD | 902-007-002-000-00221 | INDICATING CONTROLLER - PRESSURE | 15-SV-A2E-0-9025889 | 198.0 | BT04 BACK PRESSURE | -: 0 to 2.0 barg; -: +/- 2% |  |  |  |  | Bronkhorst Pressure Controller | [6 empty] | v0.3
R24 | R24-PT-049 | R24-P-049 | FLD | 902-007-002-000-00221 | TRANSMITTER - PRESSURE | 15-SV-A2E-0-9025889 | 198.0 | BT04 BACK PRESSURE | -: 0 to 2.0 barg; -: +/- 2%; I.S: I.S. |  | Comms |  |  | Bronkhorst Pressure Controller | [6 empty] | v0.3
R24 | R24-PCV-049 | R24-P-049 | FLD | 902-007-002-000-00221 | CONTROL VALVE | 15-SV-A2E-0-9025889 | 198.0 | BT04 BACK PRESSURE | -: 0 to 2.0 barg; -: +/- 2%; I.S: I.S. |  | Comms |  |  | Bronkhorst Pressure Controller | [6 empty] | v0.3
R24 | R24-DPI-050 | R24-P-050 | PLC | 902-007-002-000-00220 | INDICATOR-PRESSURE-DIFF | CR01 INLET | 198.0 | CR01 INLET PLATE DIFF PRESSURE | -: 0 to 1000 mbarg; -: +/- 2% | [8 empty] | Calculated value from PI02/PI04 |  |  | v0.4
R24 | R24-DPI-051 | R24-P-051 | PLC | 902-007-002-000-00220 | INDICATOR-PRESSURE-DIFF | CR01 OUTLET | 198.0 | CR01 DIFF PRESSURE | -: 0 to 1000 mbarg; -: +/- 2% | [8 empty] | Calculated value from PI04/PI05 |  |  | v0.4
R24 | R24-DPI-052 | R24-P-052 | PLC | 902-007-002-000-00220 | INDICATOR-PRESSURE-DIFF | CR02 INLET | 198.0 | CR02 INLET PLATE DIFF PRESSURE | -: 0 to 1000 mbarg; -: +/- 2% | [8 empty] | Calculated value from PI05/PI06 |  |  | v0.4
R24 | R24-DPI-053 | R24-P-053 | PLC | 902-007-002-000-00220 | INDICATOR-PRESSURE-DIFF | CR02 OUTLET | 198.0 | CR02 DIFF PRESSURE | -: 0 to 1000 mbarg; -: +/- 2% | [8 empty] | Calculated value from PI06/PI07 |  |  | v0.4
R24 | R24-DPI-054 | R24-P-054 | PLC | 902-007-002-000-00220 | INDICATOR-PRESSURE-DIFF | CR03 INLET | 198.0 | CR03 INLET PLATE DIFF PRESSURE | -: 0 to 1000 mbarg; -: +/- 2% | [8 empty] | Calculated value from PI07/PI08 |  |  | v0.4
R24 | R24-DPI-055 | R24-P-055 | PLC | 902-007-002-000-00220 | INDICATOR-PRESSURE-DIFF | CR03 OUTLET | 198.0 | CR03 DIFF PRESSURE | -: 0 to 1000 mbarg; -: +/- 2% | [8 empty] | Calculated value from PI08/PI09 |  |  | v0.4
R24 | R24-RV-001 | R24-R-001 | FLD | 902-007-002-000-00220 | RELIEF VALVE | 25-HT-A1E-D-9025868 | 198.0 | CR01 JACKET THERMAL RELIEF | -: set @ 6.0 barg; -: +/- 10% | [11 empty] | v0.1
R24 | R24-RV-002 | R24-R-002 | FLD | 902-007-002-000-00220 | RELIEF VALVE | 20-HT-A1E-D-9025873 | 198.0 | CR02 JACKET THERMAL RELIEF | -: set @ 6.0 barg; -: +/- 10% | [11 empty] | v0.1
R24 | R24-RV-003 | R24-R-003 | FLD | 902-007-002-000-00220 | RELIEF VALVE | 20-HT-A1E-D-9025869 | 198.0 | CR03 JACKET THERMAL RELIEF | -: set @ 6.0 barg; -: +/- 10% | [11 empty] | v0.1
R24 | R24-RV-004 | R24-R-004 | FLD | 902-007-002-000-00221 | RELIEF VALVE | 25-HT-A1E-D-9025897 | 198.0 | CU01 JACKET THERMAL RELIEF | -: set @ 6.0 barg; -: +/- 10% | [11 empty] | v0.1
R24 | R24-SIC-001 | R24-S-001 | PLC | 902-007-002-000-00219 | INDICATING CONTROLLER - SPEED |  | 198.0 | METERING PUMP 1 | -: 0 to 100%; -: +/- 2% | [11 empty] | v0.1
R24 | R24-DS-001 | R24-S-001 | PKG | 902-007-002-000-00219 | DRIVE - AVAILABLE | R24 CONTROL PANEL | 198.0 | METERING PUMP 1 | [10 empty] | DI | [9 empty] | v0.1 | bar: PKG
R24 | R24-DY-001 | R24-S-001 | PKG | 902-007-002-000-00219 | DRIVE - RUNNING | R24 CONTROL PANEL | 198.0 | METERING PUMP 1 | [10 empty] | DI | [9 empty] | v0.1 | bar: PKG
R24 | R24-DYC-001 | R24-S-001 | PKG | 902-007-002-000-00219 | DRIVE - START/STOP | R24 CONTROL PANEL | 198.0 | METERING PUMP 1 | REF: SHE; REQ: 24; F: F |  | DO | [9 empty] | v0.1
R24 | R24-SYC-001 | R24-S-001 | PKG | 902-007-002-000-00219 | SPEED CONTROLLER - MCC | R24 CONTROL PANEL | 198.0 | METERING PUMP 1 | -: 0 to 100%; -: +/- 2% |  | AO | [9 empty] | v0.1
R24 |  | R24-S-002 | [26 empty] | v0.1 | bar: PKG
R24 | R24-TI-001 | R24-T-001 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR01 TEMPERATURE 1 | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-001 | R24-T-001 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | R24-CR01 | 198.0 | CR01 TEMPERATURE 1 | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-002 | R24-T-002 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR01 TEMPERATURE 2 | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-002 | R24-T-002 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | R24-CR01 | 198.0 | CR01 TEMPERATURE 2 | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-003 | R24-T-003 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR01 TEMPERATURE 3 | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-003 | R24-T-003 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | R24-CR01 | 198.0 | CR01 TEMPERATURE 3 | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-004 | R24-T-004 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR02 TEMPERATURE 1 | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-004 | R24-T-004 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | R24-CR02 | 198.0 | CR02 TEMPERATURE 1 | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-005 | R24-T-005 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR02 TEMPERATURE 2 | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-005 | R24-T-005 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | R24-CR02 | 198.0 | CR02 TEMPERATURE 2 | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-006 | R24-T-006 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR02 TEMPERATURE 3 | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-006 | R24-T-006 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | R24-CR02 | 198.0 | CR02 TEMPERATURE 3 | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-007 | R24-T-007 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR03 TEMPERATURE 1 | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-007 | R24-T-007 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | R24-CR03 | 198.0 | CR03 TEMPERATURE 1 | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-008 | R24-T-008 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR03 TEMPERATURE 2 | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-008 | R24-T-008 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | R24-CR03 | 198.0 | CR03 TEMPERATURE 2 | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-009 | R24-T-009 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR03 TEMPERATURE 3 | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-009 | R24-T-009 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | R24-CR03 | 198.0 | CR03 TEMPERATURE 3 | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-010 | R24-T-010 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR01 JKT RETURN TEMPERATURE | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-010 | R24-T-010 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | 25-HT-A1E-D-9025868 | 198.0 | CR01 JKT RETURN TEMPERATURE | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-011 | R24-T-011 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR02 JKT RETURN TEMPERATURE | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-011 | R24-T-011 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | 20-HT-A1E-D-9025873 | 198.0 | CR02 JKT RETURN TEMPERATURE | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-012 | R24-T-012 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR03 JKT RETURN TEMPERATURE | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-012 | R24-T-012 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | 20-HT-A1E-D-9025869 | 198.0 | CR03 JKT RETURN TEMPERATURE | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-013 | R24-T-013 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR01 JKT SUPPLY TEMPERATURE | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-013 | R24-T-013 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | 25-HT-A1E-D-9025867 | 198.0 | CR01 JKT SUPPLY TEMPERATURE | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-014 | R24-T-014 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR02 JKT SUPPLY TEMPERATURE | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-014 | R24-T-014 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | 20-HT-A1E-D-9025871 | 198.0 | CR02 JKT SUPPLY TEMPERATURE | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-015 | R24-T-015 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | CR03 JKT SUPPLY TEMPERATURE | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-015 | R24-T-015 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | 20-HT-A1E-D-9025874 | 198.0 | CR03 JKT SUPPLY TEMPERATURE | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-016 | R24-T-016 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | PH01 LIQUID OUTLET TEMPERATURE | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-016 | R24-T-016 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | 10-P-E2E-D-9025846 | 198.0 | PH01 LIQUID OUTLET TEMPERATURE | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-017 | R24-T-017 | PLC | 902-007-002-000-00220 | INDICATOR - TEMPERATURE |  | 198.0 | PH01 GAS OUTLET TEMPERATURE | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-017 | R24-T-017 | FLD | 902-007-002-000-00220 | TRANSMITTER - TEMPERATURE | 10-H-E2E-D-9025850 | 198.0 | PH01 GAS OUTLET TEMPERATURE | -: -30 to +150 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-018 | R24-T-018 | PLC | 902-007-002-000-00221 | INDICATOR - TEMPERATURE |  | 198.0 | CU01 OUTLET TEMPERATURE | -: -30 to +150 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-018 | R24-T-018 | FLD | 902-007-002-000-00221 | TRANSMITTER - TEMPERATURE | 10-H-E2E-D-9025882 | 198.0 | CU01 OUTLET TEMPERATURE |  | -30 to +150 degC | +/- 2% | SHE | 24 | C |  | I.S |  |  | AI | [9 empty] | v0.1
R24 | R24-TI-019 | R24-T-019 | PLC | 902-007-002-000-00221 | INDICATOR - TEMPERATURE |  | 198.0 | BT04 TEMPERATURE | -: -30 to +80 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-019 | R24-T-019 | FLD | 902-007-002-000-00221 | TRANSMITTER - TEMPERATURE | R24-BT04 | 198.0 | BT04 TEMPERATURE | -: -30 to +80 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 | R24-TI-020 | R24-T-020 | PLC | 902-007-002-000-00219 | INDICATOR - TEMPERATURE |  | 198.0 | BT01 TEMPERATURE | -: -30 to +80 degC; -: +/- 2% | [11 empty] | v0.1
R24 | R24-TT-020 | R24-T-020 | FLD | 902-007-002-000-00219 | TRANSMITTER - TEMPERATURE | R24-BT01 | 198.0 | BT01 TEMPERATURE | -: -30 to +80 degC; -: +/- 2%; I.S: I.S |  | AI | [9 empty] | v0.1
R24 |  | R24-T-021 | [26 empty] | v0.1 | bar: PKG
R24 | R24-XA-001 | R24-X-001 | FLD | 902-007-002-000-00159 | ALARM - AUDIBLE | 3rd FLR PLANT ROOM | 198.0 | O2 LEAK N2 CYLINDER STORE | REF: SHE; REQ: 24; F: F
R24 | R24-XL-001 | R24-X-001 | FLD | 902-007-002-000-00159 | ANNUNCIATOR - LAMP | 3rd FLR PLANT ROOM | 198.0 | O2 LEAK N2 CYLINDER STORE | REF: SHE; REQ: 24; F: F | [11 empty] | v0.1
R24 | R24-XA-010 | R24-X-010 | FLD | 902-007-002-000-00221 | ALARM - AUDIBLE | R24 CONTINUOUS HYDROG. SKID | 198.0 | CONTINUOUS HYDROGENATION SKID FAULT | [10 empty] | DO | bar: PKG
R24 | R24-XL-010 | R24-X-010 | FLD | 902-007-002-000-00221 | ANNUNCIATOR - LAMP | R24 CONTINUOUS HYDROG. SKID | 198.0 | CONTINUOUS HYDROGENATION SKID FAULT | [10 empty] | DO | bar: PKG
R24 | R24-XS-011 | R24-X-011 | PLC | 902-007-002-000-00221 | INTERFACE SIGNAL | DELTAV PCS | 198.0 | HYDROGEN SUPPLY STATUS | [10 empty] | DI | [9 empty] | v0.1 | bar: PKG; DI
R24 | R24-XS-012 | R24-X-012 | PLC | 902-007-002-000-00221 | INTERFACE SIGNAL | DELTAV PCS | 198.0 | CT02 STATUS | REF: SHE; REQ: 60; F: F; DI: DO |  | DI | [9 empty] | v0.1
R24 | R24-XS-013 | R24-X-013 | PLC | 902-007-002-000-00221 | INTERFACE SIGNAL | DELTAV PCS | 198.0 | R24 HYDROGEN LEAK DETECTION STATUS | [10 empty] | DI | [9 empty] | v0.1 | bar: PKG; DI
R24 | R24-XS-014 | R24-X-014 | PLC | 902-007-002-000-00221 | INTERFACE SIGNAL | DELTAV PCS | 198.0 | R23 CRITICAL HOLD STATUS | REF: SHE; REQ: 60; F: F; DI: DO |  | DI | [9 empty] | v0.1
R24 | R24-YS-001 | R24-Y-001 | PLC | 902-007-002-000-00221 | INTERFACE SIGNAL | R24 PLC | 198.0 | R24 CONTINUOUS FLOW PKG HEALTHY | [10 empty] | DO | bar: PKG; DI
R24 | R24-YS-002 | R24-Y-002 | PLC | 902-007-002-000-00221 | INTERFACE SIGNAL | R24 PLC | 198.0 | R24 CONTINUOUS FLOW PKG CRITICAL FAULT | [10 empty] | DO | bar: PKG; DI
R24 | R24-YS-003 | R24-Y-003 | PLC | 902-007-002-000-00221 | INTERFACE SIGNAL | R24 PLC | 198.0 | R24 CONTINUOUS FLOW PKG FAULT | [10 empty] | DO | bar: PKG; DI
R24 | R24-YS-004 | R24-Y-004 | PLC | 902-007-002-000-00221 | INTERFACE SIGNAL | R24 PLC | 198.0 | R24 CONTINUOUS FLOW PKG RUNNING | [10 empty] | DO | bar: PKG; DI
R24 | R24-YS-005 | R24-Y-005 | PLC | 902-007-002-000-00221 | INTERFACE SIGNAL | R24 PLC | 198.0 | R24 HYDROGEN SUPPLY REQUEST | [10 empty] | DO | bar: PKG; DI
RC01 | RC01-BD-001 | RC01-B-001 | FLD | 107-BP | RUPTURE DISC | 50-P-PT1A-C-9021020 | 093.1 | BURSTING DISC | 6754 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
RC01 | RC01-YI-001 | RC01-B-001 | PCS | 107-BP | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC01 | RC01-LI-001A | RC01-L-001 | PCS | 107-BP | INDICATOR - LEVEL |  |  | LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC01 | RC01-LI-001B | RC01-L-001 | FLD | 107-BP | INDICATOR - LEVEL | ADJ RC01 - VISIBLE | 093.1 | LEVEL |  | 0 to 300L | +/- 1% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5039 |  |  | 01
RC01 | RC01-LT-001 | RC01-L-001 | FLD | 107-BP | TRANSMITTER - LEVEL | RC01/N4/100 | 093.1 | LEVEL | 6963 | 0 to 300 l | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ENDRESS + HAUSER | FMR245 note2/3 | KL0028/P2 | TI702-SP-5039 |  |  | 01
RC01 | RC01-PI-001 | RC01-P-001 | FLD | 107-BP | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-C-9021020 | 093.1 | PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
RC01 | RC01-PRV-002 | RC01-P-002 | FLD | 107-BP | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028634 | 043.4 | N2 SUPPLY | -: 0.02 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  |  | R1440 | KV0006 |  |  |  | 01
RC02 | RC02-BD-001 | RC02-B-001 | FLD | 107-BP | RUPTURE DISC | 50-P-PT1A-C-9021040 | 093.2 | BURSTING DISC | 6755 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
RC02 | RC02-YI-001 | RC02-B-001 | PCS | 107-BP | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC02 | RC02-LI-001A | RC02-L-001 | PCS | 107-BP | INDICATOR - LEVEL |  |  | LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC02 | RC02-LI-001B | RC02-L-001 | FLD | 107-BP | INDICATOR - LEVEL | ADJ RC02 - VISIBLE | 093.2 | LEVEL |  | 0 to 500L | +/- 1% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5039 |  |  | 01
RC02 | RC02-LT-001 | RC02-L-001 | FLD | 107-BP | TRANSMITTER - LEVEL | RC02/N4/100 | 093.2 | LEVEL | 6964 | 0 to 500 l | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP1 | ENDRESS + HAUSER | FMR245 note2/3 | KL0028/P2 | TI702-SP-5039 |  |  | 01
RC02 | RC02-PI-001 | RC02-P-001 | FLD | 107-BP | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-C-9021040 | 093.2 | PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
RC02 | RC02-PRV-002 | RC02-P-002 | FLD | 107-BP | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028662 | 043.4 | N2 SUPPLY | -: 0.02 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  |  | R1440 | KV0006 |  |  |  | 01
RC03 | RC03-BD-001 | RC03-B-001 | FLD | 107-CP | RUPTURE DISC | 50-P-PT1A-C-9022020 | 095.1 | BURSTING DISC | 6756 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
RC03 | RC03-YI-001 | RC03-B-001 | PCS | 107-CP | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC03 | RC03-LI-001A | RC03-L-001 | PCS | 107-CP | INDICATOR - LEVEL |  |  | LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC03 | RC03-LI-001B | RC03-L-001 | FLD | 107-CP | INDICATOR - LEVEL | ADJ RC03 - VISIBLE | 095.1 | LEVEL |  | 0 to 300L | +/- 1% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5039 |  |  | 01
RC03 | RC03-LT-001 | RC03-L-001 | FLD | 107-CP | TRANSMITTER - LEVEL | RC03/N4/100 | 095.1 | LEVEL | 6884 | 0 to 300 l | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ENDRESS + HAUSER | FMR245 note2/3 | KL0028/P2 | TI702-SP-5039 |  |  | 01
RC03 | RC03-PI-001 | RC03-P-001 | FLD | 107-CP | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-C-9022020 | 095.1 | PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
RC03 | RC03-PRV-002 | RC03-P-002 | FLD | 107-CP | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028684 | 043.4 | N2 SUPPLY | -: 0.02 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  |  | R1440 | KV0006 |  |  |  | 01
RC04 | RC04-BD-001 | RC04-B-001 | FLD | 107-CP | RUPTURE DISC | 50-P-PT1A-C-9022040 | 095.2 | BURSTING DISC | 6757 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | GP2 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
RC04 | RC04-YI-001 | RC04-B-001 | PCS | 107-CP | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC04 | RC04-LI-001A | RC04-L-001 | PCS | 107-CP | INDICATOR - LEVEL |  |  | LEVEL | -: +/- 3% |  |  | 0 | [7 empty] | 01
RC04 | RC04-LI-001B | RC04-L-001 | FLD | 107-CP | INDICATOR - LEVEL | ADJ RC04 - VISIBLE | 095.2 | LEVEL |  | 0 to 850L | +/- 3% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5039 |  |  | 01
RC04 | RC04-LT-001 | RC04-L-001 | FLD | 107-CP | TRANSMITTER - LEVEL | RC04/N4/100 | 095.2 | LEVEL | 6885 | 0 to 850 l | +/- 3% | REF | 12 | C |  | I.S | AI |  |  | 11 | GP2 | ENDRESS + HAUSER | FMR245 note2/3 | KL0028/P2 | TI702-SP-5039 |  |  | 01
RC04 | RC04-PI-001 | RC04-P-001 | FLD | 107-CP | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-C-9022040 | 095.2 | PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
RC04 | RC04-PRV-002 | RC04-P-002 | FLD | 107-CP | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028705 | 043.4 | N2 SUPPLY | -: 0.02 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  |  | R1440 | KV0006 |  |  |  | 01
RC05 | RC05-BD-001 | RC05-B-001 | FLD | 107-DP | RUPTURE DISC | 50-P-PT1A-C-9023020 | 097.0 | BURSTING DISC | 6758 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | FG1 | BS&B | LCN / BAS + | KS0003/P3 | TI702-SP-5077 |  |  | 01
RC05 | RC05-YI-001 | RC05-B-001 | PCS | 107-DP | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC05 | RC05-LI-001A | RC05-L-001 | PCS | 107-DP | INDICATOR - LEVEL |  |  | LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC05 | RC05-LI-001B | RC05-L-001 | FLD | 107-DP | INDICATOR - LEVEL | ADJ RC05 - VISIBLE | 097.0 | LEVEL |  | 0 to 300L | +/- 1% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5039 |  |  | 01
RC05 | RC05-LT-001 | RC05-L-001 | FLD | 107-DP | TRANSMITTER - LEVEL | RC05/N4/100 | 097.0 | LEVEL | 6674 | 0 to 300 l | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ENDRESS + HAUSER | FMR245 note2/3 | KL0028/P2 | TI702-SP-5039 |  |  | 01
RC05 | RC05-PI-001 | RC05-P-001 | FLD | 107-DP | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-C-9023020 | 097.0 | PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
RC05 | RC05-PRV-002 | RC05-P-002 | FLD | 107-DP | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028801 | 043.4 | N2 SUPPLY | -: 0.02 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  |  | R1440 | KV0006 |  |  |  | 01
RC06 | RC06-BD-001 | RC06-B-001 | FLD | 107-EP | RUPTURE DISC | 50-P-PT1A-C-9024020 | 099.0 | BURSTING DISC | 6759 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | C1 | BS&B | LCN / BAS + | KS0003/P2 | TI702-SP-5077 |  |  | 01
RC06 | RC06-YI-001 | RC06-B-001 | PCS | 107-EP | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC06 | RC06-LI-001A | RC06-L-001 | PCS | 107-EP | INDICATOR - LEVEL |  |  | LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC06 | RC06-LI-001B | RC06-L-001 | FLD | 107-EP | INDICATOR - LEVEL | ADJ RC06 - VISIBLE | 099.0 | LEVEL |  | 0 to 500L | +/- 1% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 |  |  |  | 01
RC06 | RC06-LT-001 | RC06-L-001 | FLD | 107-EP | TRANSMITTER - LEVEL | RC06/N4/100 | 099.0 | LEVEL | 6678 | 0 to 500 l | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | C1 | ENDRESS + HAUSER | FMR245 note2/3 | KL0028/P2 | TI702-SP-5039 | ACC'Y +/- 10% 0-50 l |  | 01
RC06 | RC06-PI-001 | RC06-P-001 | FLD | 107-EP | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-C-9024020 | 099.0 | PRESSURE | -: -1 to 3 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
RC06 | RC06-PRV-002 | RC06-P-002 | FLD | 107-EP | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028836 | 043.4 | N2 SUPPLY | -: 0.02 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  |  | R1440 | KV0006 |  |  |  | 01
RC09 | RC09-BD-001 | RC09-B-001 | FLD | 107-DP | RUPTURE DISC | 50-P-PT1A-C-9023040 | 116.0 | BURSTING DISC | 8171 | 3.0 barg | - |  | 12 | F |  | I.S | DI |  |  | 32 | FG1 | BS&B | BAS + |  | TI702-SP-5077 |  |  | 01
RC09 | RC09-YI-001 | RC09-B-001 | PCS | 107-DP | ALARM - RUPTURE DISC FAIL |  |  | BURSTING DISC | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC09 | RC09-LI-001A | RC09-L-001 | PCS | 107-DP | INDICATOR - LEVEL |  |  | LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
RC09 | RC09-LI-001B | RC09-L-001 | FLD | 107-DP | INDICATOR - LEVEL | ADJ TO RC09 - VISIBLE | 116.0 | LEVEL |  | 0 to 850L | +/- 1.5% | REF | 12 | C |  | I.S |  |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5039 |  |  | 01
RC09 | RC09-LT-001 | RC09-L-001 | FLD | 107-DP | TRANSMITTER - LEVEL | RC09/N4/100 | 116.0 | LEVEL | 8252 | 0 to 850 l | +/- 2% | REF | 12 | C |  | I.S | AI |  |  | 11 | FG1 | ENDRESS + HAUSER | FMR245 note 4 | KL0028/P2 | TI702-SP-5039 |  |  | 01
RC09 | RC09-PI-001 | RC09-P-001 | FLD | 107-DP | PRESSURE GAUGE | 50-P-PT1A-0-9023040 | 116.0 | PRESSURE | -: -1 to 3 barg; -: +/- 1%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
RC09 | RC09-PRV-002 | RC09-P-002 | FLD | 107-DP | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028881 | 043.4 | N2 SUPPLY | -: 0.02 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | Esme | R1440 | KV0006 |  |  |  | 01
RELNTH | RELNTH-FI-001 | RELNTH-F-001 | FLD | 107-KB | VA FLOW METER | 15-N-SS1U-0-9028786 | 043.3 | N2 PURGE | -: 1 to 10 L/min; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
RELNTH | RELNTH-FI-002 | RELNTH-F-002 | FLD | 107-KB | VA FLOW METER | 15-N-SS1U-O-9028857 | 043.3 | N2 PURGE | -: 1 to 10 L/min; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
RELNTH | RELNTH-FI-003 | RELNTH-F-003 | FLD | 107-KB | VA FLOW METER | 15-N-SS1U-0-9028885 | 043.3 | N2 PURGE | -: 1 to 10 L/min; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
RELSTH | RELSTH-FI-001 | RELSTH-F-001 | FLD | 107-KA | VA FLOW METER | 15-N-SS1U-O-9028616 | 043.3 | N2 PURGE | -: 1 to 10 L/min; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | KHRONE | DK32 | KF0027 |  |  |  | 01
RELSTH | RELSTH-FI-002 | RELSTH-F-002 | FLD | 107-KA | VA FLOW METER | 15-N-SS1U-0-9028666 | 043.3 | N2 PURGE | -: 1 to 10 L/min; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
RELSTH | RELSTH-FI-003 | RELSTH-F-003 | FLD | 107-KA | VA FLOW METER | 15-N-SS1U-0-9028647 | 043.3 | N2 PURGE | -: 1 to 10 L/min; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | KROHNE | DK32 | KF0027 |  |  |  | 01
RU1 | RU1-CV-001 | RU1-C-001 | PKG | 107-MC | EXPANSION VALVE | HTF01-RU1 | 040.1 | TEMPERATURE CONTROL |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-002A | RU1-C-002 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU1 | 040.1 | CAPACITY ADJUSTMENT |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-002B | RU1-C-002 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU1 | 040.1 | CAPACITY ADJUSTMENT |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-002C | RU1-C-002 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU1 | 040.1 | CAPACITY ADJUSTMENT |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-002D | RU1-C-002 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU1 | 040.1 | CAPACITY ADJUSTMENT |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-003A | RU1-C-003 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU1 | 040.1 | LIQUID LINE SELECTION |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-003B | RU1-C-003 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU1 | 040.1 | LIQUID LINE SELECTION |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-003C | RU1-C-003 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU1 | 040.1 | LIQUID LINE SELECTION |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-003D | RU1-C-003 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU1 | 040.1 | LIQUID LINE SELECTION |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-004A | RU1-C-004 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU1 | 040.1 | EXPANSION VALVE |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-004B | RU1-C-004 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU1 | 040.1 | EXPANSION VALVE |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-004C | RU1-C-004 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU1 | 040.1 | EXPANSION VALVE |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-004D | RU1-C-004 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU1 | 040.1 | EXPANSION VALVE |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-005 | RU1-C-005 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU1 | 040.1 | THERMOSTATIC CONTROL |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-CV-007 | RU1-C-007 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU1 | 040.1 | ECONOMISER INLET |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-DIC-001 | RU1-D-001 | PCS | 107-MC | INDICATING CONTR. - MOTOR DRIVE |  |  | REFRIG COMPRESSOR | [11 empty] | 0 | [7 empty] | 01
RU1 | RU1-DS-001 | RU1-D-001 | LCP | 107-MC | DRIVE - AVAILABLE | HTF01-RU1 CONTROL PANEL |  | REFRIG COMPRESSOR | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
RU1 | RU1-DY-001 | RU1-D-001 | LCP | 107-MC | DRIVE - RUNNING | HTF01-RU1 CONTROL PANEL |  | REFRIG COMPRESSOR | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
RU1 | RU1-DYC-001 | RU1-D-001 | LCP | 107-MC | DRIVE - START/STOP | HTF01-RU1 CONTROL PANEL | 040.1 | REFRIG COMPRESSOR | 8727 | - | - | REF | REQ | F | SER | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
RU1 | RU1-II-001 | RU1-I-001 | PCS | 107-MC | INDICATOR - CURRENT |  |  | UNIT LOAD | [11 empty] | 0 | [7 empty] | 01
RU1 | RU1-IT-001 | RU1-I-001 | LCP | 107-MC | TRANSMITTER - CURRENT | HTF01-RU1 CONTROL PANEL | 040.1 | UNIT LOAD | 8729 | 0 to 100 % | - | REF | REQ | C | SER | N.I.S | AI |  |  | 13 | UTIL | [6 empty] | 01
RU1 | RU1-PT-001 | RU1-P-001 | PKG | 107-MC | TRANSMITTER - PRESSURE | HTF01-RU1 | 040.1 | EVAPORATOR OUTLET PRESS | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PT-002 | RU1-P-002 | PKG | 107-MC | TRANSMITTER - PRESSURE | HTF01-RU1 | 040.1 | OIL INJECTOR PRESSURE | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSH-003 | RU1-P-003 | PKG | 107-MC | SWITCH (DUAL) - PRESSURE - HI | HTF01-RU1 | 040.1 | COMPRESSOR OUTLET | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSV-004 | RU1-P-004 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU1 | 040.1 | OIL REGULATING VALVE | -: Set @ 3.5 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSV-005 | RU1-P-005 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU1 | 040.1 | CONDENSOR RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSV-006 | RU1-P-006 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU1 | 040.1 | CONDENSOR RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PCV-008 | RU1-P-008 | PKG | 107-MC | CONTROL VALVE SELF ACTUATING | HTF01-RU1 | 040.1 | WATER PRESSURE CONTROL | -: +/- 5%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSV-009 | RU1-P-009 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU1 | 040.1 | OIL SEPERATOR RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSV-010 | RU1-P-010 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU1 | 040.1 | OIL SEPERATOR RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PT-014 | RU1-P-014 | PKG | 107-MC | TRANSMITTER - PRESSURE | HTF01-RU1 | 040.1 | OIL SEPERATOR PRESSURE | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PT-016 | RU1-P-016 | PKG | 107-MC | TRANSMITTER - PRESSURE | HTF01-RU1 | 040.1 | OIL FILTER PRESSURE | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSV-017 | RU1-P-017 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU1 | 040.1 | EVAPORATOR OUTLET RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSV-018 | RU1-P-018 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU1 | 040.1 | LIQUID RECEIVER RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSV-019 | RU1-P-019 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU1 | 040.1 | LIQUID RECEIVER RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-PSV-020 | RU1-P-020 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU1 | 040.1 | COOLING WATER SUPPLY RELIEF | -: set @ 6.75 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-RO-001 | RU1-R-001 | PKG | 107-MC | RESTRICTION ORIFICE PLATE | HTF01-RU1 | 040.1 | OIL RETURN |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU1 | RU1-TSL-001 | RU1-T-001 | PKG | 107-MC | SWITCH - TEMPERATURE - LOW | HTF01-RU1 | 040.1 | HTF FLUID RETURN | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-TIC-002 | RU1-T-002 | PKG | 107-MC | INDICATING CONTROLLER - TEMPERATURE | HTF01-RU1 |  | HTF FLUID RETURN | [11 empty] | 0 | [7 empty] | 01
RU1 | RU1-TT-002 | RU1-T-002 | PKG | 107-MC | TRANSMITTER - TEMPERATURE | HTF01-RU1 | 040.1 | HTF FLUID RETURN | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-TT-003 | RU1-T-003 | PKG | 107-MC | TRANSMITTER - TEMPERATURE | HTF01-RU1 | 040.1 | OIL FILTER TEMPERATURE | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-TT-004 | RU1-T-004 | PKG | 107-MC | TRANSMITTER - TEMPERATURE | HTF01-RU1 | 040.1 | COMPRESSOR INLET TEMP. | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-TT-005 | RU1-T-005 | PKG | 107-MC | TRANSMITTER - TEMPERATURE | HTF01-RU1 | 040.1 | COMPRESSOR OUTLET TEMP. | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-TC-006 | RU1-T-006 | PKG | 107-MC | CONTROLLER - TEMPERATURE | HTF01-RU1 | 040.1 | OIL HEATER | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-TSH-007 | RU1-T-007 | PKG | 107-MC | SWITCH - TEMPERATURE - HIGH | HTF01-RU1 | 040.1 | OIL HEATER | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU1 | RU1-XA-001 | RU1-X-001 | PCS | 107-MC | ALARM - MISC. |  |  | COMMON ALARM | [11 empty] | 0 | [7 empty] | 01
RU1 | RU1-XS-001 | RU1-X-001 | LCP | 107-MC | SWITCH - COMMON ALARM | HTF01-RU1 CONTROL PANEL | 040.1 | COMMON ALARM | 8731 | - | - | REF | REQ | F | SER | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
RU1 | RU1-XA-002 | RU1-X-002 | PCS | 107-MC | ALARM - MISC. |  |  | ENCLOSURE OVER TEMP. | [11 empty] | 0 | [7 empty] | 01
RU1 | RU1-XS-002 | RU1-X-002 | LCP | 107-MC | SWITCH - FAN FAIL ALARM | HTF01-RU1 CONTROL PANEL | 040.1 | ENCLOSURE OVER TEMP. | 8733 | - | - | REF | REQ | F | SER | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
RU2 | RU2-CV-001 | RU2-C-001 | PKG | 107-MC | EXPANSION VALVE | HTF01-RU2 | 040.1 | TEMPERATURE CONTROL |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-002A | RU2-C-002 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU2 | 040.1 | CAPACITY ADJUSTMENT |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-002B | RU2-C-002 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU2 | 040.1 | CAPACITY ADJUSTMENT |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-002C | RU2-C-002 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU2 | 040.1 | CAPACITY ADJUSTMENT |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-002D | RU2-C-002 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU2 | 040.1 | CAPACITY ADJUSTMENT |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-003A | RU2-C-003 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU2 | 040.1 | LIQUID LINE SELECTION |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-003B | RU2-C-003 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU2 | 040.1 | LIQUID LINE SELECTION |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-003C | RU2-C-003 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU2 | 040.1 | LIQUID LINE SELECTION |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-003D | RU2-C-003 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU2 | 040.1 | LIQUID LINE SELECTION |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-004A | RU2-C-004 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU2 | 040.1 | EXPANSION VALVE |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-004B | RU2-C-004 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU2 | 040.1 | EXPANSION VALVE |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-004C | RU2-C-004 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU2 | 040.1 | EXPANSION VALVE |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-004D | RU2-C-004 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU2 | 040.1 | EXPANSION VALVE |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-005 | RU2-C-005 | PKG | 107-MC | TEMPERATURE CONTROL VALVE | HTF01-RU2 | 040.1 | THERMOSTATIC CONTROL |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-CV-007 | RU2-C-007 | PKG | 107-MC | SOLENOID VALVE | HTF01-RU2 | 040.1 | ECONOMISER INLET |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-DIC-001 | RU2-D-001 | PCS | 107-MC | INDICATING CONTR. - MOTOR DRIVE |  |  | REFRIG COMPRESSOR | [11 empty] | 0 | [7 empty] | 01
RU2 | RU2-DS-001 | RU2-D-001 | LCP | 107-MC | DRIVE - AVAILABLE | HTF01-RU2 CONTROL PANEL |  | REFRIG COMPRESSOR | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
RU2 | RU2-DY-001 | RU2-D-001 | LCP | 107-MC | DRIVE - RUNNING | HTF01-RU2 CONTROL PANEL |  | REFRIG COMPRESSOR | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
RU2 | RU2-DYC-001 | RU2-D-001 | LCP | 107-MC | DRIVE - START/STOP | HTF01-RU2 CONTROL PANEL | 040.1 | REFRIG COMPRESSOR | 8735 | - | - | REF | REQ | F | SER | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
RU2 | RU2-II-001 | RU2-I-001 | PCS | 107-MC | INDICATOR - CURRENT |  |  | UNIT LOAD | [11 empty] | 0 | [7 empty] | 01
RU2 | RU2-IT-001 | RU2-I-001 | LCP | 107-MC | TRANSMITTER - CURRENT | HTF01-RU2 CONTROL PANEL | 040.1 | UNIT LOAD | 8743 | 0 to 100 % | - | REF | REQ | C | SER | N.I.S | AI |  |  | 13 | UTIL | [6 empty] | 01
RU2 | RU2-PT-001 | RU2-P-001 | PKG | 107-MC | TRANSMITTER - PRESSURE | HTF01-RU2 | 040.1 | EVAPORATOR OUTLET PRESS | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PT-002 | RU2-P-002 | PKG | 107-MC | TRANSMITTER - PRESSURE | HTF01-RU2 | 040.1 | OIL INJECTOR PRESSURE | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSH-003 | RU2-P-003 | PKG | 107-MC | SWITCH (DUAL) - PRESSURE - HI | HTF01-RU2 | 040.1 | COMPRESSOR OUTLET | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSV-004 | RU2-P-004 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU2 | 040.1 | OIL REGULATING VALVE | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSV-005 | RU2-P-005 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU2 | 040.1 | CONDENSOR RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSV-006 | RU2-P-006 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU2 | 040.1 | CONDENSOR RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PCV-008 | RU2-P-008 | PKG | 107-MC | CONTROL VALVE SELF ACTUATING | HTF01-RU2 | 040.1 | WATER PRESSURE CONTROL | -: +/- 5%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSV-009 | RU2-P-009 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU2 | 040.1 | OIL SEPERATOR RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSV-010 | RU2-P-010 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU2 | 040.1 | OIL SEPERATOR RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PT-014 | RU2-P-014 | PKG | 107-MC | TRANSMITTER - PRESSURE | HTF01-RU2 | 040.1 | OIL SEPERATOR PRESSURE | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PT-016 | RU2-P-016 | PKG | 107-MC | TRANSMITTER - PRESSURE | HTF01-RU2 | 040.1 | OIL FILTER PRESSURE | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSV-017 | RU2-P-017 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU2 | 040.1 | EVAPORATOR OUTLET RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSV-018 | RU2-P-018 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU2 | 040.1 | LIQUID RECEIVER RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSV-019 | RU2-P-019 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU2 | 040.1 | LIQUID RECEIVER RELIEF | -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-PSV-020 | RU2-P-020 | PKG | 107-MC | PRESSURE RELIEF VALVE | HTF01-RU2 | 040.1 | COOLING WATER SUPPLY RELIEF | -: 6.75 barg; -: +/- 10%; REQ: 24; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-RO-001 | RU2-R-001 | PKG | 107-MC | RESTRICTION ORIFICE PLATE | HTF01-RU2 | 040.1 | OIL RETURN |  | - | - | REF | REQ | F | SER |  |  |  |  | 0 | [7 empty] | 01
RU2 | RU2-TSL-001 | RU2-T-001 | PKG | 107-MC | SWITCH - TEMPERATURE - LOW | HTF01-RU2 | 040.1 | HTF FLUID RETURN | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-TIC-002 | RU2-T-002 | PKG | 107-MC | INDICATING CONTROLLER - TEMPERATURE | HTF01-RU2 |  | HTF FLUID RETURN | [11 empty] | 0 | [7 empty] | 01
RU2 | RU2-TT-002 | RU2-T-002 | PKG | 107-MC | TRANSMITTER - TEMPERATURE | HTF01-RU2 | 040.1 | HTF FLUID RETURN | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-TT-003 | RU2-T-003 | PKG | 107-MC | TRANSMITTER - TEMPERATURE | HTF01-RU2 | 040.1 | OIL FILTER TEMPERATURE | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-TT-004 | RU2-T-004 | PKG | 107-MC | TRANSMITTER - TEMPERATURE | HTF01-RU2 | 040.1 | COMPRESSOR INLET TEMP. | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-TT-005 | RU2-T-005 | PKG | 107-MC | TRANSMITTER - TEMPERATURE | HTF01-RU2 | 040.1 | COMPRESSOR OUTLET TEMP. | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-TC-006 | RU2-T-006 | PKG | 107-MC | CONTROLLER - TEMPERATURE | HTF01-RU2 | 040.1 | OIL HEATER | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-TSH-007 | RU2-T-007 | PKG | 107-MC | SWITCH - TEMPERATURE - HIGH | HTF01-RU2 | 040.1 | OIL HEATER | -: +/- ___%; REF: REF; REQ: REQ; F: C; Ref: SER |  |  | 0 | [7 empty] | 01
RU2 | RU2-XA-001 | RU2-X-001 | PCS | 107-MC | ALARM - MISC. |  |  | COMMON ALARM | [11 empty] | 0 | [7 empty] | 01
RU2 | RU2-XS-001 | RU2-X-001 | LCP | 107-MC | SWITCH - COMMON ALARM | HTF01-RU2 CONTROL PANEL | 040.1 | COMMON ALARM | 8746 | - | - | REF | REQ | F | SER | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
RU2 | RU2-XA-002 | RU2-X-002 | PCS | 107-MC | ALARM - MISC. |  |  | ENCLOSURE OVER TEMP. | [11 empty] | 0 | [7 empty] | 01
RU2 | RU2-XS-002 | RU2-X-002 | LCP | 107-MC | SWITCH - FAN FAIL ALARM | HTF01-RU2 CONTROL PANEL | 040.1 | ENCLOSURE OVER TEMP. | 8749 | - | - | REF | REQ | F | SER | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
RU3 | RU3-AAH-001A | RU3-A-001 | SGS | 107-MD | Ammonia high level alarm to SGS | SGS/IE31406 |  | Ammonia high level alarm | PKG: 13092; -: 50 ppm |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AAH-001B | RU3-A-001 | BEMS | 107-MD | Ammonia high level alarm to BEMS | BEMS/IE31406 |  | Ammonia high level alarm | PKG: 13092; -: 50 ppm |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AAH-001C | RU3-A-001 | IE31405/6 | 107-MD | Ammonia high level alarm to chiller PLC | IE31405/IE31406 |  | Ammonia high level alarm | PKG: 13092; -: 50 ppm |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AAH-002A | RU3-A-002 | SGS | 107-MD | Ammonia high high level alarm to SGS | SGS/IE31406 |  | Ammonia high high level alarm | PKG: 13093; -: 250 ppm |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AAH-002B | RU3-A-002 | BEMS | 107-MD | Ammonia high high level alarm to BEMS | BEMS/IE31406 |  | Ammonia high high level alarm | PKG: 13093; -: 250 ppm |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AAH-002C | RU3-A-002 | IE31405/6 | 107-MD | Ammonia high high level alarm to chiller PLC | IE31405/IE31406 |  | Ammonia high high level alarm | PKG: 13093; -: 250 ppm |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AAH-003A | RU3-A-003 | SGS | 107-MD | Ammonia critical level alarm to SGS | SGS/IE31406 |  | Ammonia critical level alarm | PKG: 13094; -: 400 ppm or 4% LEL |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AAH-003B | RU3-A-003 | BEMS | 107-MD | Ammonia critical level alarm to BEMS | BEMS/IE31406 |  | Ammonia critical level alarm | PKG: 13094; -: 400 ppm or 4% LEL |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AAH-003C | RU3-A-003 | IE31405/6 | 107-MD | Ammonia critical level alarm to chiller PLC | IE31405/IE31406 |  | Ammonia critical level alarm | PKG: 13094; -: 400 ppm or 4% LEL |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AAH-003D | RU3-A-003 | IE31406 | 107-MD | Ammonia critical level alarm - MCC interlock | IE31406/MCC |  | Ammonia critical level alarm | PKG: 13094; -: 400 ppm or 4% LEL |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-AI-004A | RU3-A-004 | FLD | 107-MD | Ammonia ppm level local indicator A | RU3 enclosure external | 040.1 | RU3 enclosure ammonia detection | PKG: 13095; -: 0 to 500 ppm |  |  |  |  | CROWCON | Gasmaster 4 |  |  |  |  | 01
RU3 | RU3-AI-004B | RU3-A-004 | FLD | 107-MD | Ammonia ppm level local indicator B | RU3 enclosure external | 040.1 | RU3 enclosure ammonia detection | PKG: 13095; -: 0 to 500 ppm |  |  |  |  | CROWCON | Gasmaster 4 |  |  |  |  | 01
RU3 | RU3-AI-004C | RU3-A-004 | FLD | 107-MD | Ammonia ppm level local indicator C | RU3 enclosure external | 040.1 | RU3 enclosure ammonia detection | PKG: 13095; -: 0 to 500 ppm |  |  |  |  | CROWCON | Gasmaster 4 |  |  |  |  | 01
RU3 | RU3-AI-004D | RU3-A-004 | FLD | 107-MD | Ammonia %LEL level local indicator D | RU3 enclosure external | 040.1 | RU3 enclosure ammonia detection | PKG: 13095; -: 0 to 50% LEL |  |  |  |  | CROWCON | Gasmaster 4 |  |  |  |  | 01
RU3 | RU3-AT-004A | RU3-A-004 | FLD | 107-MD | Ammonia ppm level transmitter A | RU3 enclosure internal | 040.1 | RU3 enclosure ammonia detection | PKG: 13095; -: 0 to 500 ppm |  |  |  |  | CROWCON | Xgard1-0036 |  |  |  |  | 01
RU3 | RU3-AT-004B | RU3-A-004 | FLD | 107-MD | Ammonia ppm level transmitter B | RU3 enclosure internal | 040.1 | RU3 enclosure ammonia detection | PKG: 13095; -: 0 to 500 ppm |  |  |  |  | CROWCON | Xgard1-0036 |  |  |  |  | 01
RU3 | RU3-AT-004C | RU3-A-004 | FLD | 107-MD | Ammonia ppm level transmitter C | RU3 enclosure internal | 040.1 | RU3 enclosure ammonia detection | PKG: 13095; -: 0 to 500 ppm |  |  |  |  | CROWCON | Xgard1-0036 |  |  |  |  | 01
RU3 | RU3-AT-004D | RU3-A-004 | FLD | 107-MD | Ammonia %LEL level transmitter D | RU3 enclosure internal | 040.1 | RU3 enclosure ammonia detection | PKG: 13095; -: 0 to 50% LEL |  |  |  |  | CROWCON | Xgard3-0003 |  |  |  |  | 01
RU3 | RU3-AY-004A | RU3-A-004 | IE31406 | 107-MD | IS barrier | GDS main panel |  | RU3 enclosure ammonia detection | PKG: 13095 |  |  |  |  | PEPPERL + FUCHS | KFD2-CR-Ex1.30-200 |  |  |  |  | 01
RU3 | RU3-AY-004B | RU3-A-004 | IE31406 | 107-MD | IS barrier | GDS main panel |  | RU3 enclosure ammonia detection | PKG: 13095 |  |  |  |  | PEPPERL + FUCHS | KFD2-CR-Ex1.30-200 |  |  |  |  | 01
RU3 | RU3-AY-004C | RU3-A-004 | IE31406 | 107-MD | IS barrier | GDS main panel |  | RU3 enclosure ammonia detection | PKG: 13095 |  |  |  |  | PEPPERL + FUCHS | KFD2-CR-Ex1.30-200 |  |  |  |  | 01
RU3 | RU3-CV-001 | RU3-C-001 | FLD | 107-MD | Damper | RU3 enclosure | 040.1 | RU3 enclosure inlet damper | PKG: 13084 | [10 empty] | 01
RU3 | RU3-CY-001 | RU3-C-001 | FLD | 107-MD | Control damper enable | RU3 enclosure | 040.1 | RU3 enclosure inlet damper | PKG: 13084 |  |  |  |  | BELIMO | LF230-S |  |  |  |  | 01
RU3 | RU3-ZSO-001 | RU3-C-001 | FLD | 107-MD | Control damper open end switch | RU3 enclosure | 040.1 | RU3 enclosure inlet damper | PKG: 13084 |  |  |  |  | BELIMO | LF230-S |  |  |  |  | 01
RU3 | RU3-CV-002 | RU3-C-002 | FLD | 107-MD | Damper | RU3 enclosure | 040.1 | RU3 enclosure extract damper 1 | PKG: 13085 | [10 empty] | 01
RU3 | RU3-CY-002 | RU3-C-002 | FLD | 107-MD | Control damper enable | RU3 enclosure | 040.1 | RU3 enclosure extract damper 1 | PKG: 13085 |  |  |  |  | BELIMO | LF230-S |  |  |  |  | 01
RU3 | RU3-ZSO-002 | RU3-C-002 | FLD | 107-MD | Control damper open end switch | RU3 enclosure | 040.1 | RU3 enclosure extract damper 1 | PKG: 13085 |  |  |  |  | BELIMO | LF230-S |  |  |  |  | 01
RU3 | RU3-CV-003 | RU3-C-003 | FLD | 107-MD | Damper | RU3 enclosure | 040.1 | RU3 enclosure extract damper 2 | PKG: 13086 | [10 empty] | 01
RU3 | RU3-CY-003 | RU3-C-003 | FLD | 107-MD | Control damper enable | RU3 enclosure | 040.1 | RU3 enclosure extract damper 2 | PKG: 13086 |  |  |  |  | BELIMO | LF230-S |  |  |  |  | 01
RU3 | RU3-ZSO-003 | RU3-C-003 | FLD | 107-MD | Control damper open end switch | RU3 enclosure | 040.1 | RU3 enclosure extract damper 2 | PKG: 13086 |  |  |  |  | BELIMO | LF230-S |  |  |  |  | 01
RU3 | RU3-CV-091 | RU3-C-091 | FLD | 107-MD | Solenoid valve | RU3 enclosure internal | 040.1 | Unload supply solenoid valve | PKG: 13098 |  |  |  |  | JOUCO / MYCOM | SLV-ME-24VDC |  |  |  |  | 01
RU3 | RU3-CV-093 | RU3-C-093 | FLD | 107-MD | Solenoid valve | RU3 enclosure internal | 040.1 | Load return solenoid valve | PKG: 13097 |  |  |  |  | JOUCO / MYCOM | SLV-ME-24VDC |  |  |  |  | 01
RU3 | RU3-CV-095 | RU3-C-095 | FLD | 107-MD | Solenoid valve | RU3 enclosure internal | 040.1 | Unload return solenoid valve | PKG: 13100 |  |  |  |  | JOUCO / MYCOM | SLV-ME-24VDC |  |  |  |  | 01
RU3 | RU3-CV-096 | RU3-C-096 | FLD | 107-MD | Solenoid valve | RU3 enclosure internal | 040.1 | Load supply solenoid valve | PKG: 13099 |  |  |  |  | JOUCO / MYCOM | SLV-ME-24VDC |  |  |  |  | 01
RU3 | RU3-CV-102 | RU3-C-102 | FLD | 107-MD | Solenoid valve | RU3 enclosure internal | 040.1 | Fine filter oil return solenoid valve | PKG: 13101 |  |  |  |  | JOUCO / MYCOM | SLV-ME-24VDC |  |  |  |  | 01
RU3 | RU3-CV-112 | RU3-C-112 | FLD | 107-MD | Solenoid valve | RU3 enclosure internal | 040.1 | Economiser liquid supply solenoid valve | PKG: 13103 |  |  |  |  | DANFOSS / MYCOM | SLV-EVRAT20-M |  |  |  |  | 01
RU3 | RU3-CV-115 | RU3-C-115 | FLD | 107-MD | Expansion valve | RU3 enclosure internal | 040.1 | Economiser thermostatic expansion valve | PKG: 13104; -: -20 to +30oC |  |  |  |  | DANFOSS / MYCOM | EXV-TEA20/20=>-20/+30C |  |  |  |  | 01
RU3 | RU3-CV-173 | RU3-C-173 | FLD | 107-MD | Solenoid valve | RU3 enclosure internal | 040.1 | Evaporator liquid supply solenoid valve | PKG: 13102 |  |  |  |  | DANFOSS / MYCOM | SLV-EVRAT15-M |  |  |  |  | 01
RU3 | RU3-CV-175 | RU3-C-175 | FLD | 107-MD | Expansion valve | RU3 enclosure internal | 040.1 | Evaporator expansion valve | PKG: 13105; -: KVs=1.7 |  |  |  |  | HERL / MYCOM | EXV-T150-DN25/KV1.7-110V/50HZ |  |  |  |  | 01
RU3 | RU3-DS-001 | RU3-D-001 | PCS | 107-MD | Chiller available signal | PCS/IE31405 |  | RU3 chiller | PKG: 13081 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
RU3 | RU3-DY-001 | RU3-D-001 | PCS | 107-MD | Chiller running signal | PCS/IE31405 |  | RU3 chiller | PKG: 13081 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
RU3 | RU3-DYC-001 | RU3-D-001 | PCS | 107-MD | Chiller enable signal | PCS/IE31405 |  | RU3 chiller | PKG: 13081 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
RU3 | RU3-DY-002 | RU3-D-002 | PLC/MCC | 107-MD | Fan running signal | PLC/MCC |  | RU3 chiller enclosure extract fan 1 | PKG: 13082 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
RU3 | RU3-DYC-002 | RU3-D-002 | PLC/MCC | 107-MD | Fan enable signal | PLC/MCC |  | RU3 chiller enclosure extract fan 1 | PKG: 13082 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
RU3 | RU3-DY-003 | RU3-D-003 | PLC/MCC | 107-MD | Fan running signal | PLC/MCC |  | RU3 chiller enclosure extract fan 2 | PKG: 13083 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
RU3 | RU3-DYC-003 | RU3-D-003 | PLC/MCC | 107-MD | Fan enable signal | PLC/MCC |  | RU3 chiller enclosure extract fan 2 | PKG: 13083 |  |  |  |  | MOORE INDUSTRIES | APACS |  |  |  |  | 01
RU3 | RU3-DYC-007 | RU3-D-007 | FLD | 107-MD | Oil pump enable | RU3 enclosure | 040.1 | RU3 chiller oil pump | PKG: 13132 |  |  |  |  | SIEMENS | S7-300 |  |  |  |  | 01
RU3 | RU3-HS-001 | RU3-H-001 | Rack room | 107-MD | Reset button | B902 1.02 | 040.1 | Ammonia gas detection system reset | PKG: 13096 |  |  |  |  | CROWCON | 989/1 |  |  |  |  | 01
RU3 | RU3-II-001 | RU3-I-001 | PCS | 107-MD | Chiller load | PCS/IE31405 |  | RU3 chiller load | PKG: 13091; -: 0 to 100% |  |  |  |  | CROWCON | [5 empty] | 01
RU3 | RU3-PCV-001 | RU3-P-001 | FLD | 107-MD | Pressure control valve | RU3 enclosure internal | 040.1 | Cooling water head pressure control valve | PKG: 13106; -: 4 to 25 psi dP |  |  |  |  | METREX VALVE CORP. | CRA-3130-FL-2W-TA |  |  |  |  | 01
RU3 | RU3-PSV-040 | RU3-P-040 | FLD | 107-MD | Pressure relief valve | RU3 enclosure internal | 040.1 | Oil separator pressure relief valve | PKG: 13114; -: 21 Barg |  |  |  |  | HERL / MYCOM | SAV-T23-DN50-21G |  |  |  |  | 01
RU3 | RU3-PI-071 | RU3-P-071 | PLC/HMI | 107-MD | Pressure indication - HMI | IE31405 |  | Compressor suction pressure | PKG: 13107; -: -1 to +10 barg |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-PI-076 | RU3-P-071 | FLD | 107-MD | Pressure indication - local gauge | RU3 enclosure internal | 040.1 | Compressor suction pressure | PKG: 13107; -: -1 to +10 barg |  |  |  |  | GOOSS / MYCOM | GAU-63-10BAR |  |  |  |  | 01
RU3 | RU3-PT-071 | RU3-P-071 | FLD | 107-MD | Pressure transmitter | RU3 enclosure internal | 040.1 | Compressor suction pressure | PKG: 13107; -: -1 to +10 barg |  |  |  |  | JUMO / MYCOM | SEN-PT-1/10BARG-4/20mA-IP67 |  |  |  |  | 01
RU3 | RU3-PI-072 | RU3-P-072 | PLC/HMI | 107-MD | Pressure indication - HMI | IE31405 |  | Compressor discharge pressure | PKG: 13108; -: -1 to +30 barg |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-PI-078 | RU3-P-072 | FLD | 107-MD | Pressure indication - local gauge | RU3 enclosure internal | 040.1 | Compressor discharge pressure | PKG: 13108; -: -1 to 25 barg |  |  |  |  | GOOSS / MYCOM | GAU-63-25BAR |  |  |  |  | 01
RU3 | RU3-PT-072 | RU3-P-072 | FLD | 107-MD | Pressure transmitter | RU3 enclosure internal | 040.1 | Compressor discharge pressure | PKG: 13108; -: -1 to +30 barg |  |  |  |  | JUMO / MYCOM | SEN-PT-1/30BARG-4/20mA-IP67 |  |  |  |  | 01
RU3 | RU3-PI-073 | RU3-P-073 | PLC/HMI | 107-MD | Pressure indication - HMI | IE31405 |  | Oil header pressure | PKG: 13109; -: -1 to +30 barg |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-PI-077 | RU3-P-073 | FLD | 107-MD | Pressure indication - local gauge | RU3 enclosure internal | 040.1 | Oil header pressure | PKG: 13109; -: -1 to 25 barg |  |  |  |  | GOOSS / MYCOM | GAU-63-25BAR |  |  |  |  | 01
RU3 | RU3-PT-073 | RU3-P-073 | FLD | 107-MD | Pressure transmitter | RU3 enclosure internal | 040.1 | Oil header pressure | PKG: 13109; -: -1 to +30 barg |  |  |  |  | JUMO / MYCOM | SEN-PT-1/30BARG-4/20mA-IP67 |  |  |  |  | 01
RU3 | RU3-PI-074 | RU3-P-074 | PLC/HMI | 107-MD | Pressure indication | IE31405 |  | Post oil filter pressure | PKG: 13110; -: -1 to +30 barg |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-PT-074 | RU3-P-074 | FLD | 107-MD | Pressure transmitter | RU3 enclosure internal | 040.1 | Post oil filter pressure | PKG: 13110; -: -1 to +30 barg |  |  |  |  | JUMO / MYCOM | SEN-PT-1/30BARG-4/20mA-IP67 |  |  |  |  | 01
RU3 | RU3-PI-075 | RU3-P-075 | PLC/HMI | 107-MD | Pressure indication | IE31405 |  | Post fine filter pressure | PKG: 13111; -: -1 to +30 barg |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-PT-075 | RU3-P-075 | FLD | 107-MD | Pressure transmitter | RU3 enclosure internal | 040.1 | Post fine filter pressure | PKG: 13111; -: -1 to +30 barg |  |  |  |  | JUMO / MYCOM | SEN-PT-1/30BARG-4/20mA-IP67 |  |  |  |  | 01
RU3 | RU3-PI-079 | RU3-P-079 | PLC/HMI | 107-MD | Pressure indication - HMI | IE31405 |  | Intermediate pressure | PKG: 13112; -: -1 to +30 barg |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-PI-080 | RU3-P-079 | FLD | 107-MD | Pressure indication - local gauge | RU3 enclosure internal | 040.1 | Intermediate pressure | PKG: 13112; -: -1 to 25 barg |  |  |  |  | GOOSS / MYCOM | GAU-63-25BAR |  |  |  |  | 01
RU3 | RU3-PT-079 | RU3-P-079 | FLD | 107-MD | Pressure transmitter | RU3 enclosure internal | 040.1 | Intermediate pressure | PKG: 13112; -: -1 to +30 barg |  |  |  |  | JUMO / MYCOM | SEN-PT-1/30BARG-4/20mA-IP67 |  |  |  |  | 01
RU3 | RU3-PSV-131 | RU3-P-131 | FLD | 107-MD | Pressure relief valve | RU3 enclosure internal | 040.1 | Condensor pressure relief valve | PKG: 13115; -: 21 Barg |  |  |  |  | HERL / MYCOM | SAV-T23-DN15-21G |  |  |  |  | 01
RU3 | RU3-PS-144 | RU3-P-144 | FLD | 107-MD | Pressure switch | RU3 enclosure internal | 040.1 | Compressor high pressure switch | PKG: 13113; -: 16 barg |  |  |  |  | DANFOSS / MYCOM | CTR-KP7ABS-M-CR6 |  |  |  |  | 01
RU3 | RU3-PSV-163 | RU3-P-163 | FLD | 107-MD | Pressure relief valve | RU3 enclosure internal | 040.1 | Evaporator pressure relief valve | PKG: 13116; -: 15 Barg |  |  |  |  | HERL / MYCOM | SAV-T23-DN15-15G |  |  |  |  | 01
RU3 | RU3-TI-001 | RU3-T-001 | FLD | 107-MD | Temperature indicator | 150-CWR-CS1B-W-9027360 | 040.1 | CWR local temperature gauge | PKG: 13117; -: 0 to 60oC |  |  |  |  | ROTOTHERM | BH2 42 |  |  |  |  | 01
RU3 | RU3-TAH-002 | RU3-T-002 | PLC | 107-MD | High temperature alarm | IE31405 |  | RU3 enclosure temperature | PKG: 13118; -: 26oC |  |  |  |  | SIEMENS | S7-300 |  |  |  |  | 01
RU3 | RU3-TAHH-002 | RU3-T-002 | PLC | 107-MD | High high temperature alarm | IE31405 |  | RU3 enclosure temperature | PKG: 13118; -: 40oC |  |  |  |  | SIEMENS | S7-300 |  |  |  |  | 01
RU3 | RU3-TE-002 | RU3-T-002 | FLD | 107-MD | Temperature element | RU3 enclosure internal | 040.1 | RU3 enclosure temperature | PKG: 13118 |  |  |  |  | MYCOM | [5 empty] | 01
RU3 | RU3-TI-002 | RU3-T-002 | PLC/HMI | 107-MD | HMI temperature indication | IE31405 |  | RU3 enclosure temperature | PKG: 13118 |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-TT-002 | RU3-T-002 | FLD | 107-MD | Temperature transmitter | RU3 enclosure internal | 040.1 | RU3 enclosure temperature | PKG: 13118 |  |  |  |  | MYCOM | [5 empty] | 01
RU3 | RU3-TCV-025 | RU3-T-025 | FLD | 107-MD | Temperature control valve | RU3 enclosure internal | 040.1 | Oil temperature thermostatic control valve | PKG: 13124; -: 38 to 47oC |  |  |  |  | THREG | 3WV-M40TS6D110-23 |  |  |  |  | 01
RU3 | RU3-TALL-086 | RU3-T-086 | PLC | 107-MD | Low low temperature alarm | IE31405 |  | Compressor suction temperature | PKG: 13120 |  |  |  |  | SIEMENS | S7-300 |  |  |  |  | 01
RU3 | RU3-TE-086 | RU3-T-086 | FLD | 107-MD | Temperature element | RU3 enclosure internal | 040.1 | Compressor suction temperature | PKG: 13120; -: -50 to +50oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-50/50C-4/20MA-IP65 |  |  |  |  | 01
RU3 | RU3-TI-086 | RU3-T-086 | PLC/HMI | 107-MD | HMI temperature indication | IE31405 |  | Compressor suction temperature | PKG: 13120; -: -50 to +50oC |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-TT-086 | RU3-T-086 | FLD | 107-MD | Temperature transmitter | RU3 enclosure internal | 040.1 | Compressor suction temperature | PKG: 13120; -: -50 to +50oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-50/50C-4/20MA-IP65 |  |  |  |  | 01
RU3 | RU3-TE-087 | RU3-T-087 | FLD | 107-MD | Temperature element | RU3 enclosure internal | 040.1 | Intermediate temperature | PKG: 13123; -: -50 to +50oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-50/50C-4/20MA-IP65 |  |  |  |  | 01
RU3 | RU3-TI-087 | RU3-T-087 | PLC/HMI | 107-MD | HMI temperature indication | IE31405 |  | Intermediate temperature | PKG: 13123; -: -50 to +50oC |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-TT-087 | RU3-T-087 | FLD | 107-MD | Temperature transmitter | RU3 enclosure internal | 040.1 | Intermediate temperature | PKG: 13123; -: -50 to +50oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-50/50C-4/20MA-IP65 |  |  |  |  | 01
RU3 | RU3-TAHH-088 | RU3-T-088 | PLC | 107-MD | High high temperature alarm | IE31405 |  | Oil header temperature | PKG: 13122; -: 60oC |  |  |  |  | SIEMENS | S7-300 |  |  |  |  | 01
RU3 | RU3-TE-088 | RU3-T-088 | FLD | 107-MD | Temperature element | RU3 enclosure internal | 040.1 | Oil header temperature | PKG: 13122; -: 0 to +150oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-0/150C-4/20MA-IP65 |  |  |  |  | 01
RU3 | RU3-TI-088 | RU3-T-088 | PLC/HMI | 107-MD | HMI temperature indication | IE31405 |  | Oil header temperature | PKG: 13122; -: 0 to +150oC |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-TT-088 | RU3-T-088 | FLD | 107-MD | Temperature transmitter | RU3 enclosure internal | 040.1 | Oil header temperature | PKG: 13122; -: 0 to +150oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-0/150C-4/20MA-IP65 |  |  |  |  | 01
RU3 | RU3-TAHH-089 | RU3-T-089 | PLC | 107-MD | High high temperature alarm | IE31405 |  | Compressor discharge temperature | PKG: 13121; -: 95oC |  |  |  |  | SIEMENS | S7-300 |  |  |  |  | 01
RU3 | RU3-TE-089 | RU3-T-089 | FLD | 107-MD | Temperature element | RU3 enclosure internal | 040.1 | Compressor discharge temperature | PKG: 13121; -: 0 to +150oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-0/150C-4/20MA-IP65 |  |  |  |  | 01
RU3 | RU3-TI-089 | RU3-T-089 | PLC/HMI | 107-MD | HMI temperature indication | IE31405 |  | Compressor discharge temperature | PKG: 13121; -: 0 to +150oC |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-TT-089 | RU3-T-089 | FLD | 107-MD | Temperature transmitter | RU3 enclosure internal | 040.1 | Compressor discharge temperature | PKG: 13121; -: 0 to +150oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-0/150C-4/20MA-IP65 |  |  |  |  | 01
RU3 | RU3-TALL-161 | RU3-T-161 | PLC | 107-MD | Low low temperature alarm | IE31405 |  | Evaporator HTF outlet temperature | PKG: 13119; -: -30oC |  |  |  |  | SIEMENS | S7-300 |  |  |  |  | 01
RU3 | RU3-TE-161 | RU3-T-161 | FLD | 107-MD | Temperature element | RU3 enclosure internal | 040.1 | Evaporator HTF outlet temperature | PKG: 13119; -: -50 to +50oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-50/50C-4/20MA-L200-IP65 |  |  |  |  | 01
RU3 | RU3-TI-161 | RU3-T-161 | PLC/HMI | 107-MD | HMI temperature indication | IE31405 |  | Evaporator HTF outlet temperature | PKG: 13119; -: -50 to +50oC |  |  |  |  | SIEMENS | OP-17 |  |  |  |  | 01
RU3 | RU3-TT-161 | RU3-T-161 | FLD | 107-MD | Temperature transmitter | RU3 enclosure internal | 040.1 | Evaporator HTF outlet temperature | PKG: 13119; -: -50 to +50oC |  |  |  |  | GOOSS / MYCOM | Sen-TT-50/50C-4/20MA-L200-IP65 |  |  |  |  | 01
RU3 | RU3-XA-001 | RU3-X-001 | PCS | 107-MD | Chiller common alarm signal | PCS/IE31405 |  | RU3 chiller common alarm | PKG: 13087 |  |  |  |  | SIEMENS | S7-300 |  |  |  |  | 01
RU3 | RU3-XA-002 | RU3-X-002 | PCS | 107-MD | Chiller enclosure fan alarm signal | PCS/IE31405 |  | RU3 chiller enclosure fan alarm | PKG: 13088 |  |  |  |  | SIEMENS | S7-300 |  |  |  |  | 01
RU3 | RU3-XL-003 | RU3-X-003 | FLD | 107-MD | Ammonia high level alarm beacon | RU3 enclosure external | 040.1 | Ammonia high level alarm beacon | PKG: 13089 |  |  |  |  | CROWCON / LGM | V4 amber |  |  |  |  | 01
RU3 | RU3-XL-004 | RU3-X-004 | FLD | 107-MD | Ammonia high high level alarm beacon | RU3 enclosure external | 040.1 | Ammonia high high level alarm beacon | PKG: 13090 |  |  |  |  | CROWCON / LGM | V4 red |  |  |  |  | 01
RU4 | RU4-AAH-001 | RU4-A-001 | FLD | [5 empty] | REF: SIL; I.S: N.I.S; DI: DI |  |  | 35 | SIS
RU4 | RU4-AT-001 | RU4-A-001 | [6 empty] | REF: SIL
RU4 | RU4-AAH-002 | RU4-A-002 | FLD | [5 empty] | REF: SIL; I.S: N.I.S; DI: DI |  |  | 35 | SIS
RU4 | RU4-AT-002 | RU4-A-002 | [6 empty] | REF: SIL; REQ: 6
RU4 | RU4-AAH-003 | RU4-A-003 | FLD | [5 empty] | REF: SIL; I.S: N.I.S; DI: DI |  |  | 35 | SIS
RU4 | RU4-AT-003 | RU4-A-003 | [6 empty] | REF: SIL; REQ: 6
RU4 | RU4-AT-004 | RU4-A-004 | [6 empty] | REF: SIL; REQ: 6
RU4 | RU4-AT-005 | RU4-A-005 | [6 empty] | REF: SIL; REQ: 6
RU4 | RU4-XA-001 | RU4-X-001 | bar: PKG
RU4 | RU4-XL-001 | RU4-X-001 | bar: PKG
RU4 | RU4-XA-002 | RU4-X-002 | bar: PKG
RU4 | RU4-XL-002 | RU4-X-002 | bar: PKG
RU4 | RU4-XA-003 | RU4-X-003 | bar: PKG
RU4 | RU4-XL-003 | RU4-X-003 | bar: PKG
RU4 | RU4-XL-004 | RU4-X-004 | bar: PKG
RU4 | RU4-XL-005 | RU4-X-005 | bar: PKG
RU4 | RU4-XL-006 | RU4-X-006 | bar: PKG
RU4 | RU4-XL-007 | RU4-X-007 | bar: PKG
SC01 | SC01-AE-001 | SC01-A-001 | LCP | 107-JG | ELEMENT - ANALYSIS | LOCAL CONTROL PANEL | 8.1 | CONDUCTIVITY | PKG: 6359; REF: REF; REQ: REQ | [10 empty] | 30
SC01 | SC01-AI-001 | SC01-A-001 | LCP | 107-JG | INDICATOR - LOW ALARM | LOCAL CONTROL PANEL | 008.1 | CONDUCTIVITY | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  | Deleted |  | 30
SC01 | SC01-AIC-001 | SC01-A-001 | PCS | 107-JG | INDICATING CONTROLLER - ANALYSIS |  |  | CONDUCTIVITY | [11 empty] | 0 | [5 empty] | Deleted |  | 01
SC01 | SC01-AT-001 | SC01-A-001 | LCP | 107-JG | TRANSMITTER - ANALYSIS - COND. | LOCAL CONTROL PANEL | 008.1 | CONDUCTIVITY | 6359 | 0 to 1000 uS/cm | +/- 5% | REF | REQ | C |  | N.I.S | AI |  |  | 13 | UTIL | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  | Deleted |  | 30
SC01 | SC01-AE-002 | SC01-A-002 | LCP | 107-JG | ELEMENT - ANALYSIS | LOCAL CONTROL PANEL | 8.1 | PH | PKG: 6359; REF: REF; REQ: REQ | [5 empty] | CPA442 |  |  | Deleted
SC01 | SC01-AIC-002 | SC01-A-002 | PCS | 107-JG | INDICATING CONTROLLER - ANALYSIS |  |  | PH | [11 empty] | 0 | bar: PKG
SC01 | SC01-AT-002 | SC01-A-002 | LCP | 107-JG | TRANSMITTER - ANALYSIS - COND. | LOCAL CONTROL PANEL | 008.1 | PH |  | - | - | REF | REQ | C |  | N.I.S | AI |  |  | 13 | UTIL | ENDRESS + HAUSER | CPA442 |  |  | INCLUDING TT-003
SC01 | SC01-CV-001 | SC01-C-001 | PKG | 107-JG | BALL VALVE - ON/OFF - F.C. | SC01 | 008.1 | UTIL WATER SUPPLY | 8752 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC01 | SC01-CY-001 | SC01-C-001 | PKG | 107-JG | SOLENOID VALVE | SC01 |  | UTIL WATER SUPPLY | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC01 | SC01-ZSC-001 | SC01-C-001 | PKG | 107-JG | MICROSWITCH - CLOSED | MTD. ON VALVE |  | UTIL WATER SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-ZSO-001 | SC01-C-001 | PKG | 107-JG | MICROSWICH - OPEN | MTD. ON VALVE |  | UTIL WATER SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-CV-002 | SC01-C-002 | PKG | 107-JG | BALL VALVE - ON/OFF - F.C. | SC01 | 008.1 | 20% NaOH SUPPLY | 8755 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC01 | SC01-CY-002 | SC01-C-002 | PKG | 107-JG | SOLENOID VALVE | SC01 |  | 20% NaOH SUPPLY | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC01 | SC01-ZSC-002 | SC01-C-002 | PKG | 107-JG | MICROSWITCH - CLOSED | MTD. ON VALVE |  | 20% NaOH SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-ZSO-002 | SC01-C-002 | PKG | 107-JG | MICROSWICH - OPEN | MTD. ON VALVE |  | 20% NaOH SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-CV-003 | SC01-C-003 | PKG | 107-JG | BALL VALVE - ON/OFF - F.C. | SC01 | 008.1 | 30% HCl SUPPLY | 8769 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC01 | SC01-CY-003 | SC01-C-003 | PKG | 107-JG | SOLENOID VALVE | SC01 |  | 30% HCl SUPPLY | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC01 | SC01-ZSC-003 | SC01-C-003 | PKG | 107-JG | MICROSWITCH - CLOSED | MTD. ON VALVE |  | 30% HCl SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-ZSO-003 | SC01-C-003 | PKG | 107-JG | MICROSWICH - OPEN | MTD. ON VALVE |  | 30% HCl SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-CV-004 | SC01-C-004 | PKG | 107-JG | GLOBE VALVE - CONTROL - F.O. | SC01 | 008.1 | COOLING WATER RTN | 8776 | 0 T0 100% | - | REF | REQ | F |  | N.I.S | AO |  |  | 22 | UTIL | SCORPION / PRISMA /PMV | Ball/PP2/P-2000 |  |  |  |  | 01
SC01 | SC01-CV-005 | SC01-C-005 | PKG | 107-JG | VALVE - CONTROL - F.C. | STACK AIR INLET | 008.1 | BALANCED AIR INLET | 6356 | 0 T0 100% | - | REF | REQ | F |  | N.I.S | AO |  |  | 22 | UTIL | ADMIRAL / PRISMA / PMV | Butterfly/PP2/PMV |  |  |  |  | 01
SC01 | SC01-CV-006 | SC01-C-006 | PKG | 107-JG | BUTTERFLY VALVE - ON/OFF - F.O. | SC01-FN1 DISCHARGE | 008.1 | FN1 TO VENT | 6621 | - | - | REF | REQ | F | [5 empty] | 0 |  | ADMIRAL / PRISMA | Butterfly/PP2 |  |  |  |  | 01
SC01 | SC01-CY-006 | SC01-C-006 | PKG | 107-JG | SOLENOID VALVE | SC01 |  | FN1 TO VENT | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC01 | SC01-ZSC-006 | SC01-C-006 | PKG | 107-JG | MICROSWITCH - CLOSED | MTD. ON VALVE |  | FN1 TO VENT | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-ZSO-006 | SC01-C-006 | PKG | 107-JG | MICROSWICH - OPEN | MTD. ON VALVE |  | FN1 TO VENT | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-CV-007 | SC01-C-007 | PKG | 107-JG | BUTTERFLY VALVE - ON/OFF - F.O. | SC01-FN2 DISCHARGE | 008.1 | FN2 TO VENT | 6622 | - | - | REF | REQ | F | [5 empty] | 0 |  | ADMIRAL / PRISMA | Butterfly/PP2 |  |  |  |  | 01
SC01 | SC01-CY-007 | SC01-C-007 | PKG | 107-JG | SOLENOID VALVE | SC01 |  | FN2 TO VENT | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC01 | SC01-ZSC-007 | SC01-C-007 | PKG | 107-JG | MICROSWITCH - CLOSED | MTD. ON VALVE |  | FN2 TO VENT | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-ZSO-007 | SC01-C-007 | PKG | 107-JG | MICROSWICH - OPEN | MTD. ON VALVE |  | FN2 TO VENT | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-DIC-001 | SC01-D-001 | PCS | 107-JG | INDICATING CONTR. - MOTOR DRIVE |  |  | P1 RECIRC PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC01 | SC01-DS-001 | SC01-D-001 | LCP | 107-JG | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | P1 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-DY-001 | SC01-D-001 | LCP | 107-JG | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | P1 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-DYC-001 | SC01-D-001 | LCP | 107-JG | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.1 | P1 RECIRC PUMP | 8807 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC01 | SC01-DIC-002 | SC01-D-002 | PCS | 107-JG | INDICATING CONTR. - MOTOR DRIVE |  |  | P2 RECIRC PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC01 | SC01-DS-002 | SC01-D-002 | LCP | 107-JG | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | P2 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-DY-002 | SC01-D-002 | LCP | 107-JG | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | P2 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-DYC-002 | SC01-D-002 | LCP | 107-JG | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.1 | P2 RECIRC PUMP | 8818 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC01 | SC01-DIC-003 | SC01-D-003 | PCS | 107-JG | INDICATING CONTR. - MOTOR DRIVE |  |  | FN1 EXTRACT FAN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC01 | SC01-DS-003 | SC01-D-003 | LCP | 107-JG | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | FN1 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-DY-003 | SC01-D-003 | LCP | 107-JG | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | FN1 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-DYC-003 | SC01-D-003 | LCP | 107-JG | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.1 | FN1 EXTRACT FAN | 8825 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC01 | SC01-DIC-004 | SC01-D-004 | PCS | 107-JG | INDICATING CONTR. - MOTOR DRIVE |  |  | FN2 EXTRACT FAN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC01 | SC01-DS-004 | SC01-D-004 | LCP | 107-JG | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | FN2 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-DY-004 | SC01-D-004 | LCP | 107-JG | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | FN2 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC01 | SC01-DYC-004 | SC01-D-004 | LCP | 107-JG | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.1 | FN2 EXTRACT FAN | 8836 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC01 | SC01-FI-001 | SC01-F-001 | PCS | 107-JG | INDICATOR - FLOW |  |  | CU1 OUTLET FLOW | REQ: By request |  |  | 0 | [7 empty] | 01
SC01 | SC01-FT-001 | SC01-F-001 | PKG | 107-JG | TRANSMITTER - FLOW | SC01 | 008.1 | CU1 OUTLET FLOW | REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 12 | UTIL | GEMU | 815/50/39.22.04-5-72-4M3H |  |  |  |  | 01
SC01 | SC01-HS-001 | SC01-H-001 | LCP | 107-JG | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.1 | PUMP 1 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-002A | SC01-H-002 | LCP | 107-JG | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.1 | PUMP 1 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-002B | SC01-H-002 | LCP | 107-JG | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.1 | PUMP 1 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-003 | SC01-H-003 | LCP | 107-JG | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.1 | PUMP 2 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-004A | SC01-H-004 | LCP | 107-JG | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.1 | PUMP 2 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-004B | SC01-H-004 | LCP | 107-JG | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.1 | PUMP 2 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-005 | SC01-H-005 | LCP | 107-JG | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.1 | FAN 1 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-006A | SC01-H-006 | LCP | 107-JG | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.1 | FAN 1 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-006B | SC01-H-006 | LCP | 107-JG | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.1 | FAN 1 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-007 | SC01-H-007 | LCP | 107-JG | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.1 | FAN 2 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-008A | SC01-H-008 | LCP | 107-JG | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.1 | FAN 2 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-HS-008B | SC01-H-008 | LCP | 107-JG | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.1 | FAN 2 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-LAL-001A | SC01-L-001 | PCS | 107-JG | ALARM - LEVEL - LOW |  |  | LOW LEVEL | PKG: L15865; -: On/off; -: On/off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
SC01 | SC01-LAL-001B | SC01-L-001 | LCP | 107-JG | ALARM - LEVEL - LOW | LOCAL CONTROL PANEL | 008.1 | LOW LEVEL | -: -; -: -; REF: REF; REQ: 12; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-LSL-001 | SC01-L-001 | PKG | 107-JG | SWITCH - LEVEL - LOW | SC01 | 008.1 | LOW LEVEL | L15865 | On/off | On/off | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | UTIL | KSR KEUBLER | AFH |  |  |  |  | 01
SC01 | SC01-LI-002 | SC01-L-002 | PCS | 107-JG | INDICATOR - LEVEL |  |  | LEVEL | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC01 | SC01-LT-002 | SC01-L-002 | PKG | 107-JG | TRANSMITTER - LEVEL | SC01-ST1 | 008.1 | LEVEL | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 12 | UTIL | KSR KEUBLER | BNA |  |  |  |  | 01
SC01 | SC01-PI-001 | SC01-P-001 | PKG | 107-JG | PRESSURE GAUGE - DIAPHRAGM | SC01 | 008.1 | P2 DISCHARGE PRESSURE | -: 0 to 2.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | STEWART BUCHANAN | 2033/F/GF |  |  |  |  | 01
SC01 | SC01-PI-002 | SC01-P-002 | PKG | 107-JG | PRESSURE GAUGE - DIAPHRAGM | SC01 | 008.1 | P1 DISCHARGE PRESSURE | -: 0 to 2.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | STEWART BUCHANAN | 2033/F/GF |  |  |  |  | 01
SC01 | SC01-PDAH-003 | SC01-P-003 | PCS | 107-JG | ALARM - PRESSURE - DIFF - HIGH |  |  | PS1 DIFF PRESSURE | REQ: By request |  |  | 0 | [7 empty] | 01
SC01 | SC01-PDSH-003 | SC01-P-003 | PKG | 107-JG | SWITCH - PRESSURE - DIFF - HIGH | SC01-PS1 | 008.1 | PS1 DIFF PRESSURE | REQ: By request; F: C; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | DELTA CONTROLS LTD | W30101C604F |  |  |  |  | 01
SC01 | SC01-PIC-005 | SC01-P-005 | PCS | 107-JG | INDICATING CONTROLLER - PRESSURE |  |  | ALK GAS INLET PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC01 | SC01-PT-005 | SC01-P-005 | FLD | 107-JG | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-SV-GR1A-0-9026000 | 008.1 | ALK GAS INLET PRESSURE | L6715 | -100 to 50 mbarg | +/-10mbarg | SHE | 24 | C |  | I.S | AI |  |  | 11 | UTIL | ROSEMOUNT | 3051 TG (Note 1) | KP0001 | TI702-SP-5046 |  |  | 01
SC01 | SC01-PDI-007 | SC01-P-007 | PCS | 107-JG | INDICATOR - DIFF PRESSURE |  |  | FN1/2 DIFF PRESSURE | REQ: By request |  |  | 0 | [7 empty] | 01
SC01 | SC01-PDT-007 | SC01-P-007 | PKG | 107-JG | TRANSMITTER - PRESSURE - DIFF | SC01-FN1/2 | 008.1 | FN1/2 DIFF PRESSURE | REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 12 | UTIL | YOKOGAWA | EJA110A |  |  |  |  | 01
SC01 | SC01-PSV-011 | SC01-P-011 | PKG | 107-JG | PRESSURE RELIEF VALVE | SC01 | 008.1 | CU1 COOLING WATER RELIEF | -: 5.0 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | TBA | VTA |  |  |  |  | 01
SC01 | SC01-RV-001 | SC01-R-001 | PKG | 107-JG | VACUUM BREATHER VALVE | SC01 | 008.1 | INLET HEADER RELIEF | -: -25 mbarg; -: -; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
SC01 | SC01-RV-002 | SC01-R-002 | DEL | 107-JG | VACUUM BREATHER VALVE | DELETED |  | DELETED | [11 empty] | 0 | [5 empty] | DELETED |  | 01 | bar: -
SC01 | SC01-SE-001 | SC01-S-001 | PKG | 107-JG | ELEMENT - SPEED | SC01-FN1 | 008.1 | FN1 SPEED | -: -; REF: REF; REQ: By request; F: F |  |  | 0 |  | PEPPERL + FUCHS | NJ5-18GK-N |  |  | 2 pulses/rev |  | 01
SC01 | SC01-SI-001 | SC01-S-001 | PCS | 107-JG | INDICATOR - SPEED |  |  | FN1 SPEED | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC01 | SC01-ST-001 | SC01-S-001 | LCP | 107-JG | TRANSMITTER - SPEED | LOCAL CONTROL PANEL | 008.1 | FN1 SPEED | REF: REF; REQ: By request; F: F; I.S: N.I.S; DI: AI |  |  | 13 | UTIL | PEPPERL + FUCHS | [5 empty] | 01
SC01 | SC01-SE-002 | SC01-S-002 | PKG | 107-JG | ELEMENT - SPEED | SC01-FN2 | 008.1 | FN2 SPEED | -: -; REF: REF; REQ: By request; F: F |  |  | 0 |  | PEPPERL + FUCHS | NJ5-18GK-N |  |  | 2 pulses/rev |  | 01
SC01 | SC01-SI-002 | SC01-S-002 | PCS | 107-JG | INDICATOR - SPEED |  |  | FN2 SPEED | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC01 | SC01-ST-002 | SC01-S-002 | LCP | 107-JG | TRANSMITTER - SPEED | LOCAL CONTROL PANEL | 008.1 | FN2 SPEED | REF: REF; REQ: By request; F: F; I.S: N.I.S; DI: AI |  |  | 13 | UTIL | PEPPERL + FUCHS | [5 empty] | 01
SC01 | SC01-TE-003 | SC01-T-003 | PKG | 107-JG | ELEMENT - TEMPERATURE - RTD | SC01 |  | CU1 OUTLET TEMPERATURE | PKG: L8883; -: 0 to 60 degC; -: +/- 2degC; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
SC01 | SC01-TIC-003 | SC01-T-003 | PCS | 107-JG | INDICATING CONTROLLER - TEMPERATURE |  |  | CU1 OUTLET TEMPERATURE | PKG: L8883; -: 0 to 60 degC; -: +/-2degC; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
SC01 | SC01-TT-003 | SC01-T-003 | LCP | 107-JG | TRANSMITTER - TEMPERATURE | LOCAL CONTROL PANEL | 008.1 | CU1 OUTLET TEMPERATURE | L8883 | 0 to 60 degC | +/-2degC | SHE | 24 | C |  | N.I.S | AI |  |  | 13 | UTIL | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  | INTEGRAL WITH AT-002 |  | 01
SC01 | SC01-TE-004 | SC01-T-004 | FLD | 107-JG | ELEMENT - TEMPERATURE - RTD | 100-SV-GR1A-0-9026000 |  | ALK GAS INLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
SC01 | SC01-TI-004 | SC01-T-004 | PCS | 107-JG | INDICATOR - TEMPERATURE |  |  | ALK GAS INLET TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
SC01 | SC01-TT-004 | SC01-T-004 | FLD | 107-JG | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 008.1 | ALK GAS INLET TEMPERATURE | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 01
SC01 | SC01-YI-001 | SC01-Y-001 | LCP | 107-JG | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.1 | PUMP 1 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-YI-002 | SC01-Y-002 | LCP | 107-JG | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.1 | PUMP 2 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-YI-003 | SC01-Y-003 | LCP | 107-JG | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.1 | FAN 1 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-YI-004 | SC01-Y-004 | LCP | 107-JG | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.1 | FAN 2 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-YI-005 | SC01-Y-005 | LCP | 107-JG | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.1 | PUMP 1 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-YI-006 | SC01-Y-006 | LCP | 107-JG | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.1 | PUMP 2 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-YI-007 | SC01-Y-007 | LCP | 107-JG | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.1 | FAN 1 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC01 | SC01-YI-008 | SC01-Y-008 | LCP | 107-JG | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.1 | FAN 2 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-AE-001 | SC02-A-001 | LCP | 107-JH | ELEMENT - ANALYSIS | LOCAL CONTROL PANEL | 008.2 | CONDUCTIVITY | PKG: 8884; REQ: REQ | [8 empty] | Deleted |  | 30
SC02 | SC02-AI-001 | SC02-A-001 | LCP | 107-JH | INDICATOR - LOW ALARM | LOCAL CONTROL PANEL | 008.2 | CONDUCTIVITY | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  | Deleted |  | 30
SC02 | SC02-AIC-001 | SC02-A-001 | PCS | 107-JH | INDICATING CONTROLLER - ANALYSIS |  |  | CONDUCTIVITY | [11 empty] | 0 | [5 empty] | Deleted |  | 01
SC02 | SC02-AT-001 | SC02-A-001 | LCP | 107-JH | TRANSMITTER - ANALYSIS - COND. | LOCAL CONTROL PANEL | 008.2 | CONDUCTIVITY | 8884 | 0 to 1000 uS/cm | +/- 5% |  | REQ | C |  | N.I.S | AI |  |  | 13 | UTIL | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  | Deleted |  | 30
SC02 | SC02-AE-002 | SC02-A-002 | LCP | 107-JH | ELEMENT - ANALYSIS | LOCAL CONTROL PANEL | 008.2 | CONDUCTIVITY | PKG: 8884; REQ: REQ | [10 empty] | 30
SC02 | SC02-AIC-002 | SC02-A-002 | PCS | 107-JH | INDICATING CONTROLLER - ANALYSIS |  |  | CONDUCTIVITY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC02 | SC02-AT-002 | SC02-A-002 | LCP | 107-JH | TRANSMITTER - ANALYSIS - COND. | LOCAL CONTROL PANEL | 008.2 | CONDUCTIVITY |  | - | - | REF | REQ | C |  | N.I.S | AI |  |  | 13 | UTIL | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  | INCLUDING TT-003 |  | 30
SC02 | SC02-CV-001 | SC02-C-001 | PKG | 107-JH | BALL VALVE - ON/OFF - F.C. | SC02 | 008.2 | UTIL WATER SUPPLY | 8885 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC02 | SC02-CY-001 | SC02-C-001 | PKG | 107-JH | SOLENOID VALVE | SC02 |  | UTIL WATER SUPPLY | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC02 | SC02-ZSC-001 | SC02-C-001 | PKG | 107-JH | MICROSWITCH - CLOSED | MTD. ON VALVE |  | UTIL WATER SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-ZSO-001 | SC02-C-001 | PKG | 107-JH | MICROSWICH - OPEN | MTD. ON VALVE |  | UTIL WATER SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-CV-002 | SC02-C-002 | PKG | 107-JH | BALL VALVE - ON/OFF - F.C. | SC02 | 008.2 | 20% NaOH SUPPLY | 7089 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC02 | SC02-CY-002 | SC02-C-002 | PKG | 107-JH | SOLENOID VALVE | SC02 |  | 20% NaOH SUPPLY | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC02 | SC02-ZSC-002 | SC02-C-002 | PKG | 107-JH | MICROSWITCH - CLOSED | MTD. ON VALVE |  | 20% NaOH SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-ZSO-002 | SC02-C-002 | PKG | 107-JH | MICROSWICH - OPEN | MTD. ON VALVE |  | 20% NaOH SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-CV-003 | SC02-C-003 | PKG | 107-JH | BALL VALVE - ON/OFF - F.C. | SC02 | 008.2 | 30% HCl SUPPLY | 8886 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC02 | SC02-CY-003 | SC02-C-003 | PKG | 107-JH | SOLENOID VALVE | SC02 |  | 30% HCl SUPPLY | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC02 | SC02-ZSC-003 | SC02-C-003 | PKG | 107-JH | MICROSWITCH - CLOSED | MTD. ON VALVE |  | 30% HCl SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-ZSO-003 | SC02-C-003 | PKG | 107-JH | MICROSWICH - OPEN | MTD. ON VALVE |  | 30% HCl SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-CV-004 | SC02-C-004 | PKG | 107-JH | GLOBE VALVE - CONTROL - F.O. | SC02 | 008.2 | COOLING WATER RTN | 8887 | 0 T0 100% | - | REF | REQ | F |  | N.I.S | AO |  |  | 22 | UTIL | SCORPION / PRISMA /PMV | Ball/PP1/P-2000 |  |  |  |  | 01
SC02 | SC02-CV-005 | SC02-C-005 | PKG | 107-JH | VALVE - CONTROL - F.C. | STACK AIR INLET | 008.2 | BALANCED AIR INLET | 8888 | 0 T0 100% | - | REF | REQ | F |  | N.I.S | AO |  |  | 22 | UTIL | ADMIRAL / PRISMA / PMV | Butterfly/PP2/P-2000 |  |  |  |  | 01
SC02 | SC02-CV-006 | SC02-C-006 | PKG | 107-JH | BALL VALVE - ON/OFF - F.O. | SC02-FN1 DISCHARGE | 008.2 | FN1 TO VENT | 8889 | - | - | REF | REQ | F | [5 empty] | 0 |  | ADMIRAL / PRISMA | Butterfly/PP2 |  |  |  |  | 01
SC02 | SC02-CY-006 | SC02-C-006 | PKG | 107-JH | SOLENOID VALVE | SC02 |  | FN1 TO VENT | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC02 | SC02-ZSC-006 | SC02-C-006 | PKG | 107-JH | MICROSWITCH - CLOSED | MTD. ON VALVE |  | FN1 TO VENT | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-ZSO-006 | SC02-C-006 | PKG | 107-JH | MICROSWICH - OPEN | MTD. ON VALVE |  | FN1 TO VENT | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-CV-007 | SC02-C-007 | PKG | 107-JH | BALL VALVE - ON/OFF - F.O. | SC02-FN2 DISCHARGE | 008.2 | FN2 TO VENT | 8890 | - | - | REF | REQ | F | [5 empty] | 0 |  | ADMIRAL / PRISMA | Butterfly/PP2 |  |  |  |  | 01
SC02 | SC02-CY-007 | SC02-C-007 | PKG | 107-JH | SOLENOID VALVE | SC02 |  | FN2 TO VENT | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC02 | SC02-ZSC-007 | SC02-C-007 | PKG | 107-JH | MICROSWITCH - CLOSED | MTD. ON VALVE |  | FN2 TO VENT | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-ZSO-007 | SC02-C-007 | PKG | 107-JH | MICROSWICH - OPEN | MTD. ON VALVE |  | FN2 TO VENT | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-CV-008 | SC02-C-008 | FLD | 107-JH | BALL VALVE - ON/OFF - F.I.P. | 100-SV-GR1A-0-9026200 | 008.2 | SC02 HEADER TO SCRUBBER 02 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 52
SC02 | SC02-CY-008A | SC02-C-008 | FLD | 107-JH | SOLENOID VALVE - CLOSED | RACK MOUNTED |  | SC02 HEADER TO SCRUBBER 02 | I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 52
SC02 | SC02-CY-008B | SC02-C-008 | FLD | 107-JH | SOLENOID VALVE - OPEN | RACK MOUNTED |  | SC02 HEADER TO SCRUBBER 02 | I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 52
SC02 | SC02-ZSC-008 | SC02-C-008 | FLD | 107-JH | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SC02 HEADER TO SCRUBBER 02 | I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5017 |  |  | 01
SC02 | SC02-ZSO-008 | SC02-C-008 | FLD | 107-JH | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SC02 HEADER TO SCRUBBER 02 | I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 52
SC02 | SC02-CV-009 | SC02-C-009 | FLD | 107-JH | BALL VALVE - ON/OFF - F.I.P. | 100-SV-GR1A-0-9026655 | 008.2 | SC02 HEADER TO SCRUBBER 01 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | XOMOX TUFLIN | R202 | KV0007 |  |  |  | 52
SC02 | SC02-CY-009A | SC02-C-009 | FLD | 107-JH | SOLENOID VALVE - CLOSED | RACK MOUNTED |  | SC02 HEADER TO SCRUBBER 01 | I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 52
SC02 | SC02-CY-009B | SC02-C-009 | FLD | 107-JH | SOLENOID VALVE - OPEN | RACK MOUNTED |  | SC02 HEADER TO SCRUBBER 01 | I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 52
SC02 | SC02-ZSC-009 | SC02-C-009 | FLD | 107-JH | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SC02 HEADER TO SCRUBBER 01 | I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 52
SC02 | SC02-ZSO-009 | SC02-C-009 | FLD | 107-JH | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SC02 HEADER TO SCRUBBER 01 | I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 52
SC02 | SC02-DIC-001 | SC02-D-001 | PCS | 107-JH | INDICATING CONTR. - MOTOR DRIVE |  |  | P1 RECIRC PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC02 | SC02-DS-001 | SC02-D-001 | LCP | 107-JH | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | P1 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-DY-001 | SC02-D-001 | LCP | 107-JH | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | P1 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-DYC-001 | SC02-D-001 | LCP | 107-JH | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.2 | P1 RECIRC PUMP | 8891 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC02 | SC02-DIC-002 | SC02-D-002 | PCS | 107-JH | INDICATING CONTR. - MOTOR DRIVE |  |  | P2 RECIRC PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC02 | SC02-DS-002 | SC02-D-002 | LCP | 107-JH | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | P2 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-DY-002 | SC02-D-002 | LCP | 107-JH | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | P2 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-DYC-002 | SC02-D-002 | LCP | 107-JH | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.2 | P2 RECIRC PUMP | 8892 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC02 | SC02-DIC-003 | SC02-D-003 | PCS | 107-JH | INDICATING CONTR. - MOTOR DRIVE |  |  | FN1 EXTRACT FAN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC02 | SC02-DS-003 | SC02-D-003 | LCP | 107-JH | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | FN1 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-DY-003 | SC02-D-003 | LCP | 107-JH | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | FN1 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-DYC-003 | SC02-D-003 | LCP | 107-JH | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.2 | FN1 EXTRACT FAN | 8893 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC02 | SC02-DIC-004 | SC02-D-004 | PCS | 107-JH | INDICATING CONTR. - MOTOR DRIVE |  |  | FN2 EXTRACT FAN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC02 | SC02-DS-004 | SC02-D-004 | LCP | 107-JH | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | FN2 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-DY-004 | SC02-D-004 | LCP | 107-JH | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | FN2 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC02 | SC02-DYC-004 | SC02-D-004 | LCP | 107-JH | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.2 | FN2 EXTRACT FAN | 8894 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC02 | SC02-FI-001 | SC02-F-001 | PCS | 107-JH | INDICATOR - FLOW |  |  | CU1 OUTLET FLOW | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC02 | SC02-FT-001 | SC02-F-001 | PKG | 107-JH | TRANSMITTER - FLOW | SC02 | 008.2 | CU1 OUTLET FLOW | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 12 | UTIL | GEMU | 815/40/39.22.04-5-69 |  |  |  |  | 01
SC02 | SC02-HS-001 | SC02-H-001 | LCP | 107-JH | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.2 | PUMP 1 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-002A | SC02-H-002 | LCP | 107-JH | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.2 | PUMP 1 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-002B | SC02-H-002 | LCP | 107-JH | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.2 | PUMP 1 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-003 | SC02-H-003 | LCP | 107-JH | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.2 | PUMP 2 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-004A | SC02-H-004 | LCP | 107-JH | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.2 | PUMP 2 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-004B | SC02-H-004 | LCP | 107-JH | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.2 | PUMP 2 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-005 | SC02-H-005 | LCP | 107-JH | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.2 | FAN 1 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-006A | SC02-H-006 | LCP | 107-JH | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.2 | FAN 1 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-006B | SC02-H-006 | LCP | 107-JH | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.2 | FAN 1 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-007 | SC02-H-007 | LCP | 107-JH | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.2 | FAN 2 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-008A | SC02-H-008 | LCP | 107-JH | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.2 | FAN 2 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-HS-008B | SC02-H-008 | LCP | 107-JH | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.2 | FAN 2 LOCAL STOP/START | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-LAL-001A | SC02-L-001 | PCS | 107-JH | ALARM - LEVEL - LOW |  |  | LOW LEVEL | PKG: L15866; -: On/off; -: On/off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
SC02 | SC02-LAL-001B | SC02-L-001 | LCP | 107-JH | ALARM - LEVEL - LOW | LOCAL CONTROL PANEL | 008.2 | LOW LEVEL | -: -; -: -; REF: REF; REQ: 12; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-LSL-001 | SC02-L-001 | PKG | 107-JH | SWITCH - LEVEL - LOW | SC02-ST1 | 008.2 | LOW LEVEL | L15866 | On/off | On/off | SHE | 24 | F |  | N.I.S | DI |  |  | 35 | UTIL | KSR KEUBLER | AFH |  |  |  |  | 01
SC02 | SC02-LI-002 | SC02-L-002 | PCS | 107-JH | INDICATOR - LEVEL |  |  | LEVEL | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC02 | SC02-LT-002 | SC02-L-002 | PKG | 107-JH | TRANSMITTER - LEVEL | SC02-ST1 | 008.2 | LEVEL | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 12 | UTIL | KSR KEUBLER | BNA |  |  |  |  | 01
SC02 | SC02-PI-001 | SC02-P-001 | PKG | 107-JH | PRESSURE GAUGE - DIAPHRAGM | SC02 | 008.2 | P2 DISCHARGE PRESSURE | -: 0 to 2.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
SC02 | SC02-PI-002 | SC02-P-002 | PKG | 107-JH | PRESSURE GAUGE - DIAPHRAGM | SC02 | 008.2 | P1 DISCHARGE PRESSURE | -: 0 to 2.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
SC02 | SC02-PDAH-003 | SC02-P-003 | PCS | 107-JH | ALARM - PRESSURE - DIFF - HIGH |  |  | PS1 DIFF PRESSURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC02 | SC02-PDSH-003 | SC02-P-003 | PKG | 107-JH | SWITCH - PRESSURE - DIFF - HIGH | SC02-PS1 | 008.2 | PS1 DIFF PRESSURE | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | DELTA CONTROLS LTD | W30101C404F |  |  |  |  | 01
SC02 | SC02-PIC-005 | SC02-P-005 | PCS | 107-JH | INDICATING CONTROLLER - PRESSURE |  |  | ACID GAS INLET PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC02 | SC02-PIT-005 | SC02-P-005 | [6 empty] | PKG: L6716; -: -100 to 50 mbarg; -: +/-10 mbarg; REF: REF; REQ: 24
SC02 | SC02-PT-005 | SC02-P-005 | FLD | 107-JH | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-SV-GR1A-0-9026200 | 008.2 | ACID GAS INLET PRESSURE | L15867 | -100 to 50 mbarg | +/-10 mbarg | REF | 24 | C |  | I.S | AI |  |  | 11 | UTIL | ROSEMOUNT | 3051 TG (Note 1) | KP0001 | TI702-SP-5046 |  |  | 01
SC02 | SC02-PDI-007 | SC02-P-007 | PCS | 107-JH | INDICATOR - DIFF PRESSURE |  |  | FN1/2 DIFF PRESSURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC02 | SC02-PDT-007 | SC02-P-007 | PKG | 107-JH | TRANSMITTER - PRESSURE - DIFF | SC02-FN1 | 008.2 | FN1/2 DIFF PRESSURE | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 12 | UTIL | ROSEMOUNT | 3051S |  |  |  |  | 01
SC02 | SC02-PSV-011 | SC02-P-011 | PKG | 107-JH | PRESSURE RELIEF VALVE | SC02 | 008.2 | CU1 COOLING WATER RELIEF | -: 5.0 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | TBA | VTA |  |  |  |  | 01
SC02 | SC02-RV-001 | SC02-R-001 | PKG | 107-JH | VACUUM BREATHER VALVE | SC02 | 008.2 | INLET HEADER RELIEF | -: -25 mbarg; -: -; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
SC02 | SC02-RV-002 | SC02-R-002 | DEL | 107-JH | VACUUM BREATHER VALVE | DELETED |  | DELETED | [11 empty] | 0 | [5 empty] | DELETED |  | 01 | bar: -
SC02 | SC02-SE-001 | SC02-S-001 | PKG | 107-JH | ELEMENT - SPEED | SC02-FN1 | 008.2 | FN1 SPEED | REF: REF; REQ: By request; F: F |  |  | 0 | [5 empty] | 2 pulses/rev |  | 01
SC02 | SC02-SI-001 | SC02-S-001 | PCS | 107-JH | INDICATOR - SPEED |  |  | FN1 SPEED | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC02 | SC02-ST-001 | SC02-S-001 | LCP | 107-JH | TRANSMITTER - SPEED | LOCAL CONTROL PANEL | 008.2 | FN1 SPEED | REF: REF; REQ: By request; F: F; I.S: N.I.S; DI: AI |  |  | 13 | UTIL | [6 empty] | 01
SC02 | SC02-SE-002 | SC02-S-002 | PKG | 107-JH | ELEMENT - SPEED | SC02-FN2 | 008.2 | FN2 SPEED | REF: REF; REQ: By request; F: F |  |  | 0 | [5 empty] | 2 pulses/rev |  | 01
SC02 | SC02-SI-002 | SC02-S-002 | PCS | 107-JH | INDICATOR - SPEED |  |  | FN2 SPEED | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC02 | SC02-ST-002 | SC02-S-002 | LCP | 107-JH | TRANSMITTER - SPEED | LOCAL CONTROL PANEL | 008.2 | FN2 SPEED | REF: REF; REQ: By request; F: F; I.S: N.I.S; DI: AI |  |  | 13 | UTIL | [6 empty] | 01
SC02 | SC02-TE-003 | SC02-T-003 | PKG | 107-JH | ELEMENT - TEMPERATURE - RTD | SC02 |  | CU1 OUTLET TEMPERATURE | PKG: L8903; -: 0 to 60 degC; -: +/- 2degC; REF: SHE; REQ: 24 |  |  | 0 |  | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  |  |  | 01
SC02 | SC02-TIC-003 | SC02-T-003 | PCS | 107-JH | INDICATING CONTROLLER - TEMPERATURE |  |  | CU1 OUTLET TEMPERATURE | PKG: L8903; -: 0 to 60 degC; -: +/- 2degC; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
SC02 | SC02-TT-003 | SC02-T-003 | LCP | 107-JH | TRANSMITTER - TEMPERATURE | LOCAL CONTROL PANEL | 008.2 | CU1 OUTLET TEMPERATURE | L8903 | 0 to 60 degC | +/- 2degC | SHE | 24 | C |  | N.I.S | AI |  |  | 13 | UTIL | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  | INTEGRAL WITH AT-001 |  | 01
SC02 | SC02-TE-004 | SC02-T-004 | FLD | 107-JH | ELEMENT - TEMPERATURE - RTD | 100-SV-GR1A-0-9026200 |  | ACID GAS INLET TEMPERATURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC02 | SC02-TI-004 | SC02-T-004 | PCS | 107-JH | INDICATOR - TEMPERATURE |  |  | ACID GAS INLET TEMPERATURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC02 | SC02-TT-004 | SC02-T-004 | FLD | 107-JH | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 008.2 | ACID GAS INLET TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 01
SC02 | SC02-YI-001 | SC02-Y-001 | LCP | 107-JH | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.2 | PUMP 1 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-YI-002 | SC02-Y-002 | LCP | 107-JH | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.2 | PUMP 2 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-YI-003 | SC02-Y-003 | LCP | 107-JH | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.2 | FAN 1 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-YI-004 | SC02-Y-004 | LCP | 107-JH | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.2 | FAN 2 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-YI-005 | SC02-Y-005 | LCP | 107-JH | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.2 | PUMP 1 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-YI-006 | SC02-Y-006 | LCP | 107-JH | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.2 | PUMP 2 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-YI-007 | SC02-Y-007 | LCP | 107-JH | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.2 | FAN 1 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC02 | SC02-YI-008 | SC02-Y-008 | LCP | 107-JH | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.2 | FAN 2 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC03 | SC03-AE-001 | SC03-A-001 | PKG | 107-JJ | ELEMENT - ANALYSIS |  | 008.3 | CONDUCTIVITY | REQ: By request | [10 empty] | 30
SC03 | SC03-AI-001 | SC03-A-001 | [6 empty] | REQ: By request
SC03 | SC03-AIC-001 | SC03-A-001 | PCS | 107-JJ | INDICATING CONTROLLER - ANALYSIS |  |  | CONDUCTIVITY | REQ: By request |  |  | 0 | [7 empty] | 01
SC03 | SC03-AT-001 | SC03-A-001 | PKG | 107-JJ | TRANSMITTER - ANALYSIS - COND. | SC03-ST1 | 008.3 | CONDUCTIVITY | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | ENDRESS + HAUSER | CLM153-G1A00A000 |  | TI702-SP-5166 | INCLUDING TT-003 |  | 30
SC03 | SC03-AI-002 | SC03-A-002 | [6 empty] | REQ: By request
SC03 | SC03-AIC-002 | SC03-A-002 | PCS | 107-JJ | INDICATING CONTROLLER - ANALYSIS |  |  | OXYGEN | [11 empty] | 0 | [7 empty] | 20 | bar: PKG
SC03 | SC03-AT-002 | SC03-A-002 | PKG | 107-JJ | TRANSMITTER - ANALYSIS - OXYGEN. | SC03-ST1 | 008.3 | OXYGEN | REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 11 | UTIL | TELEDYNE | 3010PACG |  |  |  |  | 20
SC03 | SC03-AI-003 | SC03-A-003 | PCS | 107-JJ | INDICATING CONTROLLER - ANALYSIS |  |  | pH ANALYSIS | [11 empty] | 0 | [7 empty] | 20 | bar: PKG
SC03 | SC03-AIC-003 | SC03-A-003 | [6 empty] | REQ: By request
SC03 | SC03-AIT-003 | SC03-A-003 | [6 empty] | REQ: By request
SC03 | SC03-AT-003 | SC03-A-003 | PKG | 107-JJ | TRANSMITTER - ANALYSIS - pH | SC03-ST1 | 008.3 | pH ANALYSIS | ???? | 1 to 14 |  |  | 6 | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | CPM253-MR4105 |  | NOT REQUIRED | NON IS FIELD DEVICE |  | 20
SC03 | SC03-CV-001 | SC03-C-001 | PKG | 107-JJ | BALL VALVE - ON/OFF - F.C. | SC03 | 008.3 | UTIL WATER SUPPLY | 8905 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC03 | SC03-CY-001 | SC03-C-001 | FLD | 107-JJ | SOLENOID VALVE | RACK MOUNTED |  | UTIL WATER SUPPLY | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
SC03 | SC03-ZSC-001 | SC03-C-001 | FLD | 107-JJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | UTIL WATER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-ZSO-001 | SC03-C-001 | FLD | 107-JJ | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | UTIL WATER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-CV-002 | SC03-C-002 | PKG | 107-JJ | BALL VALVE - ON/OFF - F.C. | SC03 | 008.3 | 20% NaOH SUPPLY | 8906 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC03 | SC03-CY-002 | SC03-C-002 | FLD | 107-JJ | SOLENOID VALVE | RACK MOUNTED |  | 20% NaOH SUPPLY | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
SC03 | SC03-ZSC-002 | SC03-C-002 | FLD | 107-JJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 20% NaOH SUPPLY | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-ZSO-002 | SC03-C-002 | FLD | 107-JJ | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 20% NaOH SUPPLY | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-CV-003 | SC03-C-003 | PKG | 107-JJ | BALL VALVE - ON/OFF - F.C. | SC03 | 008.3 | 30% HCl SUPPLY | 8907 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC03 | SC03-CY-003 | SC03-C-003 | FLD | 107-JJ | SOLENOID VALVE | RACK MOUNTED |  | 30% HCl SUPPLY | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
SC03 | SC03-ZSC-003 | SC03-C-003 | FLD | 107-JJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | 30% HCl SUPPLY | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-ZSO-003 | SC03-C-003 | FLD | 107-JJ | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | 30% HCl SUPPLY | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-CV-004 | SC03-C-004 | PKG | 107-JJ | GLOBE VALVE - CONTROL - F.O. | SC03 | 008.3 | COOLING WATER RTN | 8908 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | SCORPION / PRISMA /PMV | Ball/PP1/P-2000 |  | TI702-SP-5062 |  |  | 01
SC03 | SC03-CV-005 | SC03-C-005 | PKG | 107-JJ | VALVE - CONTROL - F.C. | STACK AIR INLET | 008.3 | BALANCED AIR INLET | 8909 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | ADMIRAL / PRISMA / PMV | Butterfly/PP2/P-2000 |  | TI702-SP-5062 |  |  | 01
SC03 | SC03-CV-006 | SC03-C-006 | PKG | 107-JJ | BALL VALVE - ON/OFF - F.O. | SC03-FN1 DISCHARGE | 008.3 | FN1 TO VENT | 8910 | - | - | REF | REQ | F | [5 empty] | 0 |  | ADMIRAL / PRISMA | Butterfly/PP2 |  |  |  |  | 01
SC03 | SC03-CY-006 | SC03-C-006 | FLD | 107-JJ | SOLENOID VALVE | RACK MOUNTED |  | FN1 TO VENT | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
SC03 | SC03-ZSC-006 | SC03-C-006 | FLD | 107-JJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | FN1 TO VENT | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-ZSO-006 | SC03-C-006 | FLD | 107-JJ | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | FN1 TO VENT | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-CV-007 | SC03-C-007 | PKG | 107-JJ | BALL VALVE - ON/OFF - F.O. | SC03-FN2 DISCHARGE | 008.3 | FN2 TO VENT | 8911 | - | - | REF | REQ | F | [5 empty] | 0 |  | ADMIRAL / PRISMA | Butterfly/PP2 |  |  |  |  | 01
SC03 | SC03-CY-007 | SC03-C-007 | FLD | 107-JJ | SOLENOID VALVE | RACK MOUNTED |  | FN2 TO VENT | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
SC03 | SC03-ZSC-007 | SC03-C-007 | FLD | 107-JJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | FN2 TO VENT | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-ZSO-007 | SC03-C-007 | FLD | 107-JJ | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | FN2 TO VENT | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ5-11-N-G |  | TI702-SP-5032 |  |  | 01
SC03 | SC03-CV-008 | SC03-C-008 | FLD | 107-JJ | BALL VALVE - ON/OFF - F.C. | 25-N-SS1U-0-9026688 | 008.3 | N2 PURGE | 14377 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
SC03 | SC03-CY-008 | SC03-C-008 | FLD | 107-JJ | SOLENOID VALVE | RACK MOUNTED | 008.3 | N2 PURGE | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
SC03 | SC03-ZSC-008 | SC03-C-008 | FLD | 107-JJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 008.3 | N2 PURGE | PKG: 14377; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
SC03 | SC03-ZSO-008 | SC03-C-008 | FLD | 107-JJ | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 008.3 | N2 PURGE | PKG: 14377; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
SC03 | SC03-CY-009 | SC03-C-009 | FLD | 107-JJ | SOLENOID VALVE | RACK MOUNTED | 008.3 | O2 PURGE | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 20
SC03 | SC03-CV-008A | SC03-C-010 | FLD | 107-JJ | BALL VALVE - ON/OFF - F.C. | 25-N-SS1U-0-9026689 | 008.3 | N2 PURGE | [13 empty] | Habonim | [5 empty] | 36 | bar: PKG
SC03 | SC03-CY-008A | SC03-C-010 | FLD | 107-JJ | SOLENOID VALVE | RACK MOUNTED | 008.3 | N2 PURGE | I.S: I.S; DI: DO |  |  | 41 | UTIL | [6 empty] | 36
SC03 | SC03-ZSC-008A | SC03-C-010 | FLD | 107-JJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 008.3 | N2 PURGE | I.S: I.S; DI: DI |  |  | 31 | UTIL | [6 empty] | 36
SC03 | SC03-ZSO-008A | SC03-C-010 | FLD | 107-JJ | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 008.3 | N2 PURGE | I.S: I.S; DI: DI |  |  | 31 | UTIL | [6 empty] | 36
SC03 | SC03-DIC-001 | SC03-D-001 | PCS | 107-JJ | INDICATING CONTR. - MOTOR DRIVE |  |  | P1 RECIRC PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC03 | SC03-DS-001 | SC03-D-001 | MCC | 107-JJ | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P1 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC03 | SC03-DY-001 | SC03-D-001 | MCC | 107-JJ | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P1 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC03 | SC03-DYC-001 | SC03-D-001 | MCC | 107-JJ | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 008.3 | P1 RECIRC PUMP | 8912 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC03 | SC03-DIC-002 | SC03-D-002 | PCS | 107-JJ | INDICATING CONTR. - MOTOR DRIVE |  |  | P2 RECIRC PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC03 | SC03-DS-002 | SC03-D-002 | MCC | 107-JJ | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | P2 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC03 | SC03-DY-002 | SC03-D-002 | MCC | 107-JJ | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | P2 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC03 | SC03-DYC-002 | SC03-D-002 | MCC | 107-JJ | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 008.3 | P2 RECIRC PUMP | 8913 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC03 | SC03-DIC-003 | SC03-D-003 | PCS | 107-JJ | INDICATING CONTR. - MOTOR DRIVE |  |  | FN1 EXTRACT FAN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC03 | SC03-DS-003 | SC03-D-003 | MCC | 107-JJ | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | FN1 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC03 | SC03-DY-003 | SC03-D-003 | MCC | 107-JJ | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | FN1 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC03 | SC03-DYC-003 | SC03-D-003 | MCC | 107-JJ | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 008.3 | FN1 EXTRACT FAN | 8914 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC03 | SC03-DIC-004 | SC03-D-004 | PCS | 107-JJ | INDICATING CONTR. - MOTOR DRIVE |  |  | FN2 EXTRACT FAN | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC03 | SC03-DS-004 | SC03-D-004 | MCC | 107-JJ | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | FN2 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC03 | SC03-DY-004 | SC03-D-004 | MCC | 107-JJ | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | FN2 EXTRACT FAN | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC03 | SC03-DYC-004 | SC03-D-004 | MCC | 107-JJ | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 008.3 | FN2 EXTRACT FAN | 8915 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC03 | SC03-FI-001 | SC03-F-001 | PCS | 107-JJ | INDICATOR - FLOW |  |  | CU1 OUTLET FLOW | REQ: By request |  |  | 0 | [7 empty] | 01
SC03 | SC03-FT-001 | SC03-F-001 | PKG | 107-JJ | TRANSMITTER - FLOW | SC03 | 008.3 | CU1 OUTLET FLOW | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | GEMU | 815/40/39.22.04-5-69 |  | NOT REQUIRED | NON IS FIELD DEVICE |  | 01
SC03 | SC03-FI-002 | SC03-F-002 | PCS | 107-JJ | INDICATOR - FLOW |  |  | N2 PURGE FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC03 | SC03-FIT-002 | SC03-F-002 | FLD | 107-JJ | TRANSMITTER - FLOW | 25-N-SS1U-0-9026688 | 008.3 | N2 PURGE FLOW | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | RMC | GMTXD |  | TI702-SP-5067 |  |  | 01
SC03 | SC03-FI-003 | SC03-F-003 | PCS | 107-JJ | INDICATOR - FLOW |  |  | CARBON DRUM FLOW | [11 empty] | 0 | [7 empty] | 20 | bar: PKG
SC03 | SC03-FT-003 | SC03-F-003 | FLD | 107-JJ | TRANSMITTER - FLOW | 100-SV-GR1A-0-9026686 | 008.3 | CARBON DRUM FLOW | REQ: By request; F: C; I.S: N.I.S; DI: AI |  |  | 11 | UTIL | FIC | GF90 |  |  |  |  | 20
SC03 | SC03-FI-004 | SC03-F-004 | FLD | 107-JJ | INDICATOR - FLOW | 25-N-SS1U-0-9026689 | 008.3 | N2 PURGE FLOW | REQ: By request | [10 empty] | 35
SC03 | SC03-HV-001 | SC03-H-001 | FLD | 107-JJ | BALL VALVE - ON/OFF - F.C. | 25-N-SS1U-0-9026686 | 008.3 | VENT/ CARBON FILTER | 14376 | - | - | REF | REQ | F | [5 empty] | 0 |  | PLATON | GMT XD |  |  |  |  | 01
SC03 | SC03-HZSC-001 | SC03-H-001 | FLD | 107-JJ | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 008.3 | TO CARBON FILTER | PKG: 14366; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
SC03 | SC03-HZSO-001 | SC03-H-001 | FLD | 107-JJ | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 008.3 | TO VENT | PKG: 14366; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
SC03 | SC03-LAL-001 | SC03-L-001 | PCS | 107-JJ | ALARM - LEVEL - LOW |  |  | LOW LEVEL | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC03 | SC03-LSL-001 | SC03-L-001 | PKG | 107-JJ | SWITCH - LEVEL - LOW | SC03-ST1 | 008.3 | LOW LEVEL | L15868 | On/off | On/off | REF | 24 | F |  | I.S | DI |  |  | 32 | UTIL | KSR KEUBLER | AFH2 |  | NOT REQUIRED | NON IS FIELD DEVICE |  | 01
SC03 | SC03-LAL-001A | SC03-L-001A | [6 empty] | PKG: L15868; -: On/off; -: On/off; REF: REF; REQ: 24
SC03 | SC03-LI-002 | SC03-L-002 | PCS | 107-JJ | INDICATOR - LEVEL |  |  | LEVEL | REQ: By request |  |  | 0 | [7 empty] | 01
SC03 | SC03-LIT-002 | SC03-L-002 | [6 empty] | REQ: By request
SC03 | SC03-LT-002 | SC03-L-002 | PKG | 107-JJ | TRANSMITTER - LEVEL | SC03-ST1 | 008.3 | LEVEL | 8918 | 180-1410 litres | +/- 10% | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | A PUISANCE | XT42-NIV |  | TI702-SP-5065 |  |  | 01
SC03 | SC03-LSH-003 | SC03-L-003 |  |  | SWITCH-LEVEL-HIGH |  |  | HIGH LEVEL | I.S: I.S; DI: DI |  |  |  | UTIL |  |  |  | NOT REQUIRED | NO FIELD DEVICE CONNECTED
SC03 | SC03-PI-001 | SC03-P-001 | PKG | 107-JJ | PRESSURE GAUGE - DIAPHRAGM | SC03 | 008.3 | P2 DISCHARGE PRESSURE | -: 0 to 2.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | STEWART BUCHANAN | [5 empty] | 01
SC03 | SC03-PI-002 | SC03-P-002 | PKG | 107-JJ | PRESSURE GAUGE - DIAPHRAGM | SC03 | 008.3 | P1 DISCHARGE PRESSURE | -: 0 to 2.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | STEWART BUCHANAN | [5 empty] | 01
SC03 | SC03-PDAH-003 | SC03-P-003 | PCS | 107-JJ | ALARM - PRESSURE - DIFF - HIGH |  |  | PS1 DIFF PRESSURE | REQ: By request |  |  | 0 | [7 empty] | 01
SC03 | SC03-PDSH-003 | SC03-P-003 | PKG | 107-JJ | SWITCH - PRESSURE - DIFF - HIGH | SC03-PS1 | 008.3 | PS1 DIFF PRESSURE | 8919 | set @ 15 mbar | +/- 5% | REF | 12 | C |  | I.S | DI |  |  | 32 | UTIL | GEORGIN | DFML 6D CX |  | TI702-SP-5069 |  |  | 01
SC03 | SC03-PIC-005 | SC03-P-005 | PCS | 107-JJ | INDICATING CONTROLLER - PRESSURE |  |  | CONT. GAS INLET PRESSURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC03 | SC03-PT-005 | SC03-P-005 | FLD | 107-JJ | TRANSMITTER - PRESSURE - DIAPHRAGM | 100-SV-GR1A-0-9026400 | 008.3 | CONT. GAS INLET PRESSURE | L6717 | -100 to 50 mbarg | +/- 10mbarg | REF | 24 | C |  | I.S | AI |  |  | 11 | UTIL | ROSEMOUNT | 3051 TG(Note 1) | KP0001 | TI702-SP-5046 |  |  | 01
SC03 | SC03-PDIC-007 | SC03-P-007 | PCS | 107-JJ | INDICATOR - DIFF PRESSURE |  |  | FN1/2 DIFF PRESSURE | REQ: By request |  |  | 0 | [7 empty] | 01
SC03 | SC03-PDT-007 | SC03-P-007 | PKG | 107-JJ | TRANSMITTER - PRESSURE - DIFF | SC03-FN1/2 | 008.3 | FN1/2 DIFF PRESSURE | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | YOKOGAWA | EJA 110A |  | TI702-SP-5059 |  |  | 01
SC03 | SC03-PSV-011 | SC03-P-011 | PKG | 107-JJ | PRESSURE RELIEF VALVE | SC03 | 008.3 | CU1 COOLING WATER RELIEF | -: 5 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | Broady | VTA |  |  |  |  | 01
SC03 | SC03-PSV-012 | SC03-P-012 | FLD | 107-JJ | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9026688 | 008.3 | N2 PRESSURE RELIEF | -: 60 mbarg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SC03 | SC03-PRV-013 | SC03-P-013 | FLD | 107-JJ | PRESSURE REDUCING VALVE | 25-N-SS1U-0-9026688 | 008.3 | N2 PRESSURE REDUCTION | -: 30 mbarg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SC03 | SC03-RV-001 | SC03-R-001 | PKG | 107-JJ | VACUUM BREATHER VALVE | SC03 | 008.3 | INLET HEADER RELIEF | -: -25 mbarg; -: -; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
SC03 | SC03-RV-002 | SC03-R-002 | DEL | 107-JJ | VACUUM BREATHER VALVE | DELETED |  | DELETED | [11 empty] | 0 | [5 empty] | DELETED |  | 01 | bar: -
SC03 | SC03-SE-001 | SC03-S-001 | PKG | 107-JJ | ELEMENT - SPEED | SC03-FN1 | 008.3 | FN1 SPEED | REQ: By request; F: F; I.S: I.S; DI: DI |  |  | 33 | UTIL | PEPPERL + FUCHS | NJ5-18GK-N |  | TI702-SP-5002 | 2 pulses/rev |  | 01
SC03 | SC03-SI-001 | SC03-S-001 | PCS | 107-JJ | INDICATOR - SPEED |  |  | FN1 SPEED | REQ: By request |  |  | 0 | [7 empty] | 01
SC03 | SC03-SE-002 | SC03-S-002 | PKG | 107-JJ | ELEMENT - SPEED | SC03-FN2 | 008.3 | FN2 SPEED | REQ: By request; F: F; I.S: I.S; DI: DI |  |  | 33 | UTIL | PEPPERL + FUCHS | NJ5-18GK-N |  | TI702-SP-5002 | 2 pulses/rev |  | 01
SC03 | SC03-SI-002 | SC03-S-002 | PCS | 107-JJ | INDICATOR - SPEED |  |  | FN2 SPEED | REQ: By request |  |  | 0 | [7 empty] | 01
SC03 | SC03-TE-003 | SC03-T-003 | PKG | 107-JJ | ELEMENT - TEMPERATURE - RTD | SC03 |  | CU1 OUTLET TEMPERATURE | PKG: L8923; -: 0 to 60 degC; -: +/- 2degC; REF: REF; REQ: 24 |  |  | 0 |  | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  |  |  | 01
SC03 | SC03-TIC-003 | SC03-T-003 | PCS | 107-JJ | INDICATING CONTROLLER - TEMPERATURE |  |  | CU1 OUTLET TEMPERATURE | PKG: L8923; -: 0 to 60 degC; -: +/- 2degC; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 01
SC03 | SC03-TT-003 | SC03-T-003 | PKG | 107-JJ | TRANSMITTER - TEMPERATURE | INTEGRAL WITH AT-001 | 008.3 | CU1 OUTLET TEMPERATURE | L8923 | 0 to 60 degC | +/- 2degC | REF | 24 | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | CLM153-G1A00A000 |  | TI702-SP-5166 | INTEGRAL WITH AT-001 |  | 01
SC03 | SC03-TE-004 | SC03-T-004 | FLD | 107-JJ | ELEMENT - TEMPERATURE - RTD | 100-SV-GR1A-0-9026400 |  | CONT. GAS INLET TEMP. | REQ: By request |  |  | 0 | [7 empty] | 01
SC03 | SC03-TI-004 | SC03-T-004 | PCS | 107-JJ | INDICATOR - TEMPERATURE |  |  | CONT. GAS INLET TEMP. | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC03 | SC03-TT-004 | SC03-T-004 | FLD | 107-JJ | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 008.3 | CONT. GAS INLET TEMP. | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
SC04 | SC04-AE-001 | SC04-A-001 | LCP | 107-JL | ELEMENT - ANALYSIS | LOCAL CONTROL PANEL | 008.4 | CONDUCTIVITY | REF: REF; REQ: REQ | [10 empty] | 30
SC04 | SC04-AI-001 | SC04-A-001 | LCP | 107-JL | INDICATOR - LOW ALARM | LOCAL CONTROL PANEL | 008.4 | CONDUCTIVITY | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  |  |  | 30
SC04 | SC04-AIC-001 | SC04-A-001 | PCS | 107-JL | INDICATING CONTROLLER - ANALYSIS |  |  | CONDUCTIVITY | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
SC04 | SC04-AT-001 | SC04-A-001 | LCP | 107-JL | TRANSMITTER - ANALYSIS - PH | LOCAL CONTROL PANEL | 008.4 | CONDUCTIVITY |  | - | - | REF | REQ | C |  | N.I.S | AI |  |  | 13 | UTIL | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  | INCLUDING TT-003 |  | 30
SC04 | SC04-CV-001 | SC04-C-001 | PKG | 107-JL | BALL VALVE - ON/OFF - F.C. | SC04 | 008.4 | UTIL WATER SUPPLY | 8925 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC04 | SC04-CY-001 | SC04-C-001 | PKG | 107-JL | SOLENOID VALVE | SC04 |  | UTIL WATER SUPPLY | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC04 | SC04-ZSC-001 | SC04-C-001 | PKG | 107-JL | MICROSWITCH - CLOSED | MTD. ON VALVE |  | UTIL WATER SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-ZSO-001 | SC04-C-001 | PKG | 107-JL | MICROSWICH - OPEN | MTD. ON VALVE |  | UTIL WATER SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-CV-002 | SC04-C-002 | PKG | 107-JL | BALL VALVE - ON/OFF - F.C. | SC04 | 008.4 | 20% NaOH SUPPLY | 7095 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC04 | SC04-CY-002 | SC04-C-002 | PKG | 107-JL | SOLENOID VALVE | SC04 |  | 20% NaOH SUPPLY | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC04 | SC04-ZSC-002 | SC04-C-002 | PKG | 107-JL | MICROSWITCH - CLOSED | MTD. ON VALVE |  | 20% NaOH SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-ZSO-002 | SC04-C-002 | PKG | 107-JL | MICROSWICH - OPEN | MTD. ON VALVE |  | 20% NaOH SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-CV-003 | SC04-C-003 | PKG | 107-JL | BALL VALVE - ON/OFF - F.C. | SC04 | 008.4 | 30% HCl SUPPLY | 8926 | - | - | REF | REQ | F | [5 empty] | 0 |  | SCORPION / PRISMA | Ball/PPO |  |  |  |  | 01
SC04 | SC04-CY-003 | SC04-C-003 | PKG | 107-JL | SOLENOID VALVE | SC04 |  | 30% HCl SUPPLY | I.S: N.I.S; DI: DO |  |  | 42 | UTIL | [6 empty] | 01
SC04 | SC04-ZSC-003 | SC04-C-003 | PKG | 107-JL | MICROSWITCH - CLOSED | MTD. ON VALVE |  | 30% HCl SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-ZSO-003 | SC04-C-003 | PKG | 107-JL | MICROSWICH - OPEN | MTD. ON VALVE |  | 30% HCl SUPPLY | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-CV-004 | SC04-C-004 | FLD | 107-JL | DAMPER - ACTUATOR - F.O. | EF-16 DISCHARGE | 008.4 | EF-16 TO HVAC STACK | 7008 | - | - | REF | REQ | F | [5 empty] | 0 | UTILS | [6 empty] | 01
SC04 | SC04-CY-004 | SC04-C-004 | FLD | 107-JL | SOLENOID VALVE | RACK MOUNTED |  | EF-16 TO HVAC STACK | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
SC04 | SC04-ZSC-004 | SC04-C-004 | FLD | 107-JL | PROXIMITY SENSOR - CLOSED | MTD. ON ACTUATOR |  | EF-16 TO HVAC STACK | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
SC04 | SC04-ZSO-004 | SC04-C-004 | FLD | 107-JL | PROXIMITY SENSOR - OPEN | MTD. ON ACTUATOR |  | EF-16 TO HVAC STACK | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
SC04 | SC04-DIC-001 | SC04-D-001 | PCS | 107-JL | INDICATING CONTR. - MOTOR DRIVE |  |  | P1 RECIRC PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC04 | SC04-DS-001 | SC04-D-001 | LCP | 107-JL | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | P1 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-DY-001 | SC04-D-001 | LCP | 107-JL | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | P1 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-DYC-001 | SC04-D-001 | LCP | 107-JL | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.4 | P1 RECIRC PUMP | 8927 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC04 | SC04-DIC-002 | SC04-D-002 | PCS | 107-JL | INDICATING CONTR. - MOTOR DRIVE |  |  | P2 RECIRC PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC04 | SC04-DS-002 | SC04-D-002 | LCP | 107-JL | DRIVE - AVAILABLE | LOCAL CONTROL PANEL |  | P2 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-DY-002 | SC04-D-002 | LCP | 107-JL | DRIVE - RUNNING | LOCAL CONTROL PANEL |  | P2 RECIRC PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-DYC-002 | SC04-D-002 | LCP | 107-JL | DRIVE - START/STOP | LOCAL CONTROL PANEL | 008.4 | P2 RECIRC PUMP | 8928 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC04 | SC04-DIC-003 | SC04-D-003 | PCS | 107-JL | INDICATING CONTR. - MOTOR DRIVE |  |  | EF-16A FAN DRIVE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC04 | SC04-DS-003 | SC04-D-003 | MCC | 107-JL | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | EF-16A FAN DRIVE | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-DY-003 | SC04-D-003 | MCC | 107-JL | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | EF-16A FAN DRIVE | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-DYC-003 | SC04-D-003 | MCC | 107-JL | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 008.4 | EF-16A FAN DRIVE | 8929 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC04 | SC04-DIC-004 | SC04-D-004 | PCS | 107-JL | INDICATING CONTR. - MOTOR DRIVE |  |  | EF-16B FAN DRIVE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SC04 | SC04-DS-004 | SC04-D-004 | MCC | 107-JL | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | EF-16B FAN DRIVE | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-DY-004 | SC04-D-004 | MCC | 107-JL | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | EF-16B FAN DRIVE | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
SC04 | SC04-DYC-004 | SC04-D-004 | MCC | 107-JL | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 008.4 | EF-16B FAN DRIVE | 8930 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
SC04 | SC04-FI-001 | SC04-F-001 | PCS | 107-JL | INDICATOR - FLOW |  |  | RECIRC FLOW | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
SC04 | SC04-FT-001 | SC04-F-001 | PKG | 107-JL | TRANSMITTER - FLOW | SC04 | 008.4 | RECIRC FLOW |  | - | - | REF | REQ | C |  | N.I.S | AI |  |  | 12 | UTIL | GEMU | 846/65/D.00.01.04-5-52 |  |  |  |  | 01
SC04 | SC04-HS-001 | SC04-H-001 | LCP | 107-JL | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.4 | PUMP 1 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-HS-002A | SC04-H-002 | LCP | 107-JL | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.4 |  | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-HS-002B | SC04-H-002 | LCP | 107-JL | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.4 |  | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-HS-003 | SC04-H-003 | LCP | 107-JL | SWITCH - HAND/OFF/AUTO | LOCAL CONTROL PANEL | 008.4 | PUMP 2 HAND/OFF/AUTO | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-HS-004A | SC04-H-004 | LCP | 107-JL | SWITCH - P/B - STOP | LOCAL CONTROL PANEL | 008.4 |  | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-HS-004B | SC04-H-004 | LCP | 107-JL | SWITCH - P/B - START | LOCAL CONTROL PANEL | 008.4 |  | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-LAL-001A | SC04-L-001 | PCS | 107-JL | ALARM - LEVEL - LOW |  |  | LOW LEVEL | PKG: L15873; -: On/off; -: On/off; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 01
SC04 | SC04-LAL-001B | SC04-L-001 | LCP | 107-JL | ALARM - LEVEL - LOW | LOCAL CONTROL PANEL | 008.4 | LOW LEVEL | -: -; -: -; REF: REF; REQ: 12; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-LSL-001 | SC04-L-001 | PKG | 107-JL | SWITCH - LEVEL - LOW | SC04-ST1 | 008.4 | LOW LEVEL | L15873 | On/off | On/off | REF | 24 | F |  | N.I.S | DI |  |  | 35 | UTIL | KSR KEUBLER | AFH |  |  |  |  | 01
SC04 | SC04-LI-002 | SC04-L-002 | PCS | 107-JL | INDICATOR - LEVEL |  |  | LEVEL | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
SC04 | SC04-LIT-002 | SC04-L-002 | [6 empty] | -: -; -: -; REF: REF; REQ: REQ
SC04 | SC04-LT-002 | SC04-L-002 | PKG | 107-JL | TRANSMITTER - LEVEL | SC04-ST1 | 008.4 | LEVEL |  | - | - | REF | REQ | C |  | N.I.S | AI |  |  | 12 | UTIL | KSR KEUBLER | BNA |  |  |  |  | 01
SC04 | SC04-PI-001 | SC04-P-001 | PKG | 107-JL | PRESSURE GAUGE - DIAPHRAGM | SC04 | 008.4 | P2 DISCHARGE PRESSURE | -: 0 to 2.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
SC04 | SC04-PI-002 | SC04-P-002 | PKG | 107-JL | PRESSURE GAUGE - DIAPHRAGM | SC04 | 008.4 | P1 DISCHARGE PRESSURE | -: 0 to 2.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
SC04 | SC04-PDAH-003 | SC04-P-003 | PCS | 107-JL | ALARM - PRESSURE - DIFF - HIGH |  |  | ST1 DIFF PRESSURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
SC04 | SC04-PDSH-003 | SC04-P-003 | PKG | 107-JL | SWITCH - PRESSURE - DIFF - HIGH | SC04-ST1 | 008.4 | ST1 DIFF PRESSURE | REF: REF; REQ: By request; F: C; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | DELTA CONTROLS LTD | W30101C604F |  |  |  |  | 01
SC04 | SC04-PT-007 | SC04-P-007 | PKG | 107-JL | TRANSMITTER - PRESSURE - DIAPHRAGM | SC04 | 008.4 | OUTLET PRESSURE |  | - | - | REF | REQ | C |  | N.I.S | AI |  |  | 12 | UTIL | [6 empty] | 01
SC04 | SC04-PI-007A | SC04-P-007A | [6 empty] | -: -; -: -; REF: REF; REQ: REQ
SC04 | SC04-PDAL-008 | SC04-P-008 | PCS | 107-JL | ALARM - PRESSURE - DIFF - LOW |  |  | EF-16 DIFF PRESSURE | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
SC04 | SC04-PDSL-008 | SC04-P-008 | FLD | 107-JL | SWITCH - PRESSURE - DIFF - LOW | EF-16 | 008.4 | EF-16 DIFF PRESSURE |  | - | - | REF | REQ | C |  | I.S | DI |  |  | 32 | UTIL | DELTA CONTROLS LTD | W30101CN04A30 | KP0012/1 | TI702-SP-5114 |  |  | 01
SC04 | SC04-TE-003 | SC04-T-003 | PKG | 107-JL | ELEMENT - TEMPERATURE - RTD | SC04 |  | RECIRC TEMPERATURE | -: -; -: -; REF: REF; REQ: REQ |  |  | 0 |  | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  |  |  | 01
SC04 | SC04-TIC-003 | SC04-T-003 | PCS | 107-JL | INDICATING CONTROLLER - TEMPERATURE |  |  | RECIRC TEMPERATURE | -: -; -: -; REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
SC04 | SC04-TT-003 | SC04-T-003 | LCP | 107-JL | TRANSMITTER - TEMPERATURE | LOCAL CONTROL PANEL | 008.4 | RECIRC TEMPERATURE | 8936 | 0 to 60 degC | +/- 10% | REF | REQ | C |  | N.I.S | AI |  |  | 13 | UTIL | ENDRESS + HAUSER | CLM152-A/CLS52 |  |  | INTEGRAL WITH AT-001 |  | 01
SC04 | SC04-TI-004A | SC04-T-004A | [6 empty] | REQ: By request
SC04 | SC04-YI-001 | SC04-Y-001 | LCP | 107-JL | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.4 | PUMP 1 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-YI-002 | SC04-Y-002 | LCP | 107-JL | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.4 | PUMP 2 RUNNING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-YI-003 | SC04-Y-003 | LCP | 107-JL | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.4 | PUMP 1 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SC04 | SC04-YI-004 | SC04-Y-004 | LCP | 107-JL | INDICATOR - LAMP | LOCAL CONTROL PANEL | 008.4 | PUMP 2 FAULT | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SOLV | SOLV-FIT-001 | SOLV-F-001 | FLD | 108-JA | TRANSMITTER - FLOW | 40-SD-SS1C-0-9028950 | 046.4 | GEN SOLVENT SUPPLY | 6457 | 0 - 6 m3/hr | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | UTIL | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
SOLV | SOLV-FQI-001 | SOLV-F-001 | PCS | 108-JA | INDICATOR - FLOW/TOTALISER |  |  | GEN SOLVENT SUPPLY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SOLV | SOLV-FIT-002 | SOLV-F-002 | FLD | 108-JA | TRANSMITTER - FLOW | 40-SD-SS1C-0-9028951 | 046.3 | ETHYL ACETATE SUPPLY | 6458 | 0 - 6 m3/hr | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | UTIL | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
SOLV | SOLV-FQI-002 | SOLV-F-002 | PCS | 108-JA | INDICATOR - FLOW/TOTALISER |  |  | ETHYL ACETATE SUPPLY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SOLV | SOLV-FIT-003 | SOLV-F-003 | FLD | 108-JA | TRANSMITTER - FLOW | 40-SD-SS1C-0-9028952 | 046.2 | ACETONE SUPPLY | 6459 | 0 - 6 m3/hr | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | UTIL | EURO | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
SOLV | SOLV-FQI-003 | SOLV-F-003 | PCS | 108-JA | INDICATOR - FLOW/TOTALISER |  |  | ACETONE SUPPLY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SOLV | SOLV-FIT-004 | SOLV-F-004 | FLD | 108-JA | TRANSMITTER - FLOW | 40-SD-SS1C-0-9028953 | 046.1 | METHANOL SUPPLY | 6460 | 0 - 6 m3/hr | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | UTIL | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
SOLV | SOLV-FQI-004 | SOLV-F-004 | PCS | 108-JA | INDICATOR - FLOW/TOTALISER |  |  | METHANOL SUPPLY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
SOLV | SP01-HS-001 | SP01-H-001 | PKG | 107-LC | SWITCH - PNEUMATIC | SP01 PANEL | 013.0 | START PUMP | REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SOLV | SP01-HS-002 | SP01-H-002 | PKG | 107-LC | SWITCH - PNEUMATIC | SP01 PANEL | 013.0 | STOP PUMP | REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SOLV | SP01-LSHL-001 | SP01-L-001 | FLD | 107-LC | SWITCH - LEVEL - HIGH/LOW | ET01/ET01 SUMP | 013.0 | SP01 CONTROL | -: set@commiss; -: +/- 10%; REF: REF; REQ: REQ; F: F |  |  | 0 |  | BESTA | TYPE 5 POV1141 |  |  | PNEUMATIC SWITCH |  | 01
SOLV | SP01-PRV-001 | SP01-P-001 | PKG | 107-LC | CONTROL VALVE SELF ACTUATING | SP01 AIR SUPPLY | 013.0 | AIR SUPPLY | -: set@commiss; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [5 empty] | REMOVED UNDER B902-1496 |  | 21
ST01 | ST01-CV-002 | ST01-C-002 | FLD | 107-LE | BALL VALVE - ON/OFF - F.C. | 50-SO-SS1C-0-9027150 | 014.1 | TANK OUTLET | 7099 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
ST01 | ST01-CY-002 | ST01-C-002 | FLD | 107-LE | SOLENOID VALVE | RACK MOUNTED |  | TANK OUTLET | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
ST01 | ST01-ZSC-002 | ST01-C-002 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TANK OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST01 | ST01-ZSO-002 | ST01-C-002 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TANK OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST01 | ST01-CV-003 | ST01-C-003 | FLD | 107-LE | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9027164 | 014.2 | ST01-VC1 COLD HTF RTN | 6776 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | UTIL | SAMSON | 241-7 / 3767-1 | KV0001 | TI702-SP-5053 |  |  | 60
ST01 | ST01-CV-004 | ST01-C-004 | FLD | 107-LE | BALL VALVE - ON/OFF - F.C. | 50-SO-SS1C-0-9027152 | 014.2 | SOLV WASTE TO WASTECARE | 7101 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  | OFF-PLOT ADJ TO KILOLAB |  | 60
ST01 | ST01-CY-004 | ST01-C-004 | FLD | 107-LE | SOLENOID VALVE | FIELD CABINET |  | SOLV WASTE TO WASTECARE | REF: REF; I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 60
ST01 | ST01-ZSC-004 | ST01-C-004 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | SOLV WASTE TO WASTECARE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-ZSO-004 | ST01-C-004 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | SOLV WASTE TO WASTECARE | REF: REF; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-CV-005 | ST01-C-005 | FLD | 107-LE | BALL VALVE - ON/OFF - F.O. | 40-CWR-CS1B-W-9027170 | 014.2 | CU1 COOLING WATER RTN | 8140 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
ST01 | ST01-CY-005 | ST01-C-005 | FLD | 107-LE | SOLENOID VALVE | RACK MOUNTED |  | CU1 COOLING WATER RTN | REF: REF; I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
ST01 | ST01-ZSC-005 | ST01-C-005 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | CU1 COOLING WATER RTN | REF: REF; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST01 | ST01-ZSO-005 | ST01-C-005 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | CU1 COOLING WATER RTN | REF: REF; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST01 | ST01-CV-006 | ST01-C-006 | FLD | 107-LE | BALL VALVE - ON/OFF - F.C. | 50-SO-SS1C-0-9027153 | 014.2 | ST01 RECIRC | 7157 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
ST01 | ST01-CY-006 | ST01-C-006 | FLD | 107-LE | SOLENOID VALVE | RACK MOUNTED |  | ST01 RECIRC | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
ST01 | ST01-ZSC-006 | ST01-C-006 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ST01 RECIRC | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST01 | ST01-ZSO-006 | ST01-C-006 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ST01 RECIRC | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST01 | ST01-CV-007 | ST01-C-007 | FLD | 107-LE | BALL VALVE - ON/OFF - F.C. | 50-SO-SS1C-0-9027154 | 014.2 | ST02 RECIRC | 7158 | - | - | SHE | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
ST01 | ST01-CY-007 | ST01-C-007 | FLD | 107-LE | SOLENOID VALVE | RACK MOUNTED |  | ST02 RECIRC | REF: SHE; I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
ST01 | ST01-ZSC-007 | ST01-C-007 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ST02 RECIRC | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST01 | ST01-ZSO-007 | ST01-C-007 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ST02 RECIRC | REF: SHE; I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST01 | ST01-CV008 | ST01-C-008 | FLD | 107-LE | ST03-P1 Solvent Transfer Control Valve | 80-SO-SS1C-0-9027192 | 014.3 | ST03-P1 to SOLV WASTE | -: -; -: -; REF: REF; REQ: By request; F: F |  |  |  |  | Habonim | 30 F47G-6666ATG/BW-SRS-WR |  |  |  |  | 60
ST01 | ST01-CY-008 | ST01-C-008 | FLD | 107-LE | ST01-CV08 SOLENOID VALVE | 80-SO-SS1C-0-9027192 | 014.3 | ST03-P1 to SOLV WASTE | REF: REF; REQ: By request; I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 60
ST01 | ST01-ZSC-008 | ST01-C-008 | FLD | 107-LE | ST01-CV08 CLOSED SENSOR | 80-SO-SS1C-0-9027192 | 014.3 | ST03-P1 to SOLV WASTE | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-ZSO-008 | ST01-C-008 | FLD | 107-LE | ST01-CV08 OPEN SENSOR | 80-SO-SS1C-0-9027192 | 014.3 | ST03-P1 to SOLV WASTE | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-CV009 | ST01-C-009 | FLD | 107-LE | Solvent Transfer Control Valve | 50-SO-SS1C-0-9027152 | 014.1 | ST01-P1 to SOLV WASTE | -: -; -: -; REF: REF; REQ: By request; F: F |  |  |  |  | Habonim | 20 F47W-6666AI/BW-SRS-LAX |  |  |  |  | 60
ST01 | ST01-CY-009 | ST01-C-009 | FLD | 107-LE | ST01-CV09 SOLENOID VALVE | 50-SO-SS1C-0-9027152 | 014.1 | ST01-P1 to SOLV WASTE | REF: REF; REQ: By request; I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 60
ST01 | ST01-ZSC-009 | ST01-C-009 | FLD | 107-LE | ST01-CV09 CLOSED SENSOR | 50-SO-SS1C-0-9027152 | 014.1 | ST01-P1 to SOLV WASTE | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-ZSO-009 | ST01-C-009 | FLD | 107-LE | ST01-CV09 OPEN SENSOR | 50-SO-SS1C-0-9027152 | 014.1 | ST01-P1 to SOLV WASTE | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-CV010 | ST01-C-010 | FLD | 107-LE | B235 Solvent Transfer Control Valve | 80-SO-SS1C-0-9027193 | 014.3 | SOLV WASTE TO ROAD TANKER | -: -; -: -; REF: REF; REQ: By request; F: F |  |  |  |  | Habonim | 30 F47G-6666ATG/BW-SRS-WR |  |  |  |  | 60
ST01 | ST01-CY-010 | ST01-C-010 | FLD | 107-LE | ST01-CV10 SOLENOID VALVE | 80-SO-SS1C-0-9027193 | 014.3 | SOLV WASTE TO ROAD TANKER | REF: REF; REQ: By request; I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 60
ST01 | ST01-ZSC-010 | ST01-C-010 | FLD | 107-LE | ST01-CV10 CLOSED SENSOR | 80-SO-SS1C-0-9027193 | 014.3 | SOLV WASTE TO ROAD TANKER | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-ZSO-010 | ST01-C-010 | FLD | 107-LE | ST01-CV10 OPEN SENSOR | 80-SO-SS1C-0-9027193 | 014.3 | SOLV WASTE TO ROAD TANKER | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-CV011 | ST01-C-011 | FLD | 107-LE | ST03 Solvent Circulation Return Control Valve | 50-SO-SS1C-0-9027196 | 014.3 | ST03 RECIRC | -: -; -: -; REF: SHE; REQ: By request; F: F |  |  |  |  | Habonim | 20 F47W-6666AI/BW-SRS-LAX |  |  |  |  | 60
ST01 | ST01-CY-011 | ST01-C-011 | FLD | 107-LE | ST01-CV11 SOLENOID VALVE | 50-SO-SS1C-0-9027196 | 014.3 | ST03 RECIRC | REF: SHE; REQ: By request; I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 60
ST01 | ST01-ZSC-011 | ST01-C-011 | FLD | 107-LE | ST01-CV11 CLOSED SENSOR | 50-SO-SS1C-0-9027196 | 014.3 | ST03 RECIRC | REF: SHE; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-ZSO-011 | ST01-C-011 | FLD | 107-LE | ST01-CV11 OPEN SENSOR | 50-SO-SS1C-0-9027196 | 014.3 | ST03 RECIRC | REF: SHE; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST01 | ST01-DIC-001 | ST01-D-001 | PCS | 107-LE | INDICATING CONTR. - MOTOR DRIVE |  |  | RECIRC PUMP | REF: SHE; REQ: By request; F: F |  |  | 0 | [7 empty] | 01
ST01 | ST01-DS-001 | ST01-D-001 | MCC | 107-LE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | RECIRC PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
ST01 | ST01-DY-001 | ST01-D-001 | MCC | 107-LE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | RECIRC PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
ST01 | ST01-DYC-001 | ST01-D-001 | MCC | 107-LE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 014.2 | RECIRC PUMP | 8937 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
ST01 | ST01-DIC-002 | ST01-D-002 | PCS | 107-LE | INDICATING CONTR. - MOTOR DRIVE |  |  | COLD HTF PUMP TO ST01-VC1 | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 60
ST01 | ST01-DS-002 | ST01-D-002 | MCC | 107-LE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | COLD HTF PUMP TO ST01-VC1 | REF: REF; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 60
ST01 | ST01-DY-002 | ST01-D-002 | MCC | 107-LE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | COLD HTF PUMP TO ST01-VC1 | REF: REF; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 60
ST01 | ST01-DYC-002 | ST01-D-002 | MCC | 107-LE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 014.2 | COLD HTF PUMP TO ST01-VC1 | 8938 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 60
ST01 | ST01-FIC-001 | ST01-F-001 | PCS | 107-LE | INDICATOR - FLOW TOTALISER |  |  | EFFLUENT SOLVENT | REF: REF; REQ: By request | [10 empty] | 01
ST01 | ST01-FIT-001 | ST01-F-001 | FLD | 107-LE | TRANSMITTER - FLOW | 50-SO-SS1C-0-9027152 | 014.1 | EFFLUENT SOLVENT | 12402 |  | +/- 0.25% | REF | By request | C |  | I.S | DI |  |  |  | UTIL | ENDRESS + HAUSER | 8F3B50-BBDCCGAFAASAAASAA2+DCDDDHLA Promass F 300, 8F3B50, DN50 2" |  | TI702-SP-5149 |  |  | 01
ST01 | ST01-LI-001 | ST01-L-001 | PCS | 107-LE | INDICATOR - LEVEL |  |  | LEVEL | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
ST01 | ST01-LT-001 | ST01-L-001 | FLD | 107-LE | TRANSMITTER - LEVEL | ST01/L1/100 | 014.1 | LEVEL | 7009 | 0-9350 litres | +/- 2% | REF | By request | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | FMR240(Note 1) | KL0028/P | TI702-SP-5115 |  |  | 01
ST01 | ST01-LAH-002 | ST01-L-002 | PCS | 107-LE | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
ST01 | ST01-LSH-002 | ST01-L-002 | FLD | 107-LE | SWITCH - LEVEL - HIGH | ST01/L2/100 | 014.1 | HIGH LEVEL | 6722 | Fixed | - | SHE | 24 | F |  | I.S | DI |  |  | 32 | UTIL | MEGGIT MOBERY | DS4FR4N1PH8/65 | KL0005 | TI702-SP-5113 |  |  | 01
ST01 | ST01-PSV-001 | ST01-P-001 | FLD | 107-LE | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028848 | 014.2 | N2 SUPPLY RELIEF | -: 30 mbarg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | TBA | VTA | KS0004 |  |  |  | 01
ST01 | ST01-PI-002 | ST01-P-002 | FLD | 107-LE | PRESSURE GAUGE | 25-N-SS1U-0-9028848 | 014.2 | N2 SUPPLY | -: 0 to 25 mbarg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 632.50.100 (Note 1) | KP0006/P |  |  |  | 01
ST01 | ST01-PI-003 | ST01-P-003 | FLD | 107-LE | PRESSURE GAUGE - DIAPHRAGM | 50-SO-SS1C-0-9027171 | 014.2 | P1 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
ST01 | ST01-PRV-004 | ST01-P-004 | FLD | 107-LE | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028848 | 014.2 | N2 SUPPLY | -: set @ 10mbarg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440/75 | KS0007 |  |  |  | 01
ST01 | ST01-PSV-005 | ST01-P-005 | FLD | 107-LE | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9027168 | 014.2 | ST01-VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 60
ST01 | ST01-PI-007 | ST01-P-007 | FLD | 107-LE | PRESSURE GAUGE - DIAPHRAGM | 25-HT-CS3A-C-9027175 | 014.2 | P2 DISCHARGE PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006 |  |  |  | 01
ST01 | ST01-PSV-008 | ST01-P-008 | FLD | 107-LE | PRESSURE RELIEF VALVE | 50-RV-SS1C-0-9027177 | 014.1 | ST01 RELIEF | -: 3 barg; -: +/- 10%; REF: SHE; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511H-S-N000 | KS0001 |  |  |  | 01
| ST01-PSV-009 | ST01-P-009 | FLD | 107-LE | PRESSURE RELIEF VALVE | 40-SO-SS1C-0-9027157 | 014.1 | ST01 PIPEWORK THERMAL RELIEF | -: 6 barg; -: +/- 10%; REF: SHE; REQ: 24 | [11 empty] | v16.0
| ST01-PSV-010 | ST01-P-010 | FLD | 107-LE | PRESSURE RELIEF VALVE | 40-SO-SS1C-0-9027157 | 014.1 | ST01 PIPEWORK THERMAL RELIEF | -: 6 barg; -: +/- 10%; REF: SHE; REQ: 24 | [11 empty] | v16.0
| ST01-PSV-011 | ST01-P-011 | FLD | 107-LE | PRESSURE RELIEF VALVE | 40-SO-SS1C-0-9027157 | 014.1 | ST01 PIPEWORK THERMAL RELIEF | -: 6 barg; -: +/- 10%; REF: SHE; REQ: 24 | [11 empty] | v16.0
ST01 | ST01-RO-001 | ST01-R-001 | FLD | 107-LE | RESTRICTION ORIFICE PLATE | 50-SO-SS1C-0-9027153 | 014.1 | ST01 RECIRCULATION | -: 16.5mm DIA; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | SITE FABRICATED |  | SITE FAB/1 |  |  |  | 01
ST01 | ST01-RO-002 | ST01-R-002 | FLD | 107-LE | RESTRICTION ORIFICE PLATE | 50-SO-SS1C-0-9027154 | 014.2 | ST02 RECIRCULATION | -: 16.5mm DIA; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | SITE FABRICATED |  | SITE FAB/1 |  |  |  | 01
ST01 | ST01-RO-003 | ST01-R-003 | FLD | 107-LE | RESTRICTION ORIFICE PLATE | 50-SO-SS1C-0-9027196 | 014.3 | ST03 RECIRCULATION | -: 16.5mm DIA; -: -; REF: REF; REQ: REQ | [10 empty] | 60
ST01 | ST01-RV-006 | ST01-R-006 | FLD | 107-LE | PRESSURE VENT | 25-RV-SS1C-0-9027169 | 014.2 | ST01-VC1 TO VENT | -: 20 mbarg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | GROTH 1260A |  | KS0004 |  |  |  | 60
ST01 | ST01-TE-001 | ST01-T-001 | FLD | 107-LE | ELEMENT - TEMPERATURE - RTD | ST01/T/50 |  | TANK TEMPERATURE | REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
ST01 | ST01-TI-001 | ST01-T-001 | PCS | 107-LE | INDICATOR - TEMPERATURE |  |  | TANK TEMPERATURE | REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
ST01 | ST01-TT-001 | ST01-T-001 | FLD | 107-LE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 014.1 | TANK TEMPERATURE | 7033 | 0 to 50 degC | +/- 5% | SHE | 12 | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 01
ST01 | ST01-TE-002 | ST01-T-002 | FLD | 107-LE | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9027164 |  | ST01-VC1 COLD HTF RTN TEMP | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 60
ST01 | ST01-TI-002 | ST01-T-002 | PCS | 107-LE | INDICATOR - TEMPERATURE |  |  | ST01-VC1 COLD HTF RTN TEMP | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 60
ST01 | ST01-TT-002 | ST01-T-002 | FLD | 107-LE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 014.2 | ST01-VC1 COLD HTF RTN TEMP | 7034 | -30 to 70 degC | +/- 5% | REF | By request | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 60
ST01 | ST01-LI-003 | ST01-Y-001 | PKG | 107-LE | INDICATOR - LEVEL | ST01-P1 SEAL POT | 014.1 | COMMON ALARM | -: Fixed; -: -; REF: REF; REQ: By request; F: F |  |  | 0 | [7 empty] | 01
ST01 | ST01-LSH-004 | ST01-Y-001 | PKG | 107-LE | SWITCH - LEVEL - HIGH | ST01-P1 SEAL POT | 014.1 | COMMON ALARM | -: Fixed; -: -; REF: SHE; F: F |  |  | 0 | [7 empty] | 01
ST01 | ST01-LSL-005 | ST01-Y-001 | PKG | 107-LE | SWITCH - LEVEL - LOW | ST01-P1 SEAL POT | 014.1 | COMMON ALARM | -: Fixed; -: -; REF: SHE; F: F |  |  | 0 | [7 empty] | 01
ST01 | ST01-PI-009 | ST01-Y-001 | PKG | 107-LE | PRESSURE GAUGE | ST01-P1 SEAL POT | 014.1 | COMMON ALARM | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
ST01 | ST01-PSL-010 | ST01-Y-001 | PKG | 107-LE | SWITCH - PRESSURE - LOW | ST01-P1 SEAL POT | 014.1 | COMMON ALARM | -: set @ 4 barg; -: +/- 5%; REF: SHE; F: C |  |  | 0 | [7 empty] | 01
ST01 | ST01-TI-003 | ST01-Y-001 | PKG | 107-LE | INDICATOR - TEMPERATURE | ST01-P1 SEAL POT | 014.1 | COMMON ALARM | -: 0 to 120 degC; -: +/- 5%; REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
ST01 | ST01-YA-001 | ST01-Y-001 | PCS | 107-LE | ALARM - COMMON |  |  | COMMON ALARM | REF: SHE |  |  | 0 | [7 empty] | 01
ST01 | ST01-YS-001 | ST01-Y-001 | PKG | 107-LE | SWITCH - COMMON ALARM | ST01-P1 SEAL POT | 014.1 | COMMON ALARM | 8687 | - | - | SHE | REQ | F |  | I.S | DI |  |  | 32 | UTIL | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5162 |  |  | 01
ST02 | ST02-CV-002 | ST02-C-002 | FLD | 107-LE | BALL VALVE - ON/OFF - F.C. | 50-SO-SS1C-0-9027151 | 014.2 | TANK OUTLET | 7100 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
ST02 | ST02-CY-002 | ST02-C-002 | FLD | 107-LE | SOLENOID VALVE | RACK MOUNTED |  | TANK OUTLET | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
ST02 | ST02-ZSC-002 | ST02-C-002 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TANK OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST02 | ST02-ZSO-002 | ST02-C-002 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TANK OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
ST02 | ST02-LI-001 | ST02-L-001 | PCS | 107-LE | INDICATOR - LEVEL |  |  | LEVEL | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
ST02 | ST02-LT-001 | ST02-L-001 | FLD | 107-LE | TRANSMITTER - LEVEL | ST02/L1/100 | 014.2 | LEVEL | 7010 | 0-15850 litres | +/- 2% | REF | By request | C |  | I.S | AI |  |  | 11 | UTIL | ENDRESS + HAUSER | FMR240(Note 1) | KL0028/P | TI702-SP-5115 |  |  | 01
ST02 | ST02-LAH-002 | ST02-L-002 | PCS | 107-LE | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
ST02 | ST02-LSH-002 | ST02-L-002 | FLD | 107-LE | SWITCH - LEVEL - HIGH | ST02/L2/100 | 014.2 | HIGH LEVEL | 6723 | Fixed | - | SHE | 24 | F |  | I.S | DI |  |  | 32 | UTIL | MEGGIT MOBERY | DS4FR4N1PH8/65 | KL0005 | TI702-SP-5113 |  |  | 01
ST02 | ST02-PSV-008 | ST02-P-008 | FLD | 107-LE | PRESSURE RELIEF VALVE | 50-RV-SS1C-0-9027179 | 014.2 | ST02 RELIEF | -: 3 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511J-S-N000 | KS0001 |  |  |  | 01
ST02 | ST02-TE-001 | ST02-T-001 | FLD | 107-LE | ELEMENT - TEMPERATURE - RTD | ST02/T/50 |  | TANK TEMPERATURE | REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
ST02 | ST02-TI-001 | ST02-T-001 | PCS | 107-LE | INDICATOR - TEMPERATURE |  |  | TANK TEMPERATURE | REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
ST02 | ST02-TT-001 | ST02-T-001 | FLD | 107-LE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 014.2 | TANK TEMPERATURE | 7035 | 0 to 50 degC | +/- 5% | SHE | 12 | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5107 |  |  | 01
ST03 | ST03-CV-001 | ST03-C-001 | FLD | 107-LE | BALL VALVE - ON/OFF - F.C. | 80-SO-SS1C-0-9027190 | 014.3 | TANK OUTLET TO ST03-P1 | REF: REF; REQ: By request; F: F |  |  |  |  | Habonim | 30 F47G-6666ATG/BW-SRS-WR |  |  |  |  | 60
ST03 | ST03-CY-001 | ST03-C-001 | FLD | 107-LE | SOLENOID VALVE | RACK MOUNTED | 014.3 | ST03-CV01 SOLENOID VALVE | REF: REF; REQ: By request; I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 60
ST03 | ST03-ZSC-001 | ST03-C-001 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 014.3 | ST03-CV01 CLOSED SENSOR | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST03 | ST03-ZSO-001 | ST03-C-001 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 014.3 | ST03-CV01 OPEN SENSOR | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST03 | ST03-CV002 | ST03-C-002 | FLD | 107-LE | BALL VALVE - ON/OFF - F.C. | 80-SO-SS1C-0-9027191 | 014.3 | TANK OUTLET TO ST01-P1 | REF: REF; REQ: By request; F: F |  |  |  |  | Habonim | 30 F47G-6666ATG/BW-SRS-WR |  |  |  |  | 60
ST03 | ST03-CY-002 | ST03-C-002 | FLD | 107-LE | SOLENOID VALVE | RACK MOUNTED | 014.3 | ST03-CV02 SOLENOID VALVE | REF: REF; REQ: By request; I.S: I.S; DI: DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 60
ST03 | ST03-ZSC-002 | ST03-C-002 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 014.3 | ST03-CV02 CLOSED SENSOR | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST03 | ST03-ZSO-002 | ST03-C-002 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 014.3 | ST03-CV02 OPEN SENSOR | REF: REF; REQ: By request; I.S: I.S; DI: DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 60
ST03 | ST03-CV003 | ST03-C-003 | FLD | 107-LE | GLOBE VALVE - CONTROL - STAYPUT | 25-HT-CS3A-C-9027204 | 014.3 | ST03-VC1 COLD HTF RTN | REF: REF; REQ: By request; F: F; I.S: I.S; DI: AO |  |  |  | UTIL | Fisher | FRGX2-1W2C2/EXTL+DVC 2000 |  | TI702-SP-5174 |  |  | 60
| ST03-CV004 | ST03-C-004 | FLD | 107-LE | BALL VALVE - ON/OFF - F.C. | 25-N-SS1U-0-9027155 | 014.3 | NITROGEN TO ST03-ST1 | REF: REF; REQ: By request | [11 empty] | v16.0
| ST03-CY-004 | ST03-C-004 | FLD | 107-LE | SOLENOID VALVE | PANEL MOUNTED | 014.3 | NITROGEN TO ST03-ST1 | REF: REF; REQ: By request | [11 empty] | v16.0
| ST03-ZSC-004 | ST03-C-004 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 014.3 | NITROGEN TO ST03-ST1 | REF: REF; REQ: By request | [11 empty] | v16.0
| ST03-ZSO-004 | ST03-C-004 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 014.3 | NITROGEN TO ST03-ST1 | REF: REF; REQ: By request | [11 empty] | v16.0
| ST03-CV005 | ST03-C-005 | FLD | 107-LE | BALL VALVE - ON/OFF - F.C. | 50-SO-SS1c-0-9027200 | 014.3 | ST03-ST1 DRAIN TO ST03 | REF: REF; REQ: By request | [11 empty] | v16.0
| ST03-CY-005 | ST03-C-005 | FLD | 107-LE | SOLENOID VALVE | PANEL MOUNTED | 014.3 | ST03-ST1 DRAIN TO ST03 | REF: REF; REQ: By request | [11 empty] | v16.0
| ST03-ZSC-005 | ST03-C-005 | FLD | 107-LE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 014.3 | ST03-ST1 DRAIN TO ST03 | REF: REF; REQ: By request | [11 empty] | v16.0
| ST03-ZSO-005 | ST03-C-005 | FLD | 107-LE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 014.3 | ST03-ST1 DRAIN TO ST03 | REF: REF; REQ: By request | [11 empty] | v16.0
ST03 | ST03-DIC-001 | ST03-D-001 | PCS | 107-LE | INDICATING CONTR. - MOTOR DRIVE |  | 014.3 | ST03-P1 WASTE TRANSFER PUMP | REF: SHE; F: F | [10 empty] | 60
ST03 | ST03-DS-001 | ST03-D-001 | MCC | 107-LE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE | 014.3 | ST03-P1 WASTE TRANSFER PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  |  | UTIL | [6 empty] | 60
ST03 | ST03-DY-001 | ST03-D-001 | MCC | 107-LE | DRIVE - RUNNING | MOTOR CONTROL CENTRE | 014.3 | ST03-P1 WASTE TRANSFER PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  |  | UTIL | [6 empty] | 60
ST03 | ST03-DYC-001 | ST03-D-001 | MCC | 107-LE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 014.3 | ST03-P1 WASTE TRANSFER PUMP | REF: SHE; I.S: N.I.S; DI: DO |  |  |  | UTIL | [6 empty] | 60
ST03 | ST03-DIC-002 | ST03-D-002 | PCS | 107-LE | INDICATING CONTR. - MOTOR DRIVE |  | 014.3 | COLD HTF PUMP TO ST03-VC1 | REF: REF; F: F | [10 empty] | 60
ST03 | ST03-DS-002 | ST03-D-002 | MCC | 107-LE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE | 014.3 | COLD HTF PUMP TO ST03-VC1 | REF: REF; I.S: N.I.S; DI: DI |  |  |  | UTIL | [6 empty] | 60
ST03 | ST03-DY-002 | ST03-D-002 | MCC | 107-LE | DRIVE - RUNNING | MOTOR CONTROL CENTRE | 014.3 | COLD HTF PUMP TO ST03-VC1 | REF: REF; I.S: N.I.S; DI: DI |  |  |  | UTIL | [6 empty] | 60
ST03 | ST03-DYC-002 | ST03-D-002 | MCC | 107-LE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 014.3 | COLD HTF PUMP TO ST03-VC1 | REF: REF; I.S: N.I.S; DI: DO |  |  |  | UTIL | [6 empty] | 60
ST03 | ST03-LI-001 | ST03-L-001 | PCS | 107-LE | INDICATOR - LEVEL |  | 014.3 | ST03 WASTE SOLVENT TANK LEVEL | REF: REF; REQ: By request | [10 empty] | 60
ST03 | ST03-LIT-001 | ST03-L-001 | FLD | 107-LE | TRANSMITTER - LEVEL | ST03/L1/100 | 014.3 | ST03 WASTE SOLVENT TANK LEVEL | 16176 |  |  | REF | By request | C |  | I.S | AI |  |  |  | UTIL | Vega | Vegapuls 64 |  | TI702-SP-5160 |  |  | 60
ST03 | ST03-LAH-002 | ST03-L-002 | PCS | 107-LE | ALARM - LEVEL - HIGH |  | 014.3 | ST03 WASTE SOLVENT TANK HIGH LEVEL SWITCH | REF: SHE; REQ: 24 | [10 empty] | 60
ST03 | ST03-LSH-002 | ST03-L-002 | FLD | 107-LE | SWITCH - LEVEL - HIGH | ST03/L2/100 | 014.3 | ST03 WASTE SOLVENT TANK HIGH LEVEL SWITCH | 16188 |  |  | SHE | 24 | F |  | I.S | DI |  |  |  | UTIL | Vega | Vegaswing 63 |  | TI702-SP-5161 |  |  | 60
ST03 | ST03-LAH-003 | ST03-L-003 | PCS | 107-LE | ALARM - LEVEL - HIGH |  | 014.3 | ST03-ST1 HIGH LEVEL | REF: SHE; REQ: 24 | [10 empty] | 60
ST03 | ST03-LSH-003 | ST03-L-003 | FLD | 107-LE | SWITCH - LEVEL - HIGH | ST03-ST1 | 014.3 | ST03-ST1 HIGH LEVEL | PKG: 16189; REF: SHE; REQ: 24 |  |  |  |  | Vega | Vegaswing 63 |  | TI702-SP-5161 | CHANGED LAL TO LAH |  | 60 | v16.0
ST03 | ST03-PI-001 | ST03-P-001 | FLD | 107-LE | PRESSURE GAUGE | 80-SO-SS1C-0-9027192 | 014.3 | ST03-P1 DISCHARGE PRESSURE | REF: REF; REQ: By request |  |  |  |  | WIKA | 232.50 |  |  | CHANGED LSL TO LSH |  | 60 | v16.0
ST03 | ST03-PI-002 | ST03-P-002 | FLD | 107-LE | PRESSURE GAUGE | 25-HT-CS3A-C-9027203 | 014.3 | ST03-P2 DISCHARGE PRESSURE | REF: REF; REQ: By request |  |  |  |  | WIKA | 232.50 |  |  |  |  | 60
ST03 | ST03-PI-003 | ST03-P-003 | FLD | 107-LE | PRESSURE GAUGE | 50-SO-SS1C-0-9027194 | 014.3 | ST03 TANKER VAPOUR RETURN LINE PRESSURE | REF: REF; REQ: By request |  |  |  |  | WIKA | 232.50 |  |  |  |  | 60
ST03 | ST03-PI-009 | ST03-P-009 | FLD | 107-LE | PRESSURE GAUGE | ST03-P1 SEAL POT | 014.3 | ST03-P1 SEAL POT PRESSURE INDICATOR | REF: REF; REQ: By request |  |  |  |  | WIKA | 341264N |  |  |  |  | 60
ST03 | ST03-PSV-005 | ST03-P-005 | FLD | 107-LE | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9027204 | 014.3 | ST03-VC1 HTF RELIEF | -: 9 barg; -: +/- 10%; REQ: 24; F: C |  |  |  |  | Broady | 3531D |  |  |  |  | 60
ST03 | ST03-PSV-008 | ST03-P-008 | FLD | 107-LE | PRESSURE RELIEF VALVE | 150-SO-SS1C-0-9027197 | 014.3 | ST03 RELIEF | -: 3 barg; -: +/- 10%; REF: SHE; REQ: 24; F: C |  |  |  |  | Broady | 3511P-SN-000A0 |  |  |  |  | 60
ST03 | ST03-RV006 | ST03-R-006 | FLD | 107-LE | PRESSURE VENT | 50-RV-SS1C-0-9027201 | 014.3 | ST03-VC1 TO VENT | -: 20 mbarg; -: +/- 10%; REQ: 24; F: C |  |  |  |  | Groth Corporation | 1260A-02-555-T00 |  |  |  |  | 60
ST03 | ST02-TI-001 | ST03-T-001 | PCS | 107-LE | INDICATOR - TEMPERATURE |  | 014.3 | ST03 WASTE SOLVENT TANK TEMPERATURE | REF: SHE; REQ: 12 | [10 empty] | 60
ST03 | ST03-TE-001 | ST03-T-001 | FLD | 107-LE | ELEMENT - TEMPERATURE - RTD | ST03/T1/40 | 014.3 | ST03 WASTE SOLVENT TANK TEMPERATURE | REF: SHE; REQ: 12 | [10 empty] | 60
ST03 | ST03-TT-001 | ST03-T-001 | FLD | 107-LE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 014.3 | ST03 WASTE SOLVENT TANK TEMPERATURE | 16178 |  |  | SHE | 12 | C |  | I.S | AI |  |  |  | UTIL | Rosemount | 248HAI1N0XAQ4F5 |  | TI702-SP-5159 |  |  | 60
ST03 | ST03-TE-002 | ST03-T-002 | FLD | 107-LE | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9027204 | 014.3 | ST03-VC1 COLD HTF RTN TEMP | REF: SHE; REQ: 12 | [10 empty] | 60
ST03 | ST03-TI-002 | ST03-T-002 | PCS | 107-LE | INDICATOR - TEMPERATURE |  | 014.3 | ST03-VC1 COLD HTF RTN TEMP | REF: SHE; REQ: 12 | [10 empty] | 60
ST03 | ST03-TT-002 | ST03-T-002 | FLD | 107-LE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 014.3 | ST03-VC1 COLD HTF RTN TEMP | 16180 |  |  | SHE | 12 | C |  | I.S | AI |  |  | 11 | UTIL | Rosemount | 248HAI1N0XAQ4F5 |  | TI702-SP-5159 |  |  | 60
ST03 | ST03-LSL-005 | ST03-Y-001 | FLD | 107-LE | SWITCH - LEVEL - LOW | ST03-P1 SEAL POT | 014.3 | ST03-P1 SEAL POT COMMON ALARM | PKG: 16172; REF: SHE; REQ: 12 |  |  |  |  | Pyropress | Argus LI522PP0/1N120SOR/215SOF |  | TI702-SP-5175 |  |  | 60
ST03 | ST03-PSL-010 | ST03-Y-001 | FLD | 107-LE | SWITCH - PRESSURE - LOW | ST03-P1 SEAL POT | 014.3 | ST03-P1 SEAL POT COMMON ALARM | PKG: 16172; -: 1 to 20.7 barg switch set at 4barg±0.5barg falling; -: +/- 1%; REF: SHE; REQ: 12 |  |  |  |  | Pyropress | Argus PI511IPT10/BT10N1/S6F |  | TI702-SP-5175 |  |  | 60
ST03 | ST03-YA-001 | ST03-Y-001 | PCS | 107-LE | ALARM - COMMON |  | 014.3 | ST03-P1 SEAL POT COMMON ALARM | 16172 |  |  | SHE | 12 | F |  | I.S | DI |  |  |  | UTIL | [6 empty] | 60
ST03 | ST03-YA-002 | ST03-Y-002 | PCS | 107-LE | ALARM - COMMON |  | 014.3 | ST03 ROAD TANKER EARTH BONDING | 16191 |  |  | SHE | 12 | F |  | I.S | DI |  |  |  | UTIL |  |  |  |  | FILL PERMISSIVE SPLIT OUT INTO YS02/03/04 |  | 60 | v16.0
ST03 | ST03-YS-002 | ST03-Y-002 | FLD | 107-LE | SWITCH - EARTH BONDING - STATUS | B235 TANKER FILLING AREA | 014.3 | ST03 ROAD TANKER EARTH BONDING | PKG: 16191; REF: SHE; REQ: 12; F: F | [10 empty] | 60 | v16.0
STM | STM-FQI-001 | STM-F-001 | CPR | 108-AA | INDICATOR - FLOW | BEMS SYSTEM |  | STEAM SUPPLY | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
STM | STM-FT-001 | STM-F-001 | FLD | 108-AA | TRANSMITTER - FLOW | 150-SLP-CS1A-H-9028000 | 023.0 | STEAM SUPPLY |  | 0- 5620 kg/hr | +/- 3% | REF | REQ | C |  | N.I.S |  |  |  | 12 |  | SPIRAX SARCO | ILVA | KF0028 |  | INPUT BEMS SYSTEM | AI | 01
STM | STM-PI-001 | STM-P-001 | FLD | 108-AA | PRESSURE GAUGE - STEAM SYPHON | 80-CLP-CS1A-0-9028099 | 022.0 | CR01-ST1 PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
STM | STM-PI-002 | STM-P-002 | FLD | 108-AA | PRESSURE GAUGE - STEAM SYPHON | 50-CLP-CS1A-H-9028060 | 022.0 | CONDENSATE RTN PRESSURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 (Note 2) | KP0006/3 |  |  |  | 01
SU10 | SU10-CY-001 | SU10-C-001 | PKG | 107-AB | SOLENOID VALVE | SU10 SAMPLE UNIT | 067.2 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU10 | SU10-FI-001 | SU10-F-001 | PKG | 107-AB | VA FLOW METER | SU10 SAMPLE UNIT | 067.2 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU10 | SU10-FSL-001 | SU10-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU10 SAMPLE UNIT | 067.2 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU10 | SU10-HS-001 | SU10-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU10 SAMPLE UNIT | 067.2 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU10 | SU10-HS-002 | SU10-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU10 SAMPLE UNIT | 067.2 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU10 | SU10-HS-003 | SU10-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU10 SAMPLE UNIT | 067.2 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU10 | SU10-HS-004 | SU10-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU10 SAMPLE UNIT | 067.2 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU10 | SU10-XL-001 | SU10-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU10 SAMPLE UNIT | 067.2 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU10 | SU10-XL-002 | SU10-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU10 SAMPLE UNIT | 067.2 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU10 | SU10-YS-001 | SU10-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU10 SAMPLE UNIT | 067.2 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU11 | SU11-CY-001 | SU11-C-001 | PKG | 107-AB | SOLENOID VALVE | SU11 SAMPLE UNIT | 067.2 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU11 | SU11-FI-001 | SU11-F-001 | PKG | 107-AB | VA FLOW METER | SU11 SAMPLE UNIT | 067.2 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU11 | SU11-FSL-001 | SU11-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU11 SAMPLE UNIT | 067.2 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU11 | SU11-HS-001 | SU11-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU11 SAMPLE UNIT | 067.2 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU11 | SU11-HS-002 | SU11-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU11 SAMPLE UNIT | 067.2 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU11 | SU11-HS-003 | SU11-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU11 SAMPLE UNIT | 067.2 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU11 | SU11-HS-004 | SU11-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU11 SAMPLE UNIT | 067.2 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU11 | SU11-XL-001 | SU11-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU11 SAMPLE UNIT | 067.2 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU11 | SU11-XL-002 | SU11-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU11 SAMPLE UNIT | 067.2 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU11 | SU11-YS-001 | SU11-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU11 SAMPLE UNIT | 067.2 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU12 | SU12-CY-001 | SU12-C-001 | PKG | 107-AB | SOLENOID VALVE | SU12 SAMPLE UNIT | 067.2 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU12 | SU12-FI-001 | SU12-F-001 | PKG | 107-AB | VA FLOW METER | SU12 SAMPLE UNIT | 067.2 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU12 | SU12-FSL-001 | SU12-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU12 SAMPLE UNIT | 067.2 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU12 | SU12-HS-001 | SU12-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU12 SAMPLE UNIT | 067.2 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU12 | SU12-HS-002 | SU12-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU12 SAMPLE UNIT | 067.2 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU12 | SU12-HS-003 | SU12-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU12 SAMPLE UNIT | 067.2 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU12 | SU12-HS-004 | SU12-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU12 SAMPLE UNIT | 067.2 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU12 | SU12-XL-001 | SU12-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU12 SAMPLE UNIT | 067.2 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU12 | SU12-XL-002 | SU12-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU12 SAMPLE UNIT | 067.2 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU12 | SU12-YS-001 | SU12-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU12 SAMPLE UNIT | 067.2 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU13 | SU13-CY-001 | SU13-C-001 | PKG | 107-AB | SOLENOID VALVE | SU13 SAMPLE UNIT | 067.3 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU13 | SU13-FI-001 | SU13-F-001 | PKG | 107-AB | VA FLOW METER | SU13 SAMPLE UNIT | 067.3 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU13 | SU13-FSL-001 | SU13-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU13 SAMPLE UNIT | 067.3 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU13 | SU13-HS-001 | SU13-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU13 SAMPLE UNIT | 067.3 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU13 | SU13-HS-002 | SU13-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU13 SAMPLE UNIT | 067.3 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU13 | SU13-HS-003 | SU13-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU13 SAMPLE UNIT | 067.3 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU13 | SU13-HS-004 | SU13-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU13 SAMPLE UNIT | 067.3 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU13 | SU13-HS-005 | SU13-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU13 SAMPLE UNIT | 067.3 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU13 | SU13-HS-006 | SU13-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU13 SAMPLE UNIT | 067.3 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU13 | SU13-XL-001 | SU13-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU13 SAMPLE UNIT | 067.3 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU13 | SU13-XL-002 | SU13-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU13 SAMPLE UNIT | 067.3 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU13 | SU13-YS-001 | SU13-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU13 SAMPLE UNIT | 067.3 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU14 | SU14-CY-001 | SU14-C-001 | PKG | 107-AB | SOLENOID VALVE | SU14 SAMPLE UNIT | 067.3 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU14 | SU14-FI-001 | SU14-F-001 | PKG | 107-AB | VA FLOW METER | SU14 SAMPLE UNIT | 067.3 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU14 | SU14-FSL-001 | SU14-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU14 SAMPLE UNIT | 067.3 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU14 | SU14-HS-001 | SU14-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU14 SAMPLE UNIT | 067.3 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU14 | SU14-HS-002 | SU14-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU14 SAMPLE UNIT | 067.3 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU14 | SU14-HS-003 | SU14-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU14 SAMPLE UNIT | 067.3 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU14 | SU14-HS-004 | SU14-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU14 SAMPLE UNIT | 067.3 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU14 | SU14-HS-005 | SU14-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU14 SAMPLE UNIT | 067.3 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU14 | SU14-HS-006 | SU14-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU14 SAMPLE UNIT | 067.3 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU14 | SU14-XL-001 | SU14-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU14 SAMPLE UNIT | 067.3 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU14 | SU14-XL-002 | SU14-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU14 SAMPLE UNIT | 067.3 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU14 | SU14-YS-001 | SU14-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU14 SAMPLE UNIT | 067.3 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU15 | SU15-CY-001 | SU15-C-001 | PKG | 107-AB | SOLENOID VALVE | SU15 SAMPLE UNIT | 067.3 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU15 | SU15-FI-001 | SU15-F-001 | PKG | 107-AB | VA FLOW METER | SU15 SAMPLE UNIT | 067.3 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU15 | SU15-FSL-001 | SU15-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU15 SAMPLE UNIT | 067.3 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU15 | SU15-HS-001 | SU15-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU15 SAMPLE UNIT | 067.3 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU15 | SU15-HS-002 | SU15-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU15 SAMPLE UNIT | 067.3 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU15 | SU15-HS-003 | SU15-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU15 SAMPLE UNIT | 067.3 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU15 | SU15-HS-004 | SU15-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU15 SAMPLE UNIT | 067.3 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU15 | SU15-XL-001 | SU15-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU15 SAMPLE UNIT | 067.3 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU15 | SU15-XL-002 | SU15-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU15 SAMPLE UNIT | 067.3 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU15 | SU15-YS-001 | SU15-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU15 SAMPLE UNIT | 067.3 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU16 | SU16-CY-001 | SU16-C-001 | PKG | 107-AB | SOLENOID VALVE | SU16 SAMPLE UNIT | 067.3 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU16 | SU16-FI-001 | SU16-F-001 | PKG | 107-AB | VA FLOW METER | SU16 SAMPLE UNIT | 067.3 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU16 | SU16-FSL-001 | SU16-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU16 SAMPLE UNIT | 067.3 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU16 | SU16-HS-001 | SU16-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU16 SAMPLE UNIT | 067.3 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU16 | SU16-HS-002 | SU16-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU16 SAMPLE UNIT | 067.3 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU16 | SU16-HS-003 | SU16-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU16 SAMPLE UNIT | 067.3 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU16 | SU16-HS-004 | SU16-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU16 SAMPLE UNIT | 067.3 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU16 | SU16-HS-005 | SU16-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU16 SAMPLE UNIT | 067.3 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU16 | SU16-HS-006 | SU16-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU16 SAMPLE UNIT | 067.3 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU16 | SU16-XL-001 | SU16-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU16 SAMPLE UNIT | 067.3 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU16 | SU16-XL-002 | SU16-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU16 SAMPLE UNIT | 067.3 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU16 | SU16-YS-001 | SU16-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU16 SAMPLE UNIT | 067.3 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU17 | SU17-CY-001 | SU17-C-001 | PKG | 107-AB | SOLENOID VALVE | SU17 SAMPLE UNIT | 067.3 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU17 | SU17-FI-001 | SU17-F-001 | PKG | 107-AB | VA FLOW METER | SU17 SAMPLE UNIT | 067.3 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU17 | SU17-FSL-001 | SU17-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU17 SAMPLE UNIT | 067.3 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU17 | SU17-HS-001 | SU17-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU17 SAMPLE UNIT | 067.3 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU17 | SU17-HS-002 | SU17-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU17 SAMPLE UNIT | 067.3 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU17 | SU17-HS-003 | SU17-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU17 SAMPLE UNIT | 067.3 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU17 | SU17-HS-004 | SU17-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU17 SAMPLE UNIT | 067.3 | MIAN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU17 | SU17-XL-001 | SU17-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU17 SAMPLE UNIT | 067.3 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU17 | SU17-XL-002 | SU17-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU17 SAMPLE UNIT | 067.3 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU17 | SU17-YS-001 | SU17-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU17 SAMPLE UNIT | 067.3 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU18 | SU18-CY-001 | SU18-C-001 | PKG | 107-AB | SOLENOID VALVE | SU18 SAMPLE UNIT | 067.3 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU18 | SU18-FI-001 | SU18-F-001 | PKG | 107-AB | VA FLOW METER | SU18 SAMPLE UNIT | 067.3 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU18 | SU18-FSL-001 | SU18-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU18 SAMPLE UNIT | 067.3 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU18 | SU18-HS-001 | SU18-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU18 SAMPLE UNIT | 067.3 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU18 | SU18-HS-002 | SU18-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU18 SAMPLE UNIT | 067.3 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU18 | SU18-HS-003 | SU18-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU18 SAMPLE UNIT | 067.3 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU18 | SU18-HS-004 | SU18-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU18 SAMPLE UNIT | 067.3 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU18 | SU18-XL-001 | SU18-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU18 SAMPLE UNIT | 067.3 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU18 | SU18-XL-002 | SU18-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU18 SAMPLE UNIT | 067.3 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU18 | SU18-YS-001 | SU18-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU18 SAMPLE UNIT | 067.3 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU19 | SU19-CY-001 | SU19-C-001 | PKG | 107-AB | SOLENOID VALVE | SU19 SAMPLE UNIT | 067.4 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU19 | SU19-FI-001 | SU19-F-001 | PKG | 107-AB | VA FLOW METER | SU19 SAMPLE UNIT | 067.4 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU19 | SU19-FSL-001 | SU19-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU19 SAMPLE UNIT | 067.4 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU19 | SU19-HS-001 | SU19-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU19 SAMPLE UNIT | 067.4 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU19 | SU19-HS-002 | SU19-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU19 SAMPLE UNIT | 067.4 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU19 | SU19-HS-003 | SU19-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU19 SAMPLE UNIT | 067.4 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU19 | SU19-HS-004 | SU19-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU19 SAMPLE UNIT | 067.4 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU19 | SU19-HS-005 | SU19-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU19 SAMPLE UNIT | 067.4 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU19 | SU19-HS-006 | SU19-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU19 SAMPLE UNIT | 067.4 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU19 | SU19-XL-001 | SU19-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU19 SAMPLE UNIT | 067.4 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU19 | SU19-XL-002 | SU19-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU19 SAMPLE UNIT | 067.4 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU19 | SU19-YS-001 | SU19-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU19 SAMPLE UNIT | 067.4 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU1 | SU1-CY-001 | SU1-C-001 | PKG | 107-AB | SOLENOID VALVE | SU1 SAMPLE UNIT | 067.1 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU1 | SU1-FI-001 | SU1-F-001 | PKG | 107-AB | VA FLOW METER | SU1 SAMPLE UNIT | 067.1 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU1 | SU1-FSL-001 | SU1-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU1 SAMPLE UNIT | 067.1 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU1 | SU1-HS-001 | SU1-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU1 SAMPLE UNIT | 067.1 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU1 | SU1-HS-002 | SU1-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU1 SAMPLE UNIT | 067.1 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU1 | SU1-HS-003 | SU1-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU1 SAMPLE UNIT | 067.1 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU1 | SU1-HS-004 | SU1-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU1 SAMPLE UNIT | 067.1 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU1 | SU1-HS-005 | SU1-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU1 SAMPLE UNIT | 067.1 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU1 | SU1-HS-006 | SU1-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU1 SAMPLE UNIT | 067.1 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU1 | SU1-XL-001 | SU1-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU1 SAMPLE UNIT | 067.1 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU1 | SU1-XL-002 | SU1-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU1 SAMPLE UNIT | 067.1 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU1 | SU1-YS-001 | SU1-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU1 SAMPLE UNIT | 067.1 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU20 | SU20-CY-001 | SU20-C-001 | PKG | 107-AB | SOLENOID VALVE | SU20 SAMPLE UNIT | 067.4 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU20 | SU20-FI-001 | SU20-F-001 | PKG | 107-AB | VA FLOW METER | SU20 SAMPLE UNIT | 067.4 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU20 | SU20-FSL-001 | SU20-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU20 SAMPLE UNIT | 067.4 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU20 | SU20-HS-001 | SU20-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU20 SAMPLE UNIT | 067.4 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU20 | SU20-HS-002 | SU20-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU20 SAMPLE UNIT | 067.4 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU20 | SU20-HS-003 | SU20-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU20 SAMPLE UNIT | 067.4 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU20 | SU20-HS-004 | SU20-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU20 SAMPLE UNIT | 067.4 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU20 | SU20-HS-005 | SU20-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU20 SAMPLE UNIT | 067.4 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU20 | SU20-HS-006 | SU20-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU20 SAMPLE UNIT | 067.4 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU20 | SU20-XL-001 | SU20-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU20 SAMPLE UNIT | 067.4 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU20 | SU20-XL-002 | SU20-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU20 SAMPLE UNIT | 067.4 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU20 | SU20-YS-001 | SU20-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU20 SAMPLE UNIT | 067.4 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU21 | SU21-CY-001 | SU21-C-001 | PKG | 107-AB | SOLENOID VALVE | SU21 SAMPLE UNIT | 067.4 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU21 | SU21-FI-001 | SU21-F-001 | PKG | 107-AB | VA FLOW METER | SU21 SAMPLE UNIT | 067.4 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU21 | SU21-FSL-001 | SU21-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU21 SAMPLE UNIT | 067.4 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU21 | SU21-HS-001 | SU21-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU21 SAMPLE UNIT | 067.4 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU21 | SU21-HS-002 | SU21-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU21 SAMPLE UNIT | 067.4 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU21 | SU21-HS-003 | SU21-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU21 SAMPLE UNIT | 067.4 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU21 | SU21-HS-004 | SU21-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU21 SAMPLE UNIT | 067.4 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU21 | SU21-XL-001 | SU21-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU21 SAMPLE UNIT | 067.4 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU21 | SU21-XL-002 | SU21-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU21 SAMPLE UNIT | 067.4 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU21 | SU21-YS-001 | SU21-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU21 SAMPLE UNIT | 067.4 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU22 | SU22-CY-001 | SU22-C-001 | PKG | 107-AB | SOLENOID VALVE | SU22 SAMPLE UNIT | 067.4 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU22 | SU22-FI-001 | SU22-F-001 | PKG | 107-AB | VA FLOW METER | SU22 SAMPLE UNIT | 067.4 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU22 | SU22-FSL-001 | SU22-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU22 SAMPLE UNIT | 067.4 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU22 | SU22-HS-001 | SU22-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU22 SAMPLE UNIT | 067.4 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU22 | SU22-HS-002 | SU22-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU22 SAMPLE UNIT | 067.4 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU22 | SU22-HS-003 | SU22-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU22 SAMPLE UNIT | 067.4 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU22 | SU22-HS-004 | SU22-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU22 SAMPLE UNIT | 067.4 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU22 | SU22-HS-005 | SU22-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU22 SAMPLE UNIT | 067.4 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU22 | SU22-HS-006 | SU22-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU22 SAMPLE UNIT | 067.4 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU22 | SU22-XL-001 | SU22-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU22 SAMPLE UNIT | 067.4 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU22 | SU22-XL-002 | SU22-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU22 SAMPLE UNIT | 067.4 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU22 | SU22-YS-001 | SU22-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU22 SAMPLE UNIT | 067.4 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU2 | SU2-CY-001 | SU2-C-001 | PKG | 107-AB | SOLENOID VALVE | SU2 SAMPLE UNIT | 067.1 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU2 | SU2-FI-001 | SU2-F-001 | PKG | 107-AB | VA FLOW METER | SU2 SAMPLE UNIT | 067.1 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU2 | SU2-FSL-001 | SU2-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU2 SAMPLE UNIT | 067.1 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU2 | SU2-HS-001 | SU2-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU2 SAMPLE UNIT | 067.1 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU2 | SU2-HS-002 | SU2-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU2 SAMPLE UNIT | 067.1 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU2 | SU2-HS-003 | SU2-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU2 SAMPLE UNIT | 067.1 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU2 | SU2-HS-004 | SU2-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU2 SAMPLE UNIT | 067.1 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU2 | SU2-HS-005 | SU2-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU2 SAMPLE UNIT | 067.1 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU2 | SU2-HS-006 | SU2-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU2 SAMPLE UNIT | 067.1 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU2 | SU2-XL-001 | SU2-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU2 SAMPLE UNIT | 067.1 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU2 | SU2-XL-002 | SU2-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU2 SAMPLE UNIT | 067.1 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU2 | SU2-YS-001 | SU2-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU2 SAMPLE UNIT | 067.1 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU3 | SU3-CY-001 | SU3-C-001 | PKG | 107-AB | SOLENOID VALVE | SU3 SAMPLE UNIT | 067.1 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU3 | SU3-FI-001 | SU3-F-001 | PKG | 107-AB | VA FLOW METER | SU3 SAMPLE UNIT | 067.1 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU3 | SU3-FSL-001 | SU3-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU3 SAMPLE UNIT | 067.1 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU3 | SU3-HS-001 | SU3-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU3 SAMPLE UNIT | 067.1 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU3 | SU3-HS-002 | SU3-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU3 SAMPLE UNIT | 067.1 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU3 | SU3-HS-003 | SU3-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU3 SAMPLE UNIT | 067.1 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU3 | SU3-HS-004 | SU3-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU3 SAMPLE UNIT | 067.1 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU3 | SU3-HS-005 | SU3-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU3 SAMPLE UNIT | 067.1 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU3 | SU3-HS-006 | SU3-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU3 SAMPLE UNIT | 067.1 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU3 | SU3-XL-001 | SU3-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU3 SAMPLE UNIT | 067.1 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU3 | SU3-XL-002 | SU3-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU3 SAMPLE UNIT | 067.1 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU3 | SU3-YS-001 | SU3-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU3 SAMPLE UNIT | 067.1 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU4 | SU4-CY-001 | SU4-C-001 | PKG | 107-AB | SOLENOID VALVE | SU4 SAMPLE UNIT | 067.1 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU4 | SU4-FI-001 | SU4-F-001 | PKG | 107-AB | VA FLOW METER | SU4 SAMPLE UNIT | 067.1 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU4 | SU4-FSL-001 | SU4-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU4 SAMPLE UNIT | 067.1 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU4 | SU4-HS-001 | SU4-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU4 SAMPLE UNIT | 067.1 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU4 | SU4-HS-002 | SU4-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU4 SAMPLE UNIT | 067.1 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU4 | SU4-HS-003 | SU4-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU4 SAMPLE UNIT | 067.1 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU4 | SU4-HS-004 | SU4-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU4 SAMPLE UNIT | 067.1 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU4 | SU4-HS-005 | SU4-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU4 SAMPLE UNIT | 067.1 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU4 | SU4-HS-006 | SU4-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU4 SAMPLE UNIT | 067.1 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU4 | SU4-XL-001 | SU4-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU4 SAMPLE UNIT | 067.1 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU4 | SU4-XL-002 | SU4-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU4 SAMPLE UNIT | 067.1 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU4 | SU4-YS-001 | SU4-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU4 SAMPLE UNIT | 067.1 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU5 | SU5-CY-001 | SU5-C-001 | PKG | 107-AB | SOLENOID VALVE | SU5 SAMPLE UNIT | 067.1 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU5 | SU5-FI-001 | SU5-F-001 | PKG | 107-AB | VA FLOW METER | SU5 SAMPLE UNIT | 067.1 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU5 | SU5-FSL-001 | SU5-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU5 SAMPLE UNIT | 067.1 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU5 | SU5-HS-001 | SU5-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU5 SAMPLE UNIT | 067.1 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU5 | SU5-HS-002 | SU5-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU5 SAMPLE UNIT | 067.1 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU5 | SU5-HS-003 | SU5-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU5 SAMPLE UNIT | 067.1 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU5 | SU5-HS-004 | SU5-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU5 SAMPLE UNIT | 067.1 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU5 | SU5-XL-001 | SU5-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU5 SAMPLE UNIT | 067.1 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU5 | SU5-XL-002 | SU5-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU5 SAMPLE UNIT | 067.1 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU5 | SU5-YS-001 | SU5-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU5 SAMPLE UNIT | 067.1 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU6 | SU6-CY-001 | SU6-C-001 | PKG | 107-AB | SOLENOID VALVE | SU6 SAMPLE UNIT | 067.1 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU6 | SU6-FI-001 | SU6-F-001 | PKG | 107-AB | VA FLOW METER | SU6 SAMPLE UNIT | 067.1 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU6 | SU6-FSL-001 | SU6-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU6 SAMPLE UNIT | 067.1 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU6 | SU6-HS-001 | SU6-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU6 SAMPLE UNIT | 067.1 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU6 | SU6-HS-002 | SU6-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU6 SAMPLE UNIT | 067.1 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU6 | SU6-HS-003 | SU6-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU6 SAMPLE UNIT | 067.1 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU6 | SU6-HS-004 | SU6-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU6 SAMPLE UNIT | 067.1 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU6 | SU6-XL-001 | SU6-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU6 SAMPLE UNIT | 067.1 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU6 | SU6-XL-002 | SU6-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU6 SAMPLE UNIT | 067.1 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU6 | SU6-YS-001 | SU6-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU6 SAMPLE UNIT | 067.1 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU7 | SU7-CY-001 | SU7-C-001 | PKG | 107-AB | SOLENOID VALVE | SU7 SAMPLE UNIT | 067.2 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU7 | SU7-FI-001 | SU7-F-001 | PKG | 107-AB | VA FLOW METER | SU7 SAMPLE UNIT | 067.2 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU7 | SU7-FSL-001 | SU7-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU7 SAMPLE UNIT | 067.2 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU7 | SU7-HS-001 | SU7-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU7 SAMPLE UNIT | 067.2 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU7 | SU7-HS-002 | SU7-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU7 SAMPLE UNIT | 067.2 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU7 | SU7-HS-003 | SU7-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU7 SAMPLE UNIT | 067.2 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU7 | SU7-HS-004 | SU7-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU7 SAMPLE UNIT | 067.2 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU7 | SU7-HS-005 | SU7-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU7 SAMPLE UNIT | 067.2 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU7 | SU7-HS-006 | SU7-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU7 SAMPLE UNIT | 067.2 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU7 | SU7-XL-001 | SU7-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU7 SAMPLE UNIT | 067.2 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU7 | SU7-XL-002 | SU7-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU7 SAMPLE UNIT | 067.2 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU7 | SU7-YS-001 | SU7-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU7 SAMPLE UNIT | 067.2 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU8 | SU8-CY-001 | SU8-C-001 | PKG | 107-AB | SOLENOID VALVE | SU8 SAMPLE UNIT | 067.2 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU8 | SU8-FI-001 | SU8-F-001 | PKG | 107-AB | VA FLOW METER | SU8 SAMPLE UNIT | 067.2 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU8 | SU8-FSL-001 | SU8-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU8 SAMPLE UNIT | 067.2 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU8 | SU8-HS-001 | SU8-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU8 SAMPLE UNIT | 067.2 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU8 | SU8-HS-002 | SU8-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU8 SAMPLE UNIT | 067.2 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU8 | SU8-HS-003 | SU8-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU8 SAMPLE UNIT | 067.2 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU8 | SU8-HS-004 | SU8-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU8 SAMPLE UNIT | 067.2 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU8 | SU8-HS-005 | SU8-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU8 SAMPLE UNIT | 067.2 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU8 | SU8-HS-006 | SU8-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU8 SAMPLE UNIT | 067.2 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU8 | SU8-XL-001 | SU8-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU8 SAMPLE UNIT | 067.2 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU8 | SU8-XL-002 | SU8-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU8 SAMPLE UNIT | 067.2 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU8 | SU8-YS-001 | SU8-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU8 SAMPLE UNIT | 067.2 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU9 | SU9-CY-001 | SU9-C-001 | PKG | 107-AB | SOLENOID VALVE | SU9 SAMPLE UNIT | 067.2 | AIR SUPPLY |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU9 | SU9-FI-001 | SU9-F-001 | PKG | 107-AB | VA FLOW METER | SU9 SAMPLE UNIT | 067.2 | N2 FLOW | -: 50 - 500 l/hr; -: +/- 2.5%; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU9 | SU9-FSL-001 | SU9-F-001 | PKG | 107-AB | SWITCH - FLOW - LOW | SU9 SAMPLE UNIT | 067.2 | N2 FLOW |  | set @ no flow | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU9 | SU9-HS-001 | SU9-H-001 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU9 SAMPLE UNIT | 067.2 | RESET |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU9 | SU9-HS-002 | SU9-H-002 | LCP | 107-AB | SWITCH - HAND OP. | SU9 SAMPLE UNIT | 067.2 | OPEN/CLOSE SAMPLER | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU9 | SU9-HS-003 | SU9-H-003 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU9 SAMPLE UNIT | 067.2 | N2 BLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU9 | SU9-HS-004 | SU9-H-004 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU9 SAMPLE UNIT | 067.2 | MAIN RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU9 | SU9-HS-005 | SU9-H-005 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU9 SAMPLE UNIT | 067.2 | PRESSURE BALANCE | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU9 | SU9-HS-006 | SU9-H-006 | LCP | 107-AB | SWITCH - PUSHBUTTON | SU9 SAMPLE UNIT | 067.2 | PRE-RINSING | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU9 | SU9-XL-001 | SU9-X-001 | LCP | 107-AB | INDICATOR - PANEL | SU9 SAMPLE UNIT | 067.2 | UNIT ON |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SU9 | SU9-XL-002 | SU9-X-002 | LCP | 107-AB | INDICATOR - PANEL | SU9 SAMPLE UNIT | 067.2 | UNIT ON | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
SU9 | SU9-YS-001 | SU9-Y-001 | PKG | 107-AB | SWITCH - POSITION | SU9 SAMPLE UNIT | 067.2 | FLASK POSITION |  | - | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
SWT01 | SWT01-PI-001 | SWT01-P-001 | PKG | 107-HJ | PRESSURE GAUGE | SWT01 | 138.1 | SWT01 PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
SWT01 | SWT01-PSV-002 | SWT01-P-002 | PKG | 107-HJ | PRESSURE RELIEF VALVE | SWT01 | 138.1 | SWT01 RELIEF | -: 6 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SWT02 | SWT02-PI-001 | SWT02-P-001 | PKG | 107-HJ | PRESSURE GAUGE | SWT02 | 138.2 | SWT02 PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
SWT02 | SWT02-PSV-002 | SWT02-P-002 | PKG | 107-HJ | PRESSURE RELIEF VALVE | SWT02 | 138.2 | SWT02 RELIEF | -: 6 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SWT03 | SWT03-PI-001 | SWT03-P-001 | PKG | 107-HJ | PRESSURE GAUGE | SWT03 | 138.3 | SWT03 PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
SWT03 | SWT03-PSV-002 | SWT03-P-002 | PKG | 107-HJ | PRESSURE RELIEF VALVE | SWT03 | 138.3 | SWT03 RELIEF | -: 6 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SWT04 | SWT04-PI-001 | SWT04-P-001 | PKG | 107-HJ | PRESSURE GAUGE | SWT04 | 138.4 | SWT04 PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
SWT04 | SWT04-PSV-002 | SWT04-P-002 | PKG | 107-HJ | PRESSURE RELIEF VALVE | SWT04 | 138.4 | SWT04 RELIEF | -: 6 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SWT05 | SWT05-PI-001 | SWT05-P-001 | PKG | 107-HJ | PRESSURE GAUGE | SWT05 | 138.5 | SWT05 PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
SWT05 | SWT05-PSV-002 | SWT05-P-002 | PKG | 107-HJ | PRESSURE RELIEF VALVE | SWT05 | 138.5 | SWT05 RELIEF | -: 6 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SWT06 | SWT06-PI-001 | SWT06-P-001 | PKG | 107-HJ | PRESSURE GAUGE | SWT06 | 138.6 | SWT06 PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
SWT06 | SWT06-PSV-002 | SWT06-P-002 | PKG | 107-HJ | PRESSURE RELIEF VALVE | SWT06 | 138.6 | SWT06 RELIEF | -: 6 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SWT07 | SWT07-PI-001 | SWT07-P-001 | PKG | 107-HJ | PRESSURE GAUGE | SWT07 | 138.7 | SWT07 PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
SWT07 | SWT07-PSV-002 | SWT07-P-002 | PKG | 107-HJ | PRESSURE RELIEF VALVE | SWT07 | 138.7 | SWT07 RELIEF | -: 6 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SWT08 | SWT08-PI-001 | SWT08-P-001 | PKG | 107-HJ | PRESSURE GAUGE | SWT08 | 138.8 | SWT08 PRESSURE | REF: REF; REQ: By request; F: C |  |  | 0 | [7 empty] | 01
SWT08 | SWT08-PSV-002 | SWT08-P-002 | PKG | 107-HJ | PRESSURE RELIEF VALVE | SWT08 | 138.8 | SWT08 RELIEF | -: 6 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
SWT09 | SWT09-PSV-001 | SWT09-P-001 | PKG | 107-HJ | PRESSURE RELIEF VALVE | SWT09 | 138.9 | SWT09 RELIEF | -: 0 to 2 barg; -: +/- 10%; REQ: 24; F: C | [10 empty] | 10
TB01 | TB01-CV-001 | TB01-C-001 | FLD | 107-BS | BALL VALVE - ON/OFF - F.C. | 25-CA-SSIU-0-9028557 | 042.2 | COMP. AIR TO DRUM PUMP | 7091 | - | - | REF | REQ | F | [5 empty] | 0 | UTIL |  |  | KV0017 |  |  |  | 01
TB01 | TB01-CY-001 | TB01-C-001 | FLD | 107-BS | SOLENOID VALVE | RACK MOUNTED |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TB01 | TB01-ZSC-001 | TB01-C-001 | FLD | 107-BS | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TB01 | TB01-ZSO-001 | TB01-C-001 | FLD | 107-BS | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TB01 | TB01-FIT-001 | TB01-F-001 | [6 empty] | PKG: L8116; REF: REF; REQ: By request
TB01 | TB01-FIT-001A | TB01-F-001 | FLD | 107-BS | TRANSMITTER - FLOW | 10-P-HS1T-0-9021841 | 029.5 | METERING FLOW | L8116 |  |  | REF | By request | C |  | N.I.S | DI |  |  | 36 | GP1 | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
TB01 | TB01-FIT-001B | TB01-F-001 | FLD | 107-BS | TRANSMITTER - FLOW |  | 029.5 | METERING FLOW | L8116 |  |  | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP1 | ENDRESS + HAUSER | NOTE 1 |  |  | 4 to 20mA |  | 01
TB01 | TB01-FQIC-001 | TB01-F-001 | PCS | 107-BS | INDICATING CONT - FLOW/TOTALISER |  |  | METERING FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TB01 | TB01-PRV-001 | TB01-P-001 | PKG | 107-BS | CONTROL VALVE SELF ACTUATING | 25-CA-SS1U-0-9028557 | 082.1 | AIR TO DP01 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TB01 | TB01-PDI-006 | TB01-P-006 | PKG | 107-BS | INDICATOR - DIFF PRESSURE | TB01 | 029.5 | AIR FLOW | L8941 | 0 to 60 pA | +/-3 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB01 | TB01-PDSH-006 | TB01-P-006 | CPR | 107-BS | SWITCH - PRESSURE - DIFF - HIGH | IE19446 | 029.5 | AIR FLOW | L8941 | 0 to 60Pa | Actuating set point = 35Pa | SHE | 12 | C | [5 empty] | 0 | GP1 | [6 empty] | 01
TB01 | TB01-PDSL-006 | TB01-P-006 | CPR | 107-BS | SWITCH - PRESSURE - DIFF - LOW | IE19446 | 029.5 | AIR FLOW | L8941 | 0 to 60 Pa | Actuating set point = 10Pa | SHE | 12 | C | [5 empty] | 0 | GP1 | [6 empty] | 01
TB01 | TB01-PDT-006 | TB01-P-006 | PKG | 107-BS | TRANSMITTER - PRESSURE - DIFFERENTIAL | TB01 | 029.5 | AIR FLOW | L8941 | 0 to 60 pA | +/-1% | SHE | 12 | C | [7 empty] | FURNESS | FC054IS |  |  |  |  | 01
| TB01-PI-007 | TB01-P-007 | PCS | 107-BS | INDICATOR - PRESSURE |  |  | PRESSURE | -: 0 to 10 barg; -: +/-10%; REF: SHE; REQ: 12 |  |  | 0 | GP1
TB01 | TB01-PSH-007 | TB01-P-007 | FLD | 107-BS | SWITCH - PRESSURE - HIGH | TB01 | 029.5 | HIGH PRESSURE |  | 8 barg rising | +/-25% | SHE | 12 | F |  | I.S. | [5 empty] | PEPPERL + FUCHS | KFD2-CRG2-Ex1.D |  |  | HW Trip on high pressure (TB01-P3)
| TB01-PT-007 | TB01-P-007 | FLD | 107-BS | SWITCH - PRESSURE - HIGH | TB01 | 029.5 | PRESSURE |  | 0 to 10 barg | +/-10% | SHE | 12 | C |  | I.S. | AI |  |  |  | GP1 | WIKA | IS-3
TB01 | TB01-DS-001 | TB01-S-001 | MCC | 107-BS | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | METERING PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
TB01 | TB01-DY-001 | TB01-S-001 | MCC | 107-BS | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | METERING PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
TB01 | TB01-DYC-001A | TB01-S-001 | MCC | 107-BS | DRIVE - START/STOP - FORWARD | MOTOR CONTROL CENTRE | 029.5 | METERING PUMP |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
TB01 | TB01-DYC-001B | TB01-S-001 | MCC | 107-BS | DRIVE - START/STOP - REVERSE | MOTOR CONTROL CENTRE | 029.5 | METERING PUMP |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
TB01 | TB01-SC-001 | TB01-S-001 | MCC | 107-BS | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 029.5 | METERING PUMP | 8940 | 6 - 130 l/hr | +/- 1% | REF | REQ | F |  | N.I.S | AO |  |  | 22 | GP1 | [6 empty] | 01
TB01 | TB01-SIC-001 | TB01-S-001 | PCS | 107-BS | INDICATING CONTROLLER - SPEED |  |  | METERING PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TB01 | TB01-XA-001 | TB01-X-001 | PKG | 107-BS | ALARM - AUDIBLE | TB01 | 029.5 | COMMON ALARM | 6357 | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | GP1 | COOPER MEDC | DB5 |  | TI702-SP-5156 |  |  | 01
TB01 | TB01-XL-001 | TB01-X-001 | PKG | 107-BS | INDICATOR - LAMP | TB01 | 029.5 | COMMON ALARM |  | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | GP1 | EAO | 704.950.0 |  | TI702-SP-5155 |  |  | 01
TB01 | TB01-YA-001 | TB01-Y-001 | PCS | 107-BS | ALARM - COMMON |  |  | COMMON ALARM | PKG: L8941; -: PCS Common Alarm function check; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
TB01 | TB01-YS-001 | TB01-Y-001 | CPR | 107-BS | COMMON ALARM | IE19446 | 029.5 | COMMON ALARM | 8941 | - | - | REF | 12 | F |  | I.S | DI |  |  | 32 | GP1 | FURNESS CONTROLS LTD | FCO54 |  | TI702-SP-5154 | PDSL/PDSH-006 |  | 01
TB02 | TB02-CV-001 | TB02-C-001 | FLD | 107-CS | BALL VALVE - ON/OFF - F.C. | 25-CA-SS1U-0-9028565 | 042.2 | COMP. AIR TO DRUM PUMP | 7092 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
TB02 | TB02-CY-001 | TB02-C-001 | FLD | 107-CS | SOLENOID VALVE | RACK MOUNTED |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TB02 | TB02-ZSC-001 | TB02-C-001 | FLD | 107-CS | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TB02 | TB02-ZSO-001 | TB02-C-001 | FLD | 107-CS | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TB02 | TB02-FIT-001 | TB02-F-001 | [6 empty] | PKG: L8117; REF: REF; REQ: By request
TB02 | TB02-FIT-001A | TB02-F-001 | FLD | 107-CS | TRANSMITTER - FLOW | 10-P-HS1T-0-9022841 | 029.6 | METERING FLOW | L8117 |  |  | REF | By request | C |  | N.I.S | DI |  |  | 36 | GP2 | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
TB02 | TB02-FIT-001B | TB02-F-001 | FLD | 107-CS | TRANSMITTER - FLOW |  | 029.6 | METERING FLOW | L8117 |  |  | REF | By request | C |  | N.I.S | AI |  |  | 13 | GP2 | ENDRESS + HAUSER | NOTE 1 |  |  | 4 to 20mA |  | 01
TB02 | TB02-FQIC-001 | TB02-F-001 | PCS | 107-CS | INDICATING CONT - FLOW/TOTALISER |  |  | METERING FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TB02 | TB02-PRV-001 | TB02-P-001 | PKG | 107-CS | CONTROL VALVE SELF ACTUATING | 25-CA-SS1U-0-9028565 | 082.2 | AIR TO DP02 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TB02 | TB02-PDI-006 | TB02-P-006 | PKG | 107-CS | INDICATOR - DIFF PRESSURE | TB02 | 029.6 | AIR FLOW | L8942 | 0 to 60 pA | +/-3 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB02 | TB02-PDSH-006 | TB02-P-006 | CPR | 107-CS | SWITCH - PRESSURE - DIFF - HIGH | IE19440 | 029.6 | AIR FLOW | L8942 | 0 to 60 Pa | Actuating set point = 35 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB02 | TB02-PDSL-006 | TB02-P-006 | CPR | 107-CS | SWITCH - PRESSURE - DIFF - LOW | IE19440 | 029.6 | AIR FLOW | L8942 | 0 to 60 Pa | Actuating set point = 10 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB02 | TB02-PDT-006 | TB02-P-006 | PKG | 107-CS | TRANSMITTER - PRESSURE - DIFFERENTIAL | TB02 | 029.6 | AIR FLOW | L8942 | 0 to 60 Pa | +/-1 % | SHE | 12 | C | [7 empty] | FURNESS | FC054IS |  |  |  |  | 01
| TB02-PI-007 | TB02-P-007 | PCS | 107-CS | INDICATOR - PRESSURE |  |  | PRESSURE | -: 0 to 10 barg; -: +/-10%; REF: SHE; REQ: 12 |  |  | 0 | GP2 | [7 empty] | 11
| TB02-PSH-007 | TB02-P-007 | FLD | 107-CS | SWITCH - PRESSURE - HIGH | TB02 | 29.6 | HIGH PRESSURE |  | 8 barg rising | +/-25% | SHE | 12 | F |  | I.S. | [5 empty] | PEPPERL + FUCHS | KFD2-CRG2-Ex1.D |  |  | HW Trip on high pressure (TB02-P2) |  |  | 11
| TB02-PT-007 | TB02-P-007 | FLD | 107-CS | SWITCH - PRESSURE - HIGH | TB02 | 29.6 | PRESSURE |  | 0 to 10 barg | +/-10% | SHE | 12 | C |  | I.S. | AI |  |  |  | GP2 | WIKA | IS-3 | [5 empty] | 11
TB02 | TB02-DS-001 | TB02-S-001 | MCC | 107-CS | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | METERING PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
TB02 | TB02-DY-001 | TB02-S-001 | MCC | 107-CS | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | METERING PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
TB02 | TB02-DYC-001A | TB02-S-001 | MCC | 107-CS | DRIVE - START/STOP - FORWARD | MOTOR CONTROL CENTRE | 029.6 | METERING PUMP |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
TB02 | TB02-DYC-001B | TB02-S-001 | MCC | 107-CS | DRIVE - START/STOP - REVERSE | MOTOR CONTROL CENTRE | 029.6 | METERING PUMP |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
TB02 | TB02-SC-001 | TB02-S-001 | MCC | 107-CS | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 029.6 | METERING PUMP | 8943 | 6 - 130 l/hr | +/- 1% | REF | REQ | F |  | N.I.S | AO |  |  | 22 | GP2 | [6 empty] | 01
TB02 | TB02-SIC-001 | TB02-S-001 | PCS | 107-CS | INDICATING CONTROLLER - SPEED |  |  | METERING PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TB02 | TB02-XA-001 | TB02-X-001 | PKG | 107-CS | ALARM - MISC. | TB02 | 029.6 | COMMON ALARM | 8944 | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | GP2 | COOPER MEDC | DB5 |  | TI702-SP-5156 |  |  | 01
TB02 | TB02-XL-001 | TB02-X-001 | PKG | 107-CS | INDICATOR - LAMP | TB02 | 029.6 | COMMON ALARM |  | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | GP2 | EAO | 704.950.0 |  | TI702-SP-5155 |  |  | 01
TB02 | TB02-YA-001 | TB02-Y-001 | PCS | 107-CS | ALARM - COMMON |  |  | COMMON ALARM | PKG: L15797; -: PCS Common Alarm function check; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
TB02 | TB02-YS-001 | TB02-Y-001 | CPR | 107-CS | COMMON ALARM | IE19440 | 029.6 | COMMON ALARM | 8942 | - | - | REF | 12 | F |  | I.S | DI |  |  | 32 | GP2 | FURNESS CONTROLS LTD | FCO54 |  | TI702-SP-5154 | DPSL/PDSH-006 |  | 01
TB03 | TB03-CV-001 | TB03-C-001 | FLD | 107-DT | BALL VALVE - ON/OFF - F.C. | 25-CA-SS1U-0-9028457 | 042.2 | COMP. AIR TO DRUM PUMP | 7094 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
TB03 | TB03-CY-001 | TB03-C-001 | FLD | 107-DT | SOLENOID VALVE | RACK MOUNTED |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TB03 | TB03-ZSC-001 | TB03-C-001 | FLD | 107-DT | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TB03 | TB03-ZSO-001 | TB03-C-001 | FLD | 107-DT | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TB03 | TB03-FIT-001 | TB03-F-001 | [6 empty] | PKG: L8118; REF: REF; REQ: By request
TB03 | TB03-FIT-001A | TB03-F-001 | FLD | 107-DT | TRANSMITTER - FLOW | 10-P-HS1T-0-9023881 | 029.7 | METERING FLOW | L8118 | 0.001 l/pulse | +/- 0.1% | REF | By request | C |  | I.S | DI |  |  | 36 | FG1 | EMERSON | Micro Motion F-Series |  |  |  |  | 01 | 20
TB03 | TB03-FIT-001B | TB03-F-001 | FLD | 107-DT | TRANSMITTER - FLOW |  | 029.7 | METERING FLOW | L8118 | 0 to 300 l/hr | +/- 0.1% | REF | By request | C |  | I.S | AI |  |  | 13 | FG1 |  |  |  |  | 4 to 20mA |  | 01 | 20
TB03 | TB03-FQIC-001 | TB03-F-001 | PCS | 107-DT | INDICATING CONT - FLOW/TOTALISER |  |  | METERING FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TB03 | TB03-PRV-001 | TB03-P-001 | PKG | 107-DT | CONTROL VALVE SELF ACTUATING | 25-CA-SS1U-0-9028457 | 080.3 | AIR TO DP03 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TB03 | TB03-PDI-006 | TB03-P-006 | PKG | 107-DT | INDICATOR - DIFF PRESSURE | TB03 | 029.7 | AIR FLOW | L8945 | 0 to 60 pA | +/-3 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB03 | TB03-PDSH-006 | TB03-P-006 | CPR | 107-DT | SWITCH - PRESSURE - DIFF - HIGH | IE19442 | 029.7 | AIR FLOW | L8945 | 0 to 60 Pa | Actuating set point = 35 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB03 | TB03-PDSL-006 | TB03-P-006 | CPR | 107-DT | SWITCH - PRESSURE - DIFF - LOW | IE19442 | 029.7 | AIR FLOW | L8945 | 0 to 60 Pa | Actuating set point = 10 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB03 | TB03-PDT-006 | TB03-P-006 | PKG | 107-DT | TRANSMITTER - PRESSURE - DIFFERENTIAL | TB03 | 029.7 | AIR FLOW | L8945 | 0 to 60 pA | +/- 1% | SHE | 12 | C | [7 empty] | FURNESS | FC054IS |  |  |  |  | 01
| TB03-PI-007 | TB03-P-007 | PCS | 107-DT | INDICATOR - PRESSURE |  |  | PRESSURE | -: 0 to 10 barg; -: +/-10%; REF: SHE; REQ: 12 |  |  | 0 | FG1 | [7 empty] | 11
| TB03-PSH-007 | TB03-P-007 | FLD | 107-DT | SWITCH - PRESSURE - HIGH | TB03 | 29.7 | HIGH PRESSURE |  | 8 barg rising | +/-25% | SHE | 12 | F |  | I.S. | [5 empty] | PEPPERL + FUCHS | KFD2-CRG2-Ex1.D |  |  | HW Trip on high pressure (TB03-P2) |  |  | 11
| TB03-PT-007 | TB03-P-007 | FLD | 107-DT | SWITCH - PRESSURE - HIGH | TB03 | 29.7 | PRESSURE |  | 0 to 10 barg | +/-10% | SHE | 12 | C |  | I.S. | AI |  |  |  | FG1 | WIKA | IS-3 | [5 empty] | 11
TB03 | TB03-DS-001 | TB03-S-001 | MCC | 107-DT | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | METERING PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
TB03 | TB03-DY-001 | TB03-S-001 | MCC | 107-DT | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | METERING PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
TB03 | TB03-DYC-001A | TB03-S-001 | MCC | 107-DT | DRIVE - START/STOP - FORWARD | MOTOR CONTROL CENTRE | 029.7 | METERING PUMP |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
TB03 | TB03-DYC-001B | TB03-S-001 | MCC | 107-DT | DRIVE - START/STOP - REVERSE | MOTOR CONTROL CENTRE | 029.7 | METERING PUMP |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
TB03 | TB03-SC-001 | TB03-S-001 | MCC | 107-DT | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 029.7 | METERING PUMP | 8946 | 6 - 130 l/hr | +/- 1% | REF | REQ | F |  | N.I.S | AO |  |  | 22 | FG1 | [6 empty] | 01
TB03 | TB03-SIC-001 | TB03-S-001 | PCS | 107-DT | INDICATING CONTR. - MOTOR DRIVE |  |  | METERING PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TB03 | TB03-XA-001 | TB03-X-001 | PKG | 107-DT | ALARM - MISC. | TB03 | 029.7 | COMMON ALARM | 8947 | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | FG1 | COOPER MEDC | DB5 |  | TI702-SP-5156 |  |  | 01
TB03 | TB03-XL-001 | TB03-X-001 | PKG | 107-DT | INDICATOR - LAMP | TB03 | 029.7 | COMMON ALARM |  | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | FG1 | EAO | 704.950.0 |  | TI702-SP-5155 |  |  | 01
TB03 | TB03-YA-001 | TB03-Y-001 | PCS | 107-DT | ALARM - COMMON |  |  | COMMON ALARM | PKG: L15798; -: PCS Common Alarm function check; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
TB03 | TB03-YS-001 | TB03-Y-001 | CPR | 107-DT | COMMON ALARM | IE19442 | 029.7 | COMMON ALARM | 8945 | - | - | REF | 12 | F |  | I.S | DI |  |  | 32 | FG1 | FURNESS CONTROLS LTD | FCO54 |  | TI702-SP-5154 | PDSL/PDSH-006 |  | 01
TB04 | TB04-CV-001 | TB04-C-001 | FLD | 107-ET | BALL VALVE - ON/OFF - F.C. | 25-CA-SS1U-0-9028468 | 042.2 | COMP. AIR TO DRUM PUMP | 7093 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
TB04 | TB04-CY-001 | TB04-C-001 | FLD | 107-ET | SOLENOID VALVE | RACK MOUNTED |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TB04 | TB04-ZSC-001 | TB04-C-001 | FLD | 107-ET | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TB04 | TB04-ZSO-001 | TB04-C-001 | FLD | 107-ET | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | COMP. AIR TO DRUM PUMP | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TB04 | TB04-FIT-001 | TB04-F-001 | [6 empty] | PKG: L8119; REF: REF; REQ: By request
TB04 | TB04-FIT-001A | TB04-F-001 | FLD | 107-ET | TRANSMITTER - FLOW | 10-P-HS1T-0-9024881 | 029.8 | METERING FLOW | L8119 |  |  | REF | By request | C |  | N.I.S | DI |  |  | 36 | C1 | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
TB04 | TB04-FIT-001B | TB04-F-001 | FLD | 107-ET | TRANSMITTER - FLOW |  | 029.8 | METERING FLOW | L8119 |  |  | REF | By request | C |  | N.I.S | AI |  |  | 13 | C1 | ENDRESS + HAUSER | NOTE 1 |  |  | 4 to 20mA |  | 01
TB04 | TB04-FQIC-001 | TB04-F-001 | PCS | 107-ET | INDICATING CONT - FLOW/TOTALISER |  |  | METERING FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TB04 | TB04-PRV-001 | TB04-P-001 | PKG | 107-ET | CONTROL VALVE SELF ACTUATING | 25-CA-SS1U-0-9028468 | 080.4 | AIR TO DP04 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TB04 | TB04-PDI-006 | TB04-P-006 | PKG | 107-ET | INDICATOR - DIFF PRESSURE | TB04 | 029.8 | AIR FLOW | L8948 | 0 to 60 pA | +/-3 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB04 | TB04-PDSH-006 | TB04-P-006 | CPR | 107-ET | SWITCH - PRESSURE - DIFF - HIGH | IE19442 | 029.8 | AIR FLOW | L8948 | 0 to 60 Pa | Actuating set point = 35 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB04 | TB04-PDSL-006 | TB04-P-006 | CPR | 107-ET | SWITCH - PRESSURE - DIFF - LOW | IE19442 | 029.8 | AIR FLOW | L8948 | 0 to 60 Pa | Actuating set point = 10 Pa | SHE | 12 | C | [5 empty] | 0 | [7 empty] | 01
TB04 | TB04-PDT-006 | TB04-P-006 | PKG | 107-ET | TRANSMITTER - PRESSURE - DIFFERENTIAL | TB04 | 029.8 | AIR FLOW | L8948 | 0 to 60 pA | +/- 1% | SHE | 12 | C | [7 empty] | FURNESS | FC054IS |  |  |  |  | 01
| TB04-PI-007 | TB04-P-007 | PCS | 107-ET | INDICATOR - PRESSURE |  |  | PRESSURE | -: 0 to 10 barg; -: +/-10%; REF: SHE; REQ: 12 |  |  | 0 | C1 | [7 empty] | 11
| TB04-PSH-007 | TB04-P-007 | FLD | 107-ET | SWITCH - PRESSURE - HIGH | TB04 | 29.8 | HIGH PRESSURE |  | 8 barg rising | +/-25% | SHE | 12 | F |  | I.S. | [5 empty] | PEPPERL + FUCHS | KFD2-CRG2-Ex1.D |  |  | HW Trip on high pressure (TB04-P2) |  |  | 11
| TB04-PT-007 | TB04-P-007 | FLD | 107-ET | SWITCH - PRESSURE - HIGH | TB04 | 29.8 | PRESSURE |  | 0 to 10 barg | +/-10% | SHE | 12 | C |  | I.S. | AI |  |  |  | C1 | WIKA | IS-3 | [5 empty] | 11
TB04 | TB04-DS-001 | TB04-S-001 | MCC | 107-ET | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | METERING PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
TB04 | TB04-DY-001 | TB04-S-001 | MCC | 107-ET | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | METERING PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
TB04 | TB04-DYC-001A | TB04-S-001 | MCC | 107-ET | DRIVE - START/STOP - FORWARD | MOTOR CONTROL CENTRE | 029.8 | METERING PUMP |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
TB04 | TB04-DYC-001B | TB04-S-001 | MCC | 107-ET | DRIVE - START/STOP - REVERSE | MOTOR CONTROL CENTRE | 029.8 | METERING PUMP |  | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
TB04 | TB04-SC-001 | TB04-S-001 | MCC | 107-ET | SPEED CONTROLLER - MCC | MOTOR CONTROL CENTRE | 029.8 | METERING PUMP | 8949 | 6 - 130 l/hr | +/- 1% | REF | REQ | F |  | N.I.S | AO |  |  | 22 | C1 | [6 empty] | 01
TB04 | TB04-SIC-001 | TB04-S-001 | PCS | 107-ET | INDICATING CONTR. - MOTOR DRIVE |  |  | METERING PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TB04 | TB04-XA-001 | TB04-X-001 | PKG | 107-ET | ALARM - MISC. | TB04 | 029.8 | COMMON ALARM | 8101 | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | C1 | COOPER MEDC | DB5 |  | TI702-SP-5156 |  |  | 01
TB04 | TB04-XL-001 | TB04-X-001 | PKG | 107-ET | INDICATOR - LAMP | TB04 | 029.8 | COMMON ALARM |  | - | - | REF | 12 | F |  | I.S | DO |  |  | 41 | C1 | EAO | 704.950.0 |  | TI702-SP-5155 |  |  | 01
TB04 | TB04-YA-001 | TB04-Y-001 | PCS | 107-ET | ALARM - COMMON |  |  | COMMON ALARM | PKG: L8948; -: PCS Common Alarm function check; REF: SHE; REQ: 12 |  |  | 0 | [7 empty] | 01
TB04 | TB04-YS-001 | TB04-Y-001 | CPR | 107-ET | COMMON ALARM | IE19449 | 029.8 | COMMON ALARM | 8948 | - | - | REF | 12 | F |  | I.S | DI |  |  | 32 | C1 | FURNESS CONTROLS LTD | FCO54 |  | TI702-SP-5154 | PDSL/PDSH-006 |  | 01
TD01 | TD01-BD-001 | TD01-B-001 | DEL | 107-BV | RUPTURE DISC | DELETED |  | DELETED | [11 empty] | 0 |  | BS&B | FRS | KS0003 |  | SPARE(DELETED) |  | 01
TD01 | TD01-YI-001 | TD01-B-001 | DEL | 107-BV | ALARM - RUPTURE DISC FAIL | DELETED |  | DELETED | [11 empty] | 0 | [5 empty] | DELETED |  | 01
TD01 | TD01-CV-001 | TD01-C-001 | FLD | 107-BV | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9021950 | 043.4 | DRYER NITROGEN SUPPLY | 7125 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TD01 | TD01-CY-001 | TD01-C-001 | FLD | 107-BV | SOLENOID VALVE | RACK MOUNTED |  | DRYER NITROGEN SUPPLY | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD01 | TD01-ZSC-001 | TD01-C-001 | FLD | 107-BV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DRYER NITROGEN SUPPLY | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD01 | TD01-ZSO-001 | TD01-C-001 | FLD | 107-BV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DRYER NITROGEN SUPPLY | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD01 | TD01-CV-002 | TD01-C-002 | FLD | 107-BV | V-BALL VALVE - CONTROL - F.C. | 40-VP-PT1A-0-9021955 | 102.0 | DRYER VACUUM | 6850 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 | TBC - TI702-SP-5090 |  | 01
TD01 | TD01-CV-003 | TD01-C-003 | FLD | 107-BV | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9021955 | 038.0 | DRYER VACUUM | 7265 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TD01 | TD01-CY-003 | TD01-C-003 | FLD | 107-BV | SOLENOID VALVE | RACK MOUNTED |  | DRYER VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD01 | TD01-ZSC-003 | TD01-C-003 | FLD | 107-BV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DRYER VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD01 | TD01-ZSO-003 | TD01-C-003 | FLD | 107-BV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DRYER VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD01 | TD01-CV-004 | TD01-C-004 | FLD | 107-BV | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-0-9021952 | 102.0 | TRAY DRYER VACUUM | 7292 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TD01 | TD01-CY-004 | TD01-C-004 | FLD | 107-BV | SOLENOID VALVE | RACK MOUNTED |  | TRAY DRYER VACUUM | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD01 | TD01-ZSC-004 | TD01-C-004 | FLD | 107-BV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TRAY DRYER VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD01 | TD01-ZSO-004 | TD01-C-004 | FLD | 107-BV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TRAY DRYER VACUUM | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD01 | TD01-CV-006 | TD01-C-006 | FLD | 107-BV | V-BALL VALVE - CONTROL - F.C. | 40-P-PT1A-0-9021953 | 102.0 | DRYER VENT | 6815 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 | TBC - TI702-SP-5090 |  | 01
TD01 | TD01-CV-007 | TD01-C-007 | FLD | 107-BV | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9021953 | 008.2 | DRYER VENT | 7266 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TD01 | TD01-CY-007 | TD01-C-007 | FLD | 107-BV | SOLENOID VALVE | RACK MOUNTED |  | DRYER VENT | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD01 | TD01-ZSC-007 | TD01-C-007 | FLD | 107-BV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | DRYER VENT | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD01 | TD01-ZSO-007 | TD01-C-007 | FLD | 107-BV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | DRYER VENT | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD01 | TD01-CV-008 | TD01-C-008 | FLD | 107-BV | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-C-9021974 | 102.0 | RECEIVER N2 SUPPLY | 6799 | 0 T0 100% | - | REF | REQ | F |  | I.S | AO |  |  | 21 | FG1 | ATOMAC / MOORE | AKH-3 / 760EA15EAAGNNB8 POSITIONER | KV0004 | TI702-SP-5090 | TBC - TI702-SP-5090 |  | 01
TD01 | TD01-FI-001 | TD01-F-001 | FLD | 107-BV | IN-LINE PITOT TUBE | 25-N-SS1U-0-9028806 | 043.4 | N2 SUPPLY | REF: REF; REQ: By request; F: C |  |  | 0 |  | PLATON | 1-EF612/EMS175 |  |  | C/W MAGNAHELIC dP GAUGE |  | 01
TD01 | TD01-HS-001 | TD01-H-001 | LCP | 107-BV | SWITCH - HAND OP. | TD01 LOCAL PANEL | 102.0 | VACUUM MAKE VALVE CELL 1 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HV-001 | TD01-H-001 | PKG | 107-BV | VACUUM MAKE VALVE | 50-P-PT1A-E-9021961 | 102.0 | VACUUM MAKE VALVE CELL 1 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HS-002 | TD01-H-002 | LCP | 107-BV | SWITCH - HAND OP. | TD01 LOCAL PANEL | 102.0 | N2 SWEEP VALVE CELL 1 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HV-002 | TD01-H-002 | PKG | 107-BV | VACUUM BREAK VALVE | 25-N-PT1A-0-9021950 | 102.0 | N2 SWEEP VALVE CELL 1 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HS-003 | TD01-H-003 | LCP | 107-BV | SWITCH - HAND OP. | TD01 LOCAL PANEL | 102.0 | VACUUM MAKE VALVE CELL 2 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HV-003 | TD01-H-003 | PKG | 107-BV | VACUUM MAKE VALVE | 50-P-PT1A-E-9021961 | 102.0 | VACUUM MAKE VALVE CELL 2 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HS-004 | TD01-H-004 | LCP | 107-BV | SWITCH - HAND OP. | TD01 LOCAL PANEL | 102.0 | N2 SWEEP VALVE CELL 2 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HV-004 | TD01-H-004 | PKG | 107-BV | VACUUM BREAK VALVE | 25-N-PT1A-0-9021950 | 102.0 | N2 SWEEP VALVE CELL 2 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HS-005 | TD01-H-005 | LCP | 107-BV | SWITCH - HAND OP. | TD01 LOCAL PANEL | 102.0 | VACUUM MAKE VALVE CELL 3 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HV-005 | TD01-H-005 | PKG | 107-BV | VACUUM MAKE VALVE | 50-P-PT1A-E-9021961 | 102.0 | VACUUM MAKE VALVE CELL 3 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HS-006 | TD01-H-006 | LCP | 107-BV | SWITCH - HAND OP. | TD01 LOCAL PANEL | 102.0 | N2 SWEEP VALVE CELL 3 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HV-006 | TD01-H-006 | PKG | 107-BV | VACUUM BREAK VALVE | 25-N-PT1A-0-9021950 | 102.0 | N2 SWEEP VALVE CELL 3 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HS-007 | TD01-H-007 | LCP | 107-BV | SWITCH - HAND OP. | TD01 LOCAL PANEL | 102.0 | VACUUM MAKE VALVE CELL 4 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HV-007 | TD01-H-007 | PKG | 107-BV | VACUUM MAKE VALVE | 50-P-PT1A-E-9021961 | 102.0 | VACUUM MAKE VALVE CELL 4 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HS-008 | TD01-H-008 | LCP | 107-BV | SWITCH - HAND OP. | TD01 LOCAL PANEL | 102.0 | N2 SWEEP VALVE CELL 4 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HV-008 | TD01-H-008 | PKG | 107-BV | VACUUM BREAK VALVE | 25-N-PT1A-0-9021950 | 102.0 | N2 SWEEP VALVE CELL 4 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TD01 | TD01-HV-009 | TD01-H-009 | FLD | 107-BV | V BALL HAND VALVE | 25-N-SS1U-0-9028806 | [13 empty] | 0 |  | HABONIM | 31 Series V-FLOW |  |  |  |  | 01 | bar: PKG to -
TD01 | TD01-LI-001A | TD01-L-001 | PCS | 107-BV | INDICATOR - LEVEL |  |  | RECEIVER LEVEL | REQ: By request |  |  | 0 | [7 empty] | 01
TD01 | TD01-LI-001B | TD01-L-001 | FLD | 107-BV | INDICATOR - LEVEL |  | 102.0 | RECEIVER LEVEL | REQ: By request; F: C; I.S: I.S |  |  | 0 |  |  |  | KX0017 |  |  |  | 01
TD01 | TD01-LT-001 | TD01-L-001 | FLD | 107-BV | TRANSMITTER - LEVEL | TD01-RC1/L1/50 | 102.0 | RECEIVER LEVEL | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | ENDRESS + HAUSER | FMR245E note3 | KL0028/P2 | TI702-SP-5026 |  |  | 01
TD01 | TD01-PI-001 | TD01-P-001 | PCS | 107-BV | INDICATOR - PRESSURE |  |  | OUTLET PRESSURE | REQ: By request |  |  | 0 | [7 empty] | 01
TD01 | TD01-PT-001 | TD01-P-001 | PKG | 107-BV | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-E-9021961 | 102.0 | OUTLET PRESSURE | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | ENDRESS + HAUSER | PMP 731 |  | TI702-SP-5083 |  |  | 01
TD01 | TD01-PIC-002 | TD01-P-002 | PCS | 107-BV | INDICATING CONTROLLER - PRESSURE |  |  | VC1 INLET PRESSURE | REQ: By request |  |  | 0 | [7 empty] | 01
TD01 | TD01-PIT-002 | TD01-P-002 | FLD | 107-BV | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-E-9021952 | 102.0 | VC1 INLET PRESSURE | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
TD01 | TD01-PI-004 | TD01-P-004 | FLD | 107-BV | PRESSURE GAUGE | 40-HWF-CS1B-H-9028945 | 074.0 | HOT WATER SUPPLY PRESSURE | -: 0 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
TD01 | TD01-PI-007 | TD01-P-007 | FLD | 107-BV | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-C-9021959 | 102.0 | RC1 PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
TD01 | TD01-PSV-008 | TD01-P-008 | FLD | 107-BV | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9021972 | 102.0 | VC1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
TD01 | TD01-PSV-009 | TD01-P-009 | PKG | 107-BV | PRESSURE RELIEF VALVE | 50-P-PT1A-C-9021973 | 102.0 | RC1 RELIEF | -: 1.0 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 | [7 empty] | 01
TD01 | TD01-PRV-010 | TD01-P-010 | FLD | 107-BV | CONTROL VALVE SELF ACTUATING | 40-HWF-CS1B-H-9028945 | 074.0 | HOT WATER SUPPLY | -: 0.8 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  |  | R1480S | KV0006 |  |  |  | 01
TD01 | TD01-PSV-011 | TD01-P-011 | FLD | 107-BV | PRESSURE RELIEF VALVE | 40-HWF-CS1B-H-9028945 | 074.0 | HOT WATER SUPPLY RELIEF | -: 1 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2511H-S-N000 | KS0001 |  |  |  | 01
TD01 | TD01-PI-012 | TD01-P-012 | LCP | 107-BV | PRESSURE GAUGE | TD01 LOCAL PANEL | 102.0 | VACUUM CELL 1 | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TD01 | TD01-PI-013 | TD01-P-013 | LCP | 107-BV | PRESSURE GAUGE | TD01 LOCAL PANEL | 102.0 | VACUUM CELL 2 | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TD01 | TD01-PI-014 | TD01-P-014 | LCP | 107-BV | PRESSURE GAUGE | TD01 LOCAL PANEL | 102.0 | VACUUM CELL 3 | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TD01 | TD01-PI-015 | TD01-P-015 | LCP | 107-BV | PRESSURE GAUGE | TD01 LOCAL PANEL | 102.0 | VACUUM CELL 4 | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TD01 | TD01-PRV-016 | TD01-P-016 | PKG | 107-BV | CONTROL VALVE SELF ACTUATING | WITH MTP01 | 089.1 | AIR TO MTP01 | -: set @ commish.; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TD01 | TD01-PRV-017 | TD01-P-017 | PKG | 107-BV | AIR FILTER REGULATOR | ADJ TD01 REAR | 089.1 | TD01 AIR SUPPLY | -: set @ 5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TD01 | TD01-TT-001 | TD01-T-001 | [6 empty] | PKG: L8105; -: 0 to 100 degC; -: +/-2degC; REF: GxP/SHE; REQ: 12
TD01 | TD01-TE-002 | TD01-T-002 | FLD | 107-BV | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-D-9021969 |  | HOT WATER SUPPLY TEMP. | PKG: L6593; REF: SHE; REQ: By request |  |  | 0 | [7 empty] | 32
TD01 | TD01-TI-002B | TD01-T-002 | LCP | 107-BV | INDICATOR - TEMPERATURE | TD01 LOCAL PANEL | 102.0 | HOT WATER SUPPLY TEMP. | PKG: L6593; REF: SHE; REQ: By request; F: C; I.S: I.S |  |  | 0 | [7 empty] | 32
TD01 | TD01-TIC-002 | TD01-T-002 | PCS | 107-BV | INDICATING CONTROLLER - TEMPERATURE |  |  | HOT WATER SUPPLY TEMP. | REF: SHE; REQ: REQ |  |  | 0 | [7 empty] | 32
TD01 | TD01-TT-002 | TD01-T-002 | FLD | 107-BV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 102.0 | HOT WATER SUPPLY TEMP. | L6593 |  |  | SHE | By request | C |  | I.S | AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 32
TD01 | TD01-TI-002A | TD01-T-002A | [6 empty] | PKG: L6593; REF: SHE; REQ: By request
TD01 | TD01-TI-003 | TD01-T-003 | FLD | 107-BV | INDICATOR - TEMPERATURE | 40-HWR-CS1B-H-9021966 | 074.0 | HOT WATER RTN TEMPERATURE | -: 0 to 100 degC; -: +/- 2%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | S5550/4 | KT0003 |  |  |  | 01
TD01 | TD01-TE-004 | TD01-T-004 | FLD | 107-BV | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9021953 |  | VC1 VENT TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
TD01 | TD01-TI-004 | TD01-T-004 | PCS | 107-BV | INDICATOR - TEMPERATURE |  |  | VC1 VENT TEMPERATURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
TD01 | TD01-TT-004 | TD01-T-004 | FLD | 107-BV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 102.0 | VC1 VENT TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
TD01 | TD01-TE-005 | TD01-T-005 | FLD | 107-BV | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9021956 |  | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
TD01 | TD01-TI-005 | TD01-T-005 | PCS | 107-BV | INDICATOR - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request |  |  | 0 | [7 empty] | 01
TD01 | TD01-TT-005 | TD01-T-005 | FLD | 107-BV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 102.0 | VC1 HTF RTN TEMPERATURE | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | FG1 | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
TD02 | TD02-PSH-018B | TD02-018A | [6 empty] | PKG: L13306; -: -50Pa falling; -: +/-5 Pa; REF: REF; REQ: 12
TD02 | TD02-AT-001 | TD02-A-001 | PKG | 107-DV | TRANSMITTER - ANALYSER | TRAY DRYER | 168.0 |  | REF: N/A; REQ: By request; F: C; Ref: SHE | [10 empty] | 01
TD02 | TD02-BD-001 | TD02-B-001 | FLD | 107-DV | RUPTURE DISC | 50-P-PT1A-C-9023068 | 168.0 | RC1 BURSTING DISC | 13281 | 1.0 barg | - | N/A | - | - | - | I.S | DI | 1 |  | 32 | FG1 | BS&B | SPR-7 / BAS + | KS0003/P4 | TI702-SP-5077 |  |  | 01
TD02 | TD02-YI-001 | TD02-B-001 | PCS | 107-DV | ALARM - RUPTURE DISC FAIL |  |  | RC1 BURSTING DISC | REF: SHE; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-CV-001 | TD02-C-001 | FLD | 107-DV | BALL VALVE - ON/OFF - F.C. | 25-N-PT1A-0-9023061 | 168.0 | DRYER NITROGEN SUPPLY | 13282 | - | - | SHE | - | - | - | [8 empty] | KV0007/P2 |  |  |  | 01
TD02 | TD02-CY-001 | TD02-C-001 | FLD | 107-DV | SOLENOID VALVE | RACK MOUNTED | 168.0 | DRYER NITROGEN SUPPLY | 13282 |  |  | SHE | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD02 | TD02-ZSC-001 | TD02-C-001 | FLD | 107-DV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 168.0 | DRYER NITROGEN SUPPLY | 13282 |  |  | SHE | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-ZSO-001 | TD02-C-001 | FLD | 107-DV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 168.0 | DRYER NITROGEN SUPPLY | 13282 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-CV-002 | TD02-C-002 | FLD | 107-DV | V-BALL VALVE - CONTROL - F.C. | 40-VP-PT1A-0-9023072 | 168.0 | DRYER VACUUM | 13283 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004/P1 | TI702-SP-5008 |  |  | 01
TD02 | TD02-CV-003 | TD02-C-003 | FLD | 107-DV | BALL VALVE - ON/OFF - F.C. | 40-VP-PT1A-0-9023072 | 168.0 | DRYER VACUUM | 13284 | - | - | N/A | - | - | - | [8 empty] | KV0007/P2 |  |  |  | 01
TD02 | TD02-CY-003 | TD02-C-003 | FLD | 107-DV | SOLENOID VALVE | RACK MOUNTED | 168.0 | DRYER VACUUM | 13284 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD02 | TD02-ZSC-003 | TD02-C-003 | FLD | 107-DV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 168.0 | DRYER VACUUM | 13284 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-ZSO-003 | TD02-C-003 | FLD | 107-DV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 168.0 | DRYER VACUUM | 13284 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-CV-004 | TD02-C-004 | FLD | 107-DV | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-H-9023062 | 168.0 | TRAY DRYER VACUUM | 13285 | - | - | N/A | - | - | - | [8 empty] | KV0007/P2 |  |  |  | 01
TD02 | TD02-CY-004 | TD02-C-004 | FLD | 107-DV | SOLENOID VALVE | RACK MOUNTED | 168.0 | TRAY DRYER VACUUM | 13285 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD02 | TD02-ZSC-004 | TD02-C-004 | FLD | 107-DV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 168.0 | TRAY DRYER VACUUM | 13285 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-ZSO-004 | TD02-C-004 | FLD | 107-DV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 168.0 | TRAY DRYER VACUUM | 13285 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-CV-006 | TD02-C-006 | FLD | 107-DV | V-BALL VALVE - CONTROL - F.C. | 40-P-PT1A-0-9023065 | 168.0 | DRYER SCRUBBER | 13286 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004/P1 | TI702-SP-5008 |  |  | 01
TD02 | TD02-CV-007 | TD02-C-007 | FLD | 107-DV | BALL VALVE - ON/OFF - F.C. | 40-P-PT1A-0-9023065 | 168.0 | TO ACID SCRUBBER | 13287 | - | - | N/A | - | - | - | [8 empty] | KV0007/P2 |  |  |  | 01
TD02 | TD02-CY-007 | TD02-C-007 | FLD | 107-DV | SOLENOID VALVE | RACK MOUNTED | 168.0 | TO ACID SCRUBBER | 13287 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD02 | TD02-ZSC-007 | TD02-C-007 | FLD | 107-DV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 168.0 | TO ACID SCRUBBER | 13287 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-ZSO-007 | TD02-C-007 | FLD | 107-DV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 168.0 | TO ACID SCRUBBER | 13287 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-CV-017 | TD02-C-017 | FLD | 107-DV | V-BALL VALVE - CONTROL - F.C. | 25-N-PT1A-C-9023069 | 168.0 | NITROGEN TO RC1 | 13288 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004/P1 | TI702-SP-5008 |  |  | 01
TD02 | TD02-CV-018 | TD02-C-018 | FLD | 107-DV | BALL VALVE - ON/OFF - F.C. | 25-P-PT1A-0-9023782 | 168.0 | TP1 DISCHARGE | 13289 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
TD02 | TD02-CY-018 | TD02-C-018 | FLD | 107-DV | SOLENOID VALVE | RACK MOUNTED | 168.0 | TP1 DISCHARGE | 13289 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD02 | TD02-ZSC-018 | TD02-C-018 | FLD | 107-DV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 168.0 | TP1 DISCHARGE | 13289 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-ZSO-018 | TD02-C-018 | FLD | 107-DV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 168.0 | TP1 DISCHARGE | 13289 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-CV-021 | TD02-C-021 | FLD | 107-DV | V-BALL VALVE - CONTROL - F.C. | 50-SV-SS1C-0-9023060 | 168.0 | GLOVEBOX SCRUBBER | 13290 | 0 T0 100% | - | N/A | - | - | - | I.S | AO | 1 |  | 21 | FG1 | ATOMAC / SAMSON | AKH-3 / 3730-2 POSITIONER | KV0004/P1 | TI702-SP-5008 |  |  | 01
TD02 | TD02-CV-022 | TD02-C-022 | FLD | 107-DV | BALL VALVE - ON/OFF - F.C. | 50-SV-GR1A-0-9023070 | 168.0 | TO ACID SCRUBBER | 13291 | - | - | N/A | - | - | - | [6 empty] | XOMOX TUFLIN | R202 | KV0007/P2 |  |  |  | 01
TD02 | TD02-CY-022 | TD02-C-022 | FLD | 107-DV | SOLENOID VALVE | RACK MOUNTED | 168.0 | TO ACID SCRUBBER | 13291 |  |  | N/A | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD02 | TD02-ZSC-022 | TD02-C-022 | FLD | 107-DV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 168.0 | TO ACID SCRUBBER | 13291 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-ZSO-022 | TD02-C-022 | FLD | 107-DV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 168.0 | TO ACID SCRUBBER | 13291 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-CV-031 | TD02-C-031 | PKG | 107-HH | V-BALL VALVE - CONTROL - F.C. |  | 168.0 | HEAT/COOL PACKAGE | REF: SHE; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-CV-032 | TD02-C-032 | FLD | 107-DV | BALL VALVE - ON/OFF - F.C. | 25-N-SS1U-O-902??? | 168.0 | N2 TO GLOVEBOX |  | - | - | SHE | - | - | - | [8 empty] | KV0007/P2 |  |  |  | 01
TD02 | TD02-CY-032 | TD02-C-032 | FLD | 107-DV | SOLENOID VALVE | RACK MOUNTED | 168.0 | N2 TO GLOVEBOX | 13305 |  |  | SHE | - | - | - | I.S | DO | 1 |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TD02 | TD02-ZSC-032 | TD02-C-032 | FLD | 107-DV | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 168.0 | N2 TO GLOVEBOX | 13305 |  |  | SHE | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-ZSO-032 | TD02-C-032 | FLD | 107-DV | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 168.0 | N2 TO GLOVEBOX | 13305 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TD02 | TD02-DIC-002 | TD02-D-002 | PCS | 107-DV | INDICATING CONTR. - MOTOR DRIVE |  |  | TP1 TRANSFER PUMP | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-DS-002 | TD02-D-002 | MCC | 107-DV | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13292 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 01
TD02 | TD02-DY-002 | TD02-D-002 | MCC | 107-DV | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13292 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 01
TD02 | TD02-DYC-002 | TD02-D-002 | MCC | 107-DV | DRIVE - START/STOP | MOTOR CONTROL CENTRE |  | TP1 TRANSFER PUMP | 13292 | - | - | N/A | - | - | - | N.I.S | DO | 1 |  | 42 | FG1 | [6 empty] | 01
TD02 | TD02-DY-003 | TD02-D-003 | PKG | 107-HH | PACKAGE RUNNING |  | 168.0 | HEAT/COOL PACKAGE | 13293 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | [7 empty] | 01
TD02 | TD02-DYC-003 | TD02-D-003 | PCS | 107-HH | PACKAGE - START/STOP |  |  | HEAT/COOL PACKAGE | 13293 |  |  | REF | - | - | - | N.I.S | DO | 1 |  | 42 | GP2 | [6 empty] | 01
TD02 | TD02-FI-001 | TD02-F-001 | FLD | 107-DV | IN-LINE PITOT TUBE | 25-N-SS1U-0-9028890 | 168.0 | N2 SUPPLY | REF: REF; REQ: By request; F: C; Ref: Ref |  |  |  |  | PLATON | 1-EF612/EMS175 | KF0027/P3 |  |  |  | 01
TD02 | TD02-FS-011 | TD02-F-011 | PKG | 107-HH | FLOW SWITCH |  | 168.0 | HEAT/COOL PACKAGE | REF: N/A; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
TD02 | TD02-HV-009 | TD02-H-009 | FLD | 107-DV | V BALL HAND VALVE | 25-N-SS1U-0-9028890 | 168.0 | ? |  | - | - | REF | - | - | - | [6 empty] | HABONIM | 31 Series V-FLOW | KV0007/P2 |  |  |  | 01
TD02 | TD02-HS-011 | TD02-H-011 | LCP | 107-DV | SWITCH - HAND OP. | GLOVEBOX PANEL | 168.0 | GLOVEBOX LIGHT | REF: REF; REQ: REQ; F: F; Ref: Ref | [10 empty] | 01
TD02 | TD02-HS-012A | TD02-H-012 | LCP | 107-DV | SWITCH - HAND OP. | GLOVEBOX PANEL | 168.0 | EXTRACT START | REF: REF; REQ: REQ; F: F; Ref: Ref | [10 empty] | 01
TD02 | TD02-HS-012B | TD02-H-012 | LCP | 107-DV | SWITCH - HAND OP. | GLOVEBOX PANEL | 168.0 | EXTRACT STOP | REF: REF; REQ: REQ; F: F; Ref: Ref | [10 empty] | 01
TD02 | TD02-HS-013 | TD02-H-013 | LCP | 107-DV | SWITCH - HAND OP. | GLOVEBOX PANEL | 168.0 | AIR PURGE VALVE | REF: REF; REQ: REQ; F: F; Ref: Ref | [10 empty] | 01
TD02 | TD02-LI-001B | TD02-L-001 | FLD | 107-DV | INDICATOR - LEVEL | FG1 | 168.0 | RECEIVER LEVEL | REF: N/A; REQ: By request; F: C; Ref: Ops; I.S: I.S |  |  |  |  | BEKA | BA324D | KX0017/P1 |  |  |  | 01
TD02 | TD02-LIC-001 | TD02-L-001 | PCS | 107-DV | INDICATOR - LEVEL |  |  | RECEIVER LEVEL | REF: REF; REQ: By request; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-LT-001 | TD02-L-001 | FLD | 107-DV | TRANSMITTER - LEVEL | TD02-RC1/N4/100 | 168.0 | RECEIVER LEVEL |  |  |  | REF | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ENDRESS + HAUSER | FMR245-24APKAA2A | KL0028/P3 | TI702-SP-5026 |  |  | 01
TD02 | TD02-LAH-002 | TD02-L-002 | PCS | 107-DV | ALARM - LEVEL - HIGH |  |  | RC1 HIGH LEVEL | L13295 | off/on | off/on | REF | 24 | - | - | [12 empty] | 01
TD02 | TD02-LSH-002 | TD02-L-002 | FLD | 107-DV | SWITCH - LEVEL - HIGH | 80-P-PT1A-C-9023066 | 168.0 | RC1 HIGH LEVEL | L13295 | off/on | off/on | N/A | 24 | C | Ops | I.S | DI | 1 |  | 31 | FG1 | ENDRESS + HAUSER | FLT51C 4ALKBK8G4AA | KL0014/P2 | TI702-SP-5036 |  |  | 01
TD02 | TD02-PI-001 | TD02-P-001 | PCS | 107-DV | INDICATOR - PRESSURE |  |  | OUTLET PRESSURE | REF: REF; REQ: By request; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-PT-001 | TD02-P-001 | PKG | 107-DV | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-H-9023064 | 168.0 | OUTLET PRESSURE |  |  |  | N/A | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 3051S |  | TI702-SP-5041 |  |  | 01
TD02 | TD02-PIC-002 | TD02-P-002 | PCS | 107-DV | INDICATING CONTROLLER - PRESSURE |  |  | VC1 INLET PRESSURE | REF: REF; REQ: By request; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-PT-002 | TD02-P-002 | FLD | 107-DV | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-PT1A-H-9023062 | 168.0 | VC1 INLET PRESSURE |  |  |  | REF | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 01
TD02 | TD02-PI-004 | TD02-P-004 | FLD | 107-DV | PRESSURE GAUGE | 40-HWF-CS1B-H-9028945 | 168.0 | HOT WATER SUPPLY PRESSURE |  | 0 to 6 barg | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | 232.50.100 | KP0006/P6 |  |  |  | 01
TD02 | TD02-PI-007 | TD02-P-007 | FLD | 107-DV | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-C-9023069 | 168.0 | RC1 PRESSURE |  | -1 to 3 barg | +/- 5% | N/A | REQ | C | Ref | [6 empty] | WIKA | 232.50.100/990.27 | KP0006/P6 |  |  |  | 01
TD02 | TD02-PSV-008 | TD02-P-008 | FLD | 107-DV | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-902???? | 168.0 | VC1 HTF RELIEF |  | 10 barg | +/- 10% | REF | - | - | - | [6 empty] | BROADY | 2531D-C-B000 | KS0001/P |  |  |  | 01
TD02 | TD02-PI-010 | TD02-P-010 | FLD | 107-DV | PRESSURE GAUGE - DIAPHRAGM | 25-P-PT1A-0-9023782 | 168.0 | TP1 DISCHARGE PRESSURE |  | 0 to 4 barg | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | 233.50.100/990.27 | KP0006/P6 |  |  |  | 01
TD02 | TD02-PI-012 | TD02-P-012 | LCP | 107-DV | PRESSURE GAUGE | TD02 LOCAL PANEL | 168.0 | VACUUM CELL 1 | -: -1 to 1.5 barg; -: +/- 5%; REQ: REQ; F: C; Ref: Ref | [10 empty] | 01
TD02 | TD02-PS-013 | TD02-P-013 | [6 empty] | REF: REF; REQ: By request
TD02 | TD02-PRV-017 | TD02-P-017 | PKG | 107-DV | AIR FILTER REGULATOR | ADJ TD02 REAR | 168.0 | TD02 AIR SUPPLY |  | set @ 5 barg | +/- 5% | N/A | REQ | C | Ref | [12 empty] | 01
TD02 | TD02-PC-018 | TD02-P-018 | PCS | 107-DV | INDICATING CONTROLLER - PRESSURE |  |  | GLOVEBOX PRESSURE CONTROL | REF: REF; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-PIC-018 | TD02-P-018 | [6 empty] | PKG: L13306; -: -900 to 100 Pa; -: +/-20Pa; REF: REF; REQ: 24
TD02 | TD02-PSH-018 | TD02-P-018 | CPR | 107-DV | TRIP AMP | GLOVEBOX | 168.0 | GLOVEBOX PURGE SIL | L13306 | -50Pa Falling | +/-5 Pa | REF | 12 | C | SHE | [12 empty] | 01
TD02 | TD02-PT-018 | TD02-P-018 | PKG | 107-DV | TRANSMITTER PRESSURE | GLOVEBOX PANEL | 168.0 | PRESSURE CONTROL | L13306 | -900 to 100Pa | +/-20Pa | REF | 12 | C | SHE | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 3051S |  | TI702-SP-5141 |  |  | 01
TD02 | TD02-PSH-018A | TD02-P-018A | [6 empty] | PKG: L13306; -: -50Pa falling; -: +/-5 Pa; REF: REF; REQ: 12
TD02 | TD02-PDI-019 | TD02-P-019 | LCP | 107-DV | DIFFERENTIAL PRESSURE GAUGE | GLOVEBOX PANEL | 168.0 | CHAMBER | REF: REF; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
TD02 | TD02-PDI-020 | TD02-P-020 | LCP | 107-DV | DIFFERENTIAL PRESSURE GAUGE | GLOVEBOX PANEL | 168.0 | AIRLOCK | REF: REF; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
TD02 | TD02-PDI-021 | TD02-P-021 | LCP | 107-DV | DIFFERENTIAL PRESSURE GAUGE | GLOVEBOX PANEL | 168.0 | INLET | REF: REF; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
TD02 | TD02-PDI-022 | TD02-P-022 | LCP | 107-DV | DIFFERENTIAL PRESSURE GAUGE | GLOVEBOX PANEL | 168.0 | OUTLET | REF: REF; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
TD02 | TD02-PSV-023 | TD02-P-023 | PKG | 107-DV | PRESSURE RELIEF VALVE | TRAY DRYER | 168.0 |  | -: set @-50 mbarg; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-PSV-030 | TD02-P-030 | PKG | 107-HH | PRESSURE RELIEF VALVE |  | 168.0 | HEAT/COOL PACKAGE | -: set @ 4 barg; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-PSH-031 | TD02-P-031 | PKG | 107-HH | SWITCH - PRESSURE - HIGH |  | 168.0 | HEAT/COOL PACKAGE | -: set @???; REF: REF; REQ: REQ; F: C; Ref: Ops | [10 empty] | 01
TD02 | TD02-PI-032 | TD02-P-032 | PKG | 107-HH | PRESSURE GAUGE |  | 168.0 | HEAT/COOL PACKAGE | REF: REF; REQ: REQ; F: C; Ref: Ref | [10 empty] | 01
TD02 | TD02-RO-001 | TD02-R-001 | FLD | 107-DV | RESTRICTION ORIFICE PLATE | 25-P-PT1A-0-9023782 | 168.0 | TP1 TRANSFER PUMP | -: 5mm; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-RO-002 | TD02-R-002 | FLD | 107-DV | RESTRICTION ORIFICE PLATE | 25-N-SSIU-0-9028899 | 168.0 | GLOVE BOX NITROGEN | -: 5.78mm; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
| TD02-RO-003 | TD02-R-003 | FLD | 107-DV | RESTRICTION ORIFICE PLATE | 25-N-SSIU-0-9028890 | 168.0 | N2 SWEEP RESTRICTION ORIFICE | -: 7mm; REF: N/A; REQ: -; F: -; Ref: -
TD02 | TD02-TE-002 | TD02-T-002 | PKG | 107-DV | ELEMENT - TEMPERATURE - RTD | 40-HWF-CS1A-H-9028945 | 168.0 | HOT WATER SUPPLY TEMP. | REF: SHE; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-TI-002A | TD02-T-002 | PCS | 107-DV | INDICATOR - TEMPERATURE |  |  | HOT WATER SUPPLY TEMP. | REF: SHE; REQ: By request; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-TT-002 | TD02-T-002 | PKG | 107-DV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 168.0 | HOT WATER SUPPLY TEMP. |  |  |  | SHE | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004 | TI702-SP-5012 |  |  | 01
TD02 | TD02-TI-003 | TD02-T-003 | LCP | 107-DV | INDICATOR - TEMPERATURE | TD02 LOCAL PANEL | 168.0 | HOT WATER SUPPLY TEMP. |  | 0 to 100 degC | +/- 5% | REF | REQ | C | Ref | [12 empty] | 01
TD02 | TD02-TE-004 | TD02-T-004 | FLD | 107-DV | ELEMENT - TEMPERATURE - RTD | 40-P-PT1A-0-9023065 | 168.0 | VC1 VENT TEMPERATURE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-TI-004 | TD02-T-004 | PCS | 107-DV | INDICATOR - TEMPERATURE |  |  | VC1 VENT TEMPERATURE | REF: N/A; REQ: By request; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-TT-004 | TD02-T-004 | FLD | 107-DV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 168.0 | VC1 VENT TEMPERATURE |  |  |  | REF | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P2 | TI702-SP-5012 |  |  | 01
TD02 | TD02-TE-005 | TD02-T-005 | FLD | 107-DV | ELEMENT - TEMPERATURE - RTD | 25-HT-CS3A-C-9023078 | 168.0 | VC1 HTF RTN TEMPERATURE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-TI-005 | TD02-T-005 | PCS | 107-DV | INDICATOR - TEMPERATURE |  |  | VC1 HTF RTN TEMPERATURE | REF: N/A; REQ: By request; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-TT-005 | TD02-T-005 | FLD | 107-DV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 168.0 | VC1 HTF RTN TEMPERATURE |  |  |  | REF | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P2 | TI702-SP-5012 |  |  | 01
TD02 | TD02-TI-006 | TD02-T-006 | FLD | 107-DV | INDICATOR - TEMPERATURE | 40-HWR-CS1B-H-9021966 | 168.0 | HOT WATER RTN TEMPERATURE |  | 0 to 100 degC | +/- 5% | REF | REQ | C | Ref | [6 empty] | WIKA | S5550/4 | KT0003/P1 |  |  |  | 01
TD02 | TD02-TC-011 | TD02-T-011 | PCS | 107-HH | REMOTE SETPOINT - TEMPERATURE |  |  | HEAT/COOL PACKAGE | 13302 | 0 to 100 C |  | N/A | - | - | - | N.I.S | AO | 1 |  | 22 | FG1 | [6 empty] | 01
TD02 | TD02-TIC-011 | TD02-T-011 | PKG | 107-HH | INDICATING CONTROLLER - TEMPERATURE |  | 168.0 | HEAT/COOL PACKAGE |  | 0 to 100 C | +/-2degC | GxP | 12 | C | Ops | N.I.S | AI | 1 |  | 13 | FG1 | [6 empty] | 01
TD02 | TD02-TSH-012 | TD02-T-012 | PKG | 107-HH | SWITCH - TEMPERATURE - HI |  | 168.0 | HEAT/COOL PACKAGE | REF: REF; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
TD02 | TD02-TI-013 | TD02-T-013 | PCS | 107-HH | INDICATOR - TEMPERATURE |  |  | HEAT/COOL PACKAGE | -: 0 to 100 C; REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-TT-013 | TD02-T-013 | PKG | 107-HH | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 168.0 | HEAT/COOL PACKAGE |  |  |  | REF | By request | C | Ops | N.I.S | AI | 1 |  | 13 | FG1 | [6 empty] | 01
TD02 | TD02-TSL-014 | TD02-T-014 | PKG | 107-HH | SWITCH - TEMPERATURE - LOW |  | 168.0 | HEAT/COOL PACKAGE | REF: REF; REQ: By request; F: C; Ref: Ops | [10 empty] | 01
TD02 | TD02-TE-015 | TD02-T-015 | FLD | 107-DV | ELEMENT - TEMPERATURE - RTD | 50-P-PT1A-H-9023062 | 168.0 | VC1 INLET TEMPERATURE | REF: REF; REQ: By request; F: C; Ref: SHE |  |  |  | FG1 | [6 empty] | 01
TD02 | TD02-TI-015 | TD02-T-015 | PCS | 107-DV | INDICATOR - TEMPERATURE |  |  | VC1 INLET TEMPERATURE | REF: N/A; REQ: -; F: -; Ref: - |  |  |  | FG1 | [6 empty] | 01
TD02 | TD02-TSH-015 | TD02-T-015 | CPR | 107-DV | SWITCH - TEMPERATURE - HI | SAFETY PANEL | 168.0 | TEMPERATURE HIGH | REF: REF; REQ: 12; F: C; Ref: GMP | [10 empty] | 01
TD02 | TD02-TT-015 | TD02-T-015 | FLD | 107-DV | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 168.0 | VC1 INLET TEMPERATURE |  |  |  | REF | By request | C | Ops | I.S | AI | 1 |  | 11 | FG1 | ROSEMOUNT | 644H | KT0004/P2 | TI702-SP-5140 |  |  | 01
TD02 | TD02-XS-001 | TD02-X-001 | PKG | 107-DV | SOLENOID VALVE | TRAY DRYER | 168.0 |  | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-YI-001 | TD02-Y-001 | LCP | 107-DV | INDICATOR - LAMP | GLOVEBOX PANEL | 168.0 | SAFE TO OPEN | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-YI-002 | TD02-Y-002 | LCP | 107-DV | INDICATOR - LAMP | GLOVEBOX PANEL | 168.0 | NOT SAFE TO OPEN | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-YS-003 | TD02-Y-003 | PKG | 107-DV | GLOVEBOX PRESS CONTROL REQ | GLOVEBOX | 168.0 | GLOVEBOX PRESS CONTROL REQ | 13307 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 01
TD02 | TD02-YA-021 | TD02-Y-021 | PCS | 107-HH | ALARM - FAULT |  | 168.0 | HEAT/COOL PACKAGE | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01
TD02 | TD02-YS-021 | TD02-Y-021 | PKG | 107-HH | SWITCH - FAULT |  | 168.0 | HEAT/COOL PACKAGE | 13304 |  |  | N/A | - | - | - | N.I.S | DI | 1 |  | 35 | FG1 | [6 empty] | 01
TD02 | TD02-YS-022 | TD02-Y-022 | CPR | 107-HH | SWITCH - CRASH COOL |  | 168.0 | HEAT/COOL PACKAGE | REF: SHE; REQ: 12; F: F; Ref: GMP | [10 empty] | 01
TD02 | TD02-ZS-001 | TD02-Z-001 | PKG | 107-DV | SWITCH - DOOR OPEN | GLOVEBOX DOOR | 168.0 |  | REF: SHE; REQ: -; F: -; Ref: - | [10 empty] | 01
TEST | TEST-FI-001 | TEST-F-001 |  | N/A | VA FLOW METER | LOCAL TO EQUIP. |  | ENVIROMENTAL TESTING | -: 5 to 150 Nl/min |  |  | 0 |  | KROHNE | VA20/K |  |  | SCRUBBER TESTING |  | 01
TP01 | TP01-CV-001 | TP01-C-001 | FLD | 107-BS | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-O-9021848 | 068.0 | GP1 FLOW METER SUPPLY | 7168 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TP01 | TP01-CY-001 | TP01-C-001 | FLD | 107-BS | SOLENOID VALVE | RACK MOUNTED |  | GP1 FLOW METER SUPPLY | I.S: I.S; DI: DO |  |  | 41 | GP1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TP01 | TP01-ZSC-001 | TP01-C-001 | FLD | 107-BS | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP1 FLOW METER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TP01 | TP01-ZSO-001 | TP01-C-001 | FLD | 107-BS | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP1 FLOW METER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TP01 | TP01-DIC-001 | TP01-D-001 | PCS | 107-BS | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP01 | TP01-DS-001 | TP01-D-001 | MCC | 107-BS | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
TP01 | TP01-DY-001 | TP01-D-001 | MCC | 107-BS | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
TP01 | TP01-DYC-001 | TP01-D-001 | MCC | 107-BS | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 068.0 | TRANSFER PUMP | 8950 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
TP01 | TP01-FIT-001 | TP01-F-001 | FLD | 107-BS | TRANSMITTER - FLOW | 25-SO-PT1A-0-9021848 | 068.0 | GP1 FLOW METER | 6451 | 0 - 4 m3/hr | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | GP1 | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
TP01 | TP01-FQI-001 | TP01-F-001 | PCS | 107-BS | INDICATOR - FLOW/TOTALISER |  |  | GP1 FLOW METER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP01 | TP01-PI-001 | TP01-P-001 | FLD | 107-BS | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-0-9021850 | 068.0 | PUMP DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TP01 | TP01-PI-002 | TP01-P-002 | FLD | 107-BS | PRESSURE GAUGE - DIAPHRAGM | 40-SV-PT1A-0-9021816 | 008.2 | SCRUBBER SUCTION PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
TP01 | TP01-LI-001 | TP01-Y-002 | PKG | 107-BS | INDICATOR - LEVEL GAUGE | TP01 SEAL POT | 068.0 | SEAL POT FAILURE | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TP01 | TP01-LSH-002 | TP01-Y-002 | PKG | 107-BS | SWITCH - LEVEL - HIGH | TP01 SEAL POT | 068.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP01 | TP01-LSL-003 | TP01-Y-002 | PKG | 107-BS | SWITCH - LEVEL - LOW | TP01 SEAL POT | 068.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP01 | TP01-PI-003 | TP01-Y-002 | PKG | 107-BS | PRESSURE GAUGE | TP01 SEAL POT | 068.0 | SEAL POT FAILURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP01 | TP01-PSL-004 | TP01-Y-002 | PKG | 107-BS | SWITCH - PRESSURE - LOW | TP01 SEAL POT | 068.0 | SEAL POT FAILURE |  | set @ 4 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | [7 empty] | 01
TP01 | TP01-TI-001 | TP01-Y-002 | PKG | 107-BS | INDICATOR - TEMPERATURE | TP01 SEAL POT | 068.0 | SEAL POT FAILURE | -: 0 to 120 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP01 | TP01-YA-002 | TP01-Y-002 | PCS | 107-BS | ALARM - COMMON |  |  | SEAL POT FAILURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP01 | TP01-YS-002 | TP01-Y-002 | PKG | 107-BS | SWITCH - COMMON ALARM | TP01 SEAL POT | 068.0 | SEAL POT FAILURE | 8951 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | GP1 | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
TP02 | TP02-DIC-001 | TP02-D-001 | PCS | 107-BT | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP02 | TP02-DS-001 | TP02-D-001 | MCC | 107-BT | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
TP02 | TP02-DY-001 | TP02-D-001 | MCC | 107-BT | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP1 | [6 empty] | 01
TP02 | TP02-DYC-001 | TP02-D-001 | MCC | 107-BT | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 069.0 | TRANSFER PUMP | 8952 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP1 | [6 empty] | 01
TP02 | TP02-PI-001 | TP02-P-001 | FLD | 107-BT | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-0-9021890 | 069.0 | PUMP DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TP02 | TP02-PI-002 | TP02-P-002 | FLD | 107-BT | PRESSURE GAUGE - DIAPHRAGM | 40-SV-GR1C-0-9021886 | 008.2 | SCRUBBER SUCTION PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
TP02 | TP02-LI-001 | TP02-Y-002 | PKG | 107-BT | INDICATOR - LEVEL GAUGE | TP02 SEAL POT | 069.0 | SEAL POT FAILURE | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TP02 | TP02-LSH-002 | TP02-Y-002 | PKG | 107-BT | SWITCH - LEVEL - HIGH | TP02 SEAL POT | 069.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP02 | TP02-LSL-003 | TP02-Y-002 | PKG | 107-BT | SWITCH - LEVEL - LOW | TP02 SEAL POT | 069.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP02 | TP02-PI-003 | TP02-Y-002 | PKG | 107-BT | PRESSURE GAUGE | TP02 SEAL POT | 069.0 | SEAL POT FAILURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP02 | TP02-PSL-004 | TP02-Y-002 | PKG | 107-BT | SWITCH - PRESSURE - LOW | TP02 SEAL POT | 069.0 | SEAL POT FAILURE |  | set @ 4 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | [7 empty] | 01
TP02 | TP02-TI-001 | TP02-Y-002 | PKG | 107-BT | INDICATOR - TEMPERATURE | TP02 SEAL POT | 069.0 | SEAL POT FAILURE | -: 0 to 120 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP02 | TP02-YA-002 | TP02-Y-002 | PCS | 107-BT | ALARM - COMMON |  |  | SEAL POT FAILURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP02 | TP02-YS-002 | TP02-Y-002 | PKG | 107-BT | SWITCH - COMMON ALARM | TP02 SEAL POT | 069.0 | SEAL POT FAILURE | 8953 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | GP1 | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
TP03 | TP03-CV-001 | TP03-C-001 | FLD | 107-CS | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-9022848 | 070.0 | GP2 FLOW METER SUPPLY | 7174 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TP03 | TP03-CY-001 | TP03-C-001 | FLD | 107-CS | SOLENOID VALVE | RACK MOUNTED |  | GP2 FLOW METER SUPPLY | I.S: I.S; DI: DO |  |  | 41 | GP2 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TP03 | TP03-ZSC-001 | TP03-C-001 | FLD | 107-CS | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP2 FLOW METER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TP03 | TP03-ZSO-001 | TP03-C-001 | FLD | 107-CS | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP2 FLOW METER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | GP2 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TP03 | TP03-DIC-001 | TP03-D-001 | PCS | 107-CS | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP03 | TP03-DS-001 | TP03-D-001 | MCC | 107-CS | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
TP03 | TP03-DY-001 | TP03-D-001 | MCC | 107-CS | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
TP03 | TP03-DYC-001 | TP03-D-001 | MCC | 107-CS | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 070.0 | TRANSFER PUMP | 8954 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
TP03 | TP03-FIT-001 | TP03-F-001 | FLD | 107-CS | TRANSMITTER - FLOW | 25-SO-PT1A-0-9022848 | 070.0 | GP2 FLOW METER | 6452 | 0 - 4 m3/hr | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | GP2 | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
TP03 | TP03-FQI-001 | TP03-F-001 | PCS | 107-CS | INDICATOR - FLOW/TOTALISER |  |  | GP2 FLOW METER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP03 | TP03-PI-001 | TP03-P-001 | FLD | 107-CS | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-0-9022850 | 070.0 | PUMP DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TP03 | TP03-PI-002 | TP03-P-002 | FLD | 107-CS | PRESSURE GAUGE - DIAPHRAGM | 40-SV-PT1A-0-9022816 | 008.2 | SCRUBBER SUCTION PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
TP03 | TP03-LI-001 | TP03-Y-002 | PKG | 107-CS | INDICATOR - LEVEL GAUGE | TP03 SEAL POT | 070.0 | SEAL POT FAILURE | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TP03 | TP03-LSH-002 | TP03-Y-002 | PKG | 107-CS | SWITCH - LEVEL - HIGH | TP03 SEAL POT | 070.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP03 | TP03-LSL-003 | TP03-Y-002 | PKG | 107-CS | SWITCH - LEVEL - LOW | TP03 SEAL POT | 070.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP03 | TP03-PI-003 | TP03-Y-002 | PKG | 107-CS | PRESSURE GAUGE | TP03 SEAL POT | 070.0 | SEAL POT FAILURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP03 | TP03-PSL-004 | TP03-Y-002 | PKG | 107-CS | SWITCH - PRESSURE - LOW | TP03 SEAL POT | 070.0 | SEAL POT FAILURE |  | set @ 4 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | [7 empty] | 01
TP03 | TP03-TI-001 | TP03-Y-002 | PKG | 107-CS | INDICATOR - TEMPERATURE | TP03 SEAL POT | 070.0 | SEAL POT FAILURE | -: 0 to 120 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP03 | TP03-YA-002 | TP03-Y-002 | PCS | 107-CS | ALARM - COMMON |  |  | SEAL POT FAILURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP03 | TP03-YS-002 | TP03-Y-002 | PKG | 107-CS | SWITCH - COMMON ALARM | TP03 SEAL POT | 070.0 | SEAL POT FAILURE | 8955 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | GP2 | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
TP04 | TP04-DIC-001 | TP04-D-001 | PCS | 107-CT | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP04 | TP04-DS-001 | TP04-D-001 | MCC | 107-CT | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
TP04 | TP04-DY-001 | TP04-D-001 | MCC | 107-CT | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | GP2 | [6 empty] | 01
TP04 | TP04-DYC-001 | TP04-D-001 | MCC | 107-CT | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 071.0 | TRANSFER PUMP | 8956 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | GP2 | [6 empty] | 01
TP04 | TP04-PI-001 | TP04-P-001 | FLD | 107-CT | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-0-9022890 | 071.0 | PUMP DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TP04 | TP04-PI-002 | TP04-P-002 | FLD | 107-CT | PRESSURE GAUGE - DIAPHRAGM | 40-SV-PT1A-0-9022862 | 008.2 | SCRUBBER SUCTION PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
TP04 | TP04-LI-001 | TP04-Y-002 | PKG | 107-CT | INDICATOR - LEVEL GAUGE | TP04 SEAL POT | 071.0 | SEAL POT FAILURE | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TP04 | TP04-LSH-002 | TP04-Y-002 | PKG | 107-CT | SWITCH - LEVEL - HIGH | TP04 SEAL POT | 071.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP04 | TP04-LSL-003 | TP04-Y-002 | PKG | 107-CT | SWITCH - LEVEL - LOW | TP04 SEAL POT | 071.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP04 | TP04-PI-003 | TP04-Y-002 | PKG | 107-CT | PRESSURE GAUGE | TP04 SEAL POT | 071.0 | SEAL POT FAILURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP04 | TP04-PSL-004 | TP04-Y-002 | PKG | 107-CT | SWITCH - PRESSURE - LOW | TP04 SEAL POT | 071.0 | SEAL POT FAILURE |  | set @ 4 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | [7 empty] | 01
TP04 | TP04-TI-001 | TP04-Y-002 | PKG | 107-CT | INDICATOR - TEMPERATURE | TP04 SEAL POT | 071.0 | SEAL POT FAILURE | -: 0 to 120 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP04 | TP04-YA-002 | TP04-Y-002 | PCS | 107-CT | ALARM - COMMON |  |  | SEAL POT FAILURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP04 | TP04-YS-002 | TP04-Y-002 | PKG | 107-CT | SWITCH - COMMON ALARM | TP04 SEAL POT | 071.0 | SEAL POT FAILURE | 8957 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | GP2 | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
TP05 | TP05-CV-001 | TP05-C-001 | FLD | 107-DT | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-9023888 | 078.0 | FG1 FLOW METER SUPPLY | 7175 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TP05 | TP05-CY-001 | TP05-C-001 | FLD | 107-DT | SOLENOID VALVE | RACK MOUNTED |  | FG1 FLOW METER SUPPLY | I.S: I.S; DI: DO |  |  | 41 | FG1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TP05 | TP05-ZSC-001 | TP05-C-001 | FLD | 107-DT | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | FG1 FLOW METER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TP05 | TP05-ZSO-001 | TP05-C-001 | FLD | 107-DT | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | FG1 FLOW METER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | FG1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TP05 | TP05-DIC-001 | TP05-D-001 | PCS | 107-DT | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP05 | TP05-DS-001 | TP05-D-001 | MCC | 107-DT | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
TP05 | TP05-DY-001 | TP05-D-001 | MCC | 107-DT | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
TP05 | TP05-DYC-001 | TP05-D-001 | MCC | 107-DT | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 078.0 | TRANSFER PUMP | 8958 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
TP05 | TP05-FIT-001 | TP05-F-001 | FLD | 107-DT | TRANSMITTER - FLOW | 25-SO-PT1A-0-90223888 | 078.0 | FG1 FLOW METER | 6453 | 0 - 4 m3/hr | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | FG1 | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
TP05 | TP05-FQI-001 | TP05-F-001 | PCS | 107-DT | INDICATOR - FLOW/TOTALISER |  |  | FG1 FLOW METER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP05 | TP05-PI-001 | TP05-P-001 | FLD | 107-DT | PRESSURE GAUGE - DIAPHRAGM | 40-PO-PT1A-0-9023890 | 078.0 | PUMP DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TP05 | TP05-PI-002 | TP05-P-002 | FLD | 107-DT | PRESSURE GAUGE - DIAPHRAGM | 40-SV-PT1A-0-9023886 | 008.2 | SCRUBBER SUCTION PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
TP05 | TP05-LI-001 | TP05-Y-002 | PKG | 107-DT | INDICATOR - LEVEL GAUGE | TP05 SEAL POT | 078.0 | SEAL POT FAILURE | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TP05 | TP05-LSH-002 | TP05-Y-002 | PKG | 107-DT | SWITCH - LEVEL - HIGH | TP05 SEAL POT | 078.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP05 | TP05-LSL-003 | TP05-Y-002 | PKG | 107-DT | SWITCH - LEVEL - LOW | TP05 SEAL POT | 078.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP05 | TP05-PI-003 | TP05-Y-002 | PKG | 107-DT | PRESSURE GAUGE | TP05 SEAL POT | 078.0 | SEAL POT FAILURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP05 | TP05-PSL-004 | TP05-Y-002 | PKG | 107-DT | SWITCH - PRESSURE - LOW | TP05 SEAL POT | 078.0 | SEAL POT FAILURE |  | set @ 4 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | [7 empty] | 01
TP05 | TP05-TI-001 | TP05-Y-002 | PKG | 107-DT | INDICATOR - TEMPERATURE | TP05 SEAL POT | 078.0 | SEAL POT FAILURE | -: 0 to 120 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP05 | TP05-YA-002 | TP05-Y-002 | PCS | 107-DT | ALARM - COMMON |  |  | SEAL POT FAILURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP05 | TP05-YS-002 | TP05-Y-002 | PKG | 107-DT | SWITCH - COMMON ALARM | TP05 SEAL POT | 078.0 | SEAL POT FAILURE | 8959 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | FG1 | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
TP06 | TP06-CV-001 | TP06-C-001 | FLD | 107-ET | BALL VALVE - ON/OFF - F.C. | 25-SO-PT1A-0-9024888 | 077.0 | C1 FLOW METER SUPPLY | 7176 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TP06 | TP06-CY-001 | TP06-C-001 | FLD | 107-ET | SOLENOID VALVE | RACK MOUNTED |  | C1 FLOW METER SUPPLY | I.S: I.S; DI: DO |  |  | 41 | C1 | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
TP06 | TP06-ZSC-001 | TP06-C-001 | FLD | 107-ET | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | C1 FLOW METER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TP06 | TP06-ZSO-001 | TP06-C-001 | FLD | 107-ET | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | C1 FLOW METER SUPPLY | I.S: I.S; DI: DI |  |  | 31 | C1 | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
TP06 | TP06-DIC-001 | TP06-D-001 | PCS | 107-ES | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP06 | TP06-DS-001 | TP06-D-001 | MCC | 107-ES | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
TP06 | TP06-DY-001 | TP06-D-001 | MCC | 107-ES | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | C1 | [6 empty] | 01
TP06 | TP06-DYC-001 | TP06-D-001 | MCC | 107-ES | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 077.0 | TRANSFER PUMP | 8960 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | C1 | [6 empty] | 01
TP06 | TP06-FIT-001 | TP06-F-001 | FLD | 107-ET | TRANSMITTER - FLOW | 25-SO-PT1A-0-904888 | 077.0 | C1 FLOW METER | 6454 | 0 - 4 m3/hr | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | C1 | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
TP06 | TP06-FQI-001 | TP06-F-001 | PCS | 107-ET | INDICATOR - FLOW/TOTALISER |  |  | C1 FLOW METER | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP06 | TP06-FQIC-001 | TP06-F-001 | FLD | 107-ES | MOBILE WASTE SOLVENT BATCH METER | C1-TS2 | 077.2 | WASTE SOLVENT TO ST1/2 |  | 45 to 450 L/min | +/- 5% | REF | REQ | C |  | I.S | [5 empty] | APOLLO | RM3SP | KF0018/P1 |  |  |  | 01
TP06 | TP06-PI-001 | TP06-P-001 | FLD | 107-ES | PRESSURE GAUGE - DIAPHRAGM | 40-P-PT1A-0-9024850 | 077.0 | PUMP DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TP06 | TP06-PI-002 | TP06-P-002 | FLD | 107-ES | PRESSURE GAUGE - DIAPHRAGM | 40-SV-PT1A-0-9024816 | 008.3 | SCRUBBER SUCTION PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
TP06 | TP06-LI-001 | TP06-Y-002 | PKG | 107-ES | INDICATOR - LEVEL GAUGE | TP06 SEAL POT | 077.0 | SEAL POT FAILURE | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TP06 | TP06-LSH-002 | TP06-Y-002 | PKG | 107-ES | SWITCH - LEVEL - HIGH | TP06 SEAL POT | 077.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP06 | TP06-LSL-003 | TP06-Y-002 | PKG | 107-ES | SWITCH - LEVEL - LOW | TP06 SEAL POT | 077.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP06 | TP06-PI-003 | TP06-Y-002 | PKG | 107-ES | PRESSURE GAUGE | TP06 SEAL POT | 077.0 | SEAL POT FAILURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP06 | TP06-PSL-004 | TP06-Y-002 | PKG | 107-ES | SWITCH - PRESSURE - LOW | TP06 SEAL POT | 077.0 | SEAL POT FAILURE |  | set @ 4 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | [7 empty] | 01
TP06 | TP06-TI-001 | TP06-Y-002 | PKG | 107-ES | INDICATOR - TEMPERATURE | TP06 SEAL POT | 077.0 | SEAL POT FAILURE | -: 0 120 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP06 | TP06-YA-002 | TP06-Y-002 | PCS | 107-ES | ALARM - COMMON |  |  | SEAL POT FAILURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP06 | TP06-YS-002 | TP06-Y-002 | PKG | 107-ES | SWITCH - COMMON ALARM | TP06 SEAL POT | 077.0 | SEAL POT FAILURE | 8961 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | C1 | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
TP07 | TP07-DIC-001 | TP07-D-001 | PCS | 107-PF | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP07 | TP07-DS-001 | TP07-D-001 | MCC | 107-PF | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
TP07 | TP07-DY-001 | TP07-D-001 | MCC | 107-PF | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
TP07 | TP07-DYC-001 | TP07-D-001 | MCC | 107-PF | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 081.0 | TRANSFER PUMP | 8962 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
TP07 | TP07-FIT-001 | TP07-F-001 | FLD | 107-PF | TRANSMITTER - FLOW | 25-SO-SS1C-0-9027865 | 081.0 | LIBC OUTLET FLOW | 6456 | 0 - 8 m3/hr | +/- 0.25% | REF | 5 YR | C |  | N.I.S | DI |  |  | 36 | UTIL | ENDRESS + HAUSER | NOTE 1 | KF0002 |  | 0 to 400 hz |  | 01
TP07 | TP07-FQIC-001 | TP07-F-001 | PCS | 107-PF | INDICATING CONTROLLER - FLOW |  |  | LIBC OUTLET FLOW | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP07 | TP07-PI-001 | TP07-P-001 | FLD | 107-PF | PRESSURE GAUGE - DIAPHRAGM | 25-SD-SS1C-0-9027865 | 081.0 | PUMP DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 1%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TP07 | TP07-PSV-002 | TP07-P-002 | FLD | 107-PF | PRESSURE RELIEF VALVE | 25-N-SS1U-0-9028638 | 043.4 | LIBC N2 RELIEF | -: 10 mbarg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  |  |  | KS0004 |  |  |  | 01
TP07 | TP07-PRV-003 | TP07-P-003 | FLD | 107-PF | CONTROL VALVE SELF ACTUATING | 25-N-SS1U-0-9028638 | 043.4 | N2 SUPPLY TO LIBC | -: set @ 5mbarg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | ESME | R1440/75 | KS0007 |  |  |  | 01
TP07 | TP07-PI-006 | TP07-P-006 | FLD | 107-PF | PRESSURE GAUGE | 25-N-SS1U-0-9028638 | 043.4 | N2 SUPPLY TO LIBC | -: 0 to 25 mbarg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 632.50.100 (Note 1) | KP0006/P |  |  |  | 01
TP07 | TP07-LI-001 | TP07-Y-001 | PKG | 107-PF | INDICATOR - LEVEL GAUGE | TP07 SEAL POT | 081.0 | SEAL POT FAILURE | -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
TP07 | TP07-LSH-003 | TP07-Y-001 | PKG | 107-PF | SWITCH - LEVEL - HIGH | TP07 SEAL POT | 081.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP07 | TP07-LSL-002 | TP07-Y-001 | PKG | 107-PF | SWITCH - LEVEL - LOW | TP07 SEAL POT | 081.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | [7 empty] | 01
TP07 | TP07-PI-004 | TP07-Y-001 | PKG | 107-PF | PRESSURE GAUGE | TP07 SEAL POT | 081.0 | SEAL POT FAILURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP07 | TP07-PSL-005 | TP07-Y-001 | PKG | 107-PF | SWITCH - PRESSURE - LOW | TP07 SEAL POT | 081.0 | SEAL POT FAILURE |  | set @ 4 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | [7 empty] | 01
TP07 | TP07-TI-001 | TP07-Y-001 | PKG | 107-PF | INDICATOR - TEMPERATURE | TP07 SEAL POT | 081.0 | SEAL POT FAILURE | -: 0 to120 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | [7 empty] | 01
TP07 | TP07-YA-001 | TP07-Y-001 | PCS | 107-PF | ALARM - COMMON |  |  | SEAL POT FAILURE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TP07 | TP07-YS-001 | TP07-Y-001 | PKG | 107-PF | SWITCH - COMMON ALARM | TP07 SEAL POT | 081.0 | SEAL POT FAILURE | 8963 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
TP08 | TP08-DIC-001 | TP08-D-001 | PCS | 107-DS | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | FG1 | [6 empty] | 01 | bar: PKG
TP08 | TP08-DS-001 | TP08-D-001 | MCC | 107-DS | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
TP08 | TP08-DY-001 | TP08-D-001 | MCC | 107-DS | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | FG1 | [6 empty] | 01
TP08 | TP08-DYC-001 | TP08-D-001 | MCC | 107-DS | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 076.0 | TRANSFER PUMP | 8964 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | FG1 | [6 empty] | 01
TP08 | TP08-PI-001 | TP08-P-001 | FLD | 107-DS | PRESSURE GAUGE | 40-P-PT1A-0-9023850 | 076.0 | PUMP DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | FG1 | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TP08 | TP08-PI-002 | TP08-P-002 | FLD | 107-DS | PRESSURE GAUGE | 40-SV-PT1A-0-9023848 | 008.2 | SCRUBBER SUCTION PRESSURE | -: -1 to 1.5 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | FG1 | WIKA | 232.50.100/990.27 | KP0006/1 |  |  |  | 01
TP08 | TP08-LI-001 | TP08-Y-002 | PKG | 107-DS | INDICATOR - LEVEL | TP08 SEAL POT | 076.0 | SEAL POT FAILURE | -: Fixed; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | FG1 | [6 empty] | 01
TP08 | TP08-LSH-002 | TP08-Y-002 | PKG | 107-DS | SWITCH - LEVEL - HIGH | TP08 SEAL POT | 076.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | FG1 | [6 empty] | 01
TP08 | TP08-LSL-003 | TP08-Y-002 | PKG | 107-DS | SWITCH - LEVEL - LOW | TP08 SEAL POT | 076.0 | SEAL POT FAILURE |  | Fixed | - | REF | REQ | F |  | I.S |  |  |  | 0 | FG1 | [6 empty] | 01
TP08 | TP08-PI-003 | TP08-Y-002 | PKG | 107-DS | PRESSURE GAUGE | TP08 SEAL POT | 076.0 | SEAL POT FAILURE | -: 0 to 10 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | FG1 | [6 empty] | 01
TP08 | TP08-PSL-004 | TP08-Y-002 | PKG | 107-DS | SWITCH - PRESSURE - LOW | TP08 SEAL POT | 076.0 | SEAL POT FAILURE |  | set @ 4 barg | +/- 5% | REF | REQ | C |  | I.S |  |  |  | 0 | FG1 | [6 empty] | 01
TP08 | TP08-TI-001 | TP08-Y-002 | PKG | 107-DS | INDICATOR - TEMPERATURE | TP08 SEAL POT | 076.0 | SEAL POT FAILURE | -: 0 to 120 degC; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 | FG1 | [6 empty] | 01
TP08 | TP08-YA-002 | TP08-Y-002 | PCS | 107-DS | ALARM - COMMON |  |  | SEAL POT FAILURE | [11 empty] | 0 | FG1 | [6 empty] | 01 | bar: PKG
TP08 | TP08-YS-002 | TP08-Y-002 | PKG | 107-DS | SWITCH - COMMON ALARM | TP08 SEAL POT | 076.0 | SEAL POT FAILURE | 8965 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | FG1 | TAV ENGINEERING LTD / DELTA CONTROLS LTD | F71 / HS210GEA02H |  | TI702-SP-5153 |  |  | 01
TT01 | TT01-AI-001 | TT01-A-001 | PCS | 107-LD | INDICATOR - ANALYSIS - PH |  |  | pH ANALYSIS | REQ: By request |  |  | 0 | [7 empty] | 01
TT01 | TT01-AT-001 | TT01-A-001 | FLD | 107-LD | TRANSMITTER - ANALYSIS - PH | 50-P-PT1A-W-9027103 | 011.1 | pH ANALYSIS | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | YOKOGAWA | NOTE 4 / PH202S | KA0019 | TI702-SP-5044 |  |  | 01
TT01 | TT01-CV-001 | TT01-C-001 | FLD | 107-LD | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-W-9027112 | 011.1 | EFFLUENT INLET | 7310 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TT01 | TT01-CY-001 | TT01-C-001 | FLD | 107-LD | SOLENOID VALVE | RACK MOUNTED |  | EFFLUENT INLET | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
TT01 | TT01-ZSC-001 | TT01-C-001 | FLD | 107-LD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | EFFLUENT INLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
TT01 | TT01-ZSO-001 | TT01-C-001 | FLD | 107-LD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | EFFLUENT INLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
TT01 | TT01-CV-002 | TT01-C-002 | FLD | 107-LD | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-W-9027103 | 011.1 | RE-CIRC. TT01 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | NAEGELEN | R202 |  |  | OPERATED BY TT01-HS-002 |  | 01
TT01 | TT01-DIC-001 | TT01-D-001 | PCS | 107-LD | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TT01 | TT01-DS-001 | TT01-D-001 | MCC | 107-LD | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
TT01 | TT01-DY-001 | TT01-D-001 | MCC | 107-LD | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
TT01 | TT01-DYC-001 | TT01-D-001 | MCC | 107-LD | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 011.1 | TRANSFER PUMP | 8966 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
TT01 | TT01-HS-001A | TT01-H-001 | FLD | 107-LD | START PUSHBUTTON | AD TO PUMP TT01-P1 | 011.1 | P1 PUMP CONTROL | 8967 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | COOPER MEDC | GHG 411 8295 R0001 |  | TI702-SP-5118 | BY TRADE CONTRACTOR |  | 01
TT01 | TT01-HS-001B | TT01-H-001 | FLD | 107-LD | STOP PUSHBUTTON (STAYPUT) | AD TO PUMP TT01-P1 | 011.1 | P1 PUMP CONTROL |  | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | COOPER MEDC | GHG 411 8295 R0001 |  | TI702-SP-5118 | BY TRADE CONTRACTOR |  | 01
TT01 | TT01-HS-002 | TT01-H-002 | FLD | 107-LD | SWITCH - PUSHBUTTON | OUTSIDE BUND ADJ. VALVE | 011.1 | OPEN/CLOSE TT01-CV-002 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | PNEUMATIC |  | 01
TT01 | TT01-LI-001A | TT01-L-001 | PCS | 107-LD | INDICATOR - LEVEL |  |  | LEVEL | REQ: By request |  |  | 0 | [7 empty] | 01
TT01 | TT01-LI-001B | TT01-L-001 | FLD | 107-LD | INDICATOR - LEVEL | ADJ TANK TT01 | 011.1 | LEVEL | REQ: By request; F: C; I.S: I.S |  |  | 0 | UTIL | BEKA | BA324C-GRP | KX0017 | TI702-SP-5116 |  |  | 01
TT01 | TT01-LT-001 | TT01-L-001 | FLD | 107-LD | TRANSMITTER - LEVEL | TT01/N1/100 | 011.1 | LEVEL | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | VEGA | VEGAPULS 6X (PS6X.2SWGPFXAWKMAHACXXXXXX) |  |  |  |  | 01 | 20
TT01 | TT01-LAH-002 | TT01-L-002 | PCS | 107-LD | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L15859; -: On/off; -: On/off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
TT01 | TT01-LE-002 | TT01-L-002 | [6 empty] | PKG: L15859; -: On/off; -: On/off; REF: SHE; REQ: 24
TT01 | TT01-LSH-002 | TT01-L-002 | FLD | 107-LD | SWITCH - LEVEL - HIGH/LOW | TT01/N2/100 | 011.1 | HIGH LEVEL | -: -; F: F; I.S: I.S; DI: DI |  |  | 32 | UTIL | VEGA | SWING63.CAAIFXPZ |  |  |  |  | 01 | 20
TT01 | TT01-PI-001 | TT01-P-001 | FLD | 107-LD | PRESSURE GAUGE - DIAPHRAGM | 80-P-PT1A-W-9027102 | 011.1 | P1 DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TT01 | TT01-TE-001 | TT01-T-001 | FLD | 107-LD | ELEMENT - TEMPERATURE - RTD | SKIN - TT01 |  | TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
TT01 | TT01-TI-001A | TT01-T-001 | PCS | 107-LD | INDICATOR - TEMPERATURE |  |  | TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
TT01 | TT01-TI-001B | TT01-T-001 | FLD | 107-LD | INDICATOR - TEMPERATURE | ADJ TANK TT01 | 011.1 | TEMPERATURE | REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5120 |  |  | 01
TT01 | TT01-TT-001 | TT01-T-001 | FLD | 107-LD | TRANSMITTER - TEMPERATURE | ADJ TO TE | 011.1 | TEMPERATURE | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5120 |  |  | 01
TT02 | TT02-CV-001 | TT02-C-001 | FLD | 107-LD | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-W-9027060 | 011.1 | EFFLUENT INLET | 7311 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01
TT02 | TT02-CY-001 | TT02-C-001 | FLD | 107-LD | SOLENOID VALVE | RACK MOUNTED |  | EFFLUENT INLET | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5050 |  |  | 01
TT02 | TT02-ZSC-001 | TT02-C-001 | FLD | 107-LD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | EFFLUENT INLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
TT02 | TT02-ZSO-001 | TT02-C-001 | FLD | 107-LD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | EFFLUENT INLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5043 |  |  | 01
TT02 | TT02-CV-002 | TT02-C-002 | FLD | 107-LD | BALL VALVE - ON/OFF - F.C. | 50-P-PT1A-W-9027104 | 011.1 | RE-CIRC. TT02 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | NAEGELEN | R202 |  |  | OPERATED BY TT02-HS-002 |  | 01
TT02 | TT02-HS-002 | TT02-H-002 | FLD | 107-LD | SWITCH - PUSHBUTTON | OUTSIDE BUND ADJ. VALVE | 011.1 | OPEN/CLOSE TT02-CV-002 | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [5 empty] | PNEUMATIC |  | 01
TT02 | TT02-LI-001A | TT02-L-001 | PCS | 107-LD | INDICATOR - LEVEL |  |  | LEVEL | REQ: By request |  |  | 0 | [7 empty] | 01
TT02 | TT02-LI-001B | TT02-L-001 | FLD | 107-LD | INDICATOR - LEVEL | ADJ TANK TT02 | 011.1 | LEVEL | REF: REF; REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324G-GRP | KX0017 | TI702-SP-5117 |  |  | 01
TT02 | TT02-LT-001 | TT02-L-001 | FLD | 107-LD | TRANSMITTER - LEVEL | TT02 | 011.1 | LEVEL | REF: REF; REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | VEGA | VEGASON61 | KL0025 | TI702-SP-5117 |  |  | 01
TT02 | TT02-LAH-002 | TT02-L-002 | PCS | 107-LD | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L15860; -: On/off; -: On/off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
TT02 | TT02-LE-002 | TT02-L-002 | [6 empty] | PKG: L15860; -: On/off; -: On/off; REF: SHE; REQ: 24
TT02 | TT02-LSH-002 | TT02-L-002 | FLD | 107-LD | SWITCH - LEVEL - HIGH/LOW | TT02/N2/100 | 011.1 | HIGH LEVEL | F: F; I.S: I.S; DI: DI |  |  | 32 | UTIL | MEGGIT MOBERY | DS1FR4N1PH8/65 | KL0005 | TI702-SP-5113 |  |  | 01
TT02 | TT02-TE-001 | TT02-T-001 | FLD | 107-LD | ELEMENT - TEMPERATURE - RTD | SKIN TT02 |  | TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
TT02 | TT02-TI-001A | TT02-T-001 | PCS | 107-LD | INDICATOR - TEMPERATURE |  |  | TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
TT02 | TT02-TI-001B | TT02-T-001 | FLD | 107-LD | INDICATOR - TEMPERATURE | ADJ TANK TT02 | 011.1 | TEMPERATURE | REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324G-GRP | KX0017 | TI702-SP-5121 |  |  | 01
TT02 | TT02-TT-001 | TT02-T-001 | FLD | 107-LD | TRANSMITTER - TEMPERATURE | ADJ TO TE | 011.1 | TEMPERATURE | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5121 |  |  | 01
TT03 | TT03-AI-001 | TT03-A-001 | PCS | 107-LD | INDICATOR - ANALYSIS - PH |  |  | pH ANALYSIS | REQ: By request |  |  | 0 | [7 empty] | 01
TT03 | TT03-AT-001 | TT03-A-001 | FLD | 107-LD | TRANSMITTER - ANALYSIS - PH | 50-P-PT1A-W-9027107 | 012.0 | pH ANALYSIS | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | YOKOGAWA | NOTE 4 / PH202S | KA0019 | TI702-SP-5044 |  |  | 01
TT03 | TT03-DIC-001 | TT03-D-001 | PCS | 107-LD | INDICATING CONTR. - MOTOR DRIVE |  |  | TRANSFER PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
TT03 | TT03-DS-001 | TT03-D-001 | MCC | 107-LD | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
TT03 | TT03-DY-001 | TT03-D-001 | MCC | 107-LD | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | TRANSFER PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
TT03 | TT03-DYC-001 | TT03-D-001 | MCC | 107-LD | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 012.0 | TRANSFER PUMP | 8968 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
TT03 | TT03-HS-001A | TT03-H-001 | FLD | 107-LD | START PUSHBUTTON | AD TO PUMP TT03-P1 | 012.0 | P1 PUMP CONTROL | 8969 | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | COOPER MEDC | GHG 411 8295 R0001 |  | TI702-SP-5118 | BY TRADE CONTRACTOR |  | 01
TT03 | TT03-HS-001B | TT03-H-001 | FLD | 107-LD | STOP PUSHBUTTON (STAYPUT) | AD TO PUMP TT03-P1 | 012.0 | P1 PUMP CONTROL |  | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | COOPER MEDC | GHG 411 8295 R0001 |  | TI702-SP-5118 | BY TRADE CONTRACTOR |  | 01
TT03 | TT03-LI-001A | TT03-L-001 | PCS | 107-LD | INDICATOR - LEVEL |  |  | LEVEL | REQ: By request |  |  | 0 | [7 empty] | 01
TT03 | TT03-LI-001B | TT03-L-001 | FLD | 107-LD | INDICATOR - LEVEL | ADJ TANK TT03 | 012.0 | LEVEL | REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5116 |  |  | 01
TT03 | TT03-LT-001 | TT03-L-001 | FLD | 107-LD | TRANSMITTER - LEVEL | TT03 | 012.0 | LEVEL | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | VEGA | VEGASON61 | KL0025 | TI702-SP-5116 |  |  | 01
TT03 | TT03-LAH-002 | TT03-L-002 | PCS | 107-LD | ALARM - LEVEL - HIGH |  |  | HIGH LEVEL | PKG: L15861; -: On/off; -: On/off; REF: SHE; REQ: 24 |  |  | 0 | [7 empty] | 01
TT03 | TT03-LE-002 | TT03-L-002 | [6 empty] | PKG: L15861; -: On/off; -: On/off; REF: SHE; REQ: 24
TT03 | TT03-LSH-002 | TT03-L-002 | FLD | 107-LD | SWITCH - LEVEL - HIGH/LOW | TT03/N2/100 | 012.0 | HIGH LEVEL | -: -; F: F; I.S: I.S; DI: DI |  |  | 32 | UTIL | MEGGIT MOBERY | DS1FR4N1PH8/65 | KL0005 | TI702-SP-5113 |  |  | 01
TT03 | TT03-PI-001 | TT03-P-001 | FLD | 107-LD | PRESSURE GAUGE - DIAPHRAGM | 50-P-PT1A-W-9027106 | 012.0 | P1 DISCHARGE PRESSURE | -: 0 to 6 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100/990.27(Note2) | KP0006/1 |  |  |  | 01
TT03 | TT03-TE-001 | TT03-T-001 | FLD | 107-LD | ELEMENT - TEMPERATURE - RTD | SKIN TT03 |  | TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
TT03 | TT03-TI-001A | TT03-T-001 | PCS | 107-LD | INDICATOR - TEMPERATURE |  |  | TEMPERATURE | REQ: By request |  |  | 0 | [7 empty] | 01
TT03 | TT03-TI-001B | TT03-T-001 | FLD | 107-LD | INDICATOR - TEMPERATURE | ADJ TANK TT03 | 012.0 | TEMPERATURE | REQ: By request; F: C; I.S: I.S |  |  | 0 |  | BEKA | BA324C-GRP | KX0017 | TI702-SP-5120 |  |  | 01
TT03 | TT03-TT-001 | TT03-T-001 | FLD | 107-LD | TRANSMITTER - TEMPERATURE | ADJ TO TE | 012.0 | TEMPERATURE | REQ: By request; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5120 |  |  | 01
UPS | UPS-HS-001A | UPS-X-001 | MCC | N/A | SWITCH - KEY OPERATED | UPS IN SWITCHROOM |  | UPS STATUS | PKG: 8970; -: -; -: - |  |  | 0 | [5 empty] | UPS MAINT. ALARM BYPASS |  | 01
UPS | UPS-XA-001 | UPS-X-001 | PCS | N/A | ALARM - UPS COMMON FAULT |  |  | UPS STATUS | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
UPS | UPS-XS-001 | UPS-X-001 | MCC | N/A | SWITCH - UPS STATUS | UPS IN SWITCHROOM | 084.0 | UPS STATUS | 8970 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
UPS | UPS-HS-001B | UPS-X-002 | MCC | N/A | SWITCH - PUSHBUTTON |  |  | UPS BATTERY 50% CHARGE | PKG: 8970; -: -; -: - |  |  | 0 | [5 empty] | UPS MAINT. ALARM BYPASS |  | 01
UPS | UPS-XAL-002 | UPS-X-002 | PCS | N/A | ALARM - UPS COMMON FAULT |  |  | UPS BATTERY 50% CHARGE | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
UPS | UPS-XSL-002 | UPS-X-002 | MCC | N/A | SWITCH - BATTERY LOW | UPS IN SWITCHROOM | 084.0 | UPS BATTERY 50% CHARGE | 8971 | - | - | REF | REQ | F |  | N.I.S | DI |  |  | 35 | UTIL | [6 empty] | 01
VACNTH | VACNTH-CV-001 | VACNTH-C-001 | FLD | 107-GB | HAND VALVE | 50-VP-PT1A-O-9025945 | 038 | VACUUM DVP03 TO DVP01 | REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01 | v16.0
VACNTH | VACNTH-CY-001 | VACNTH-C-001 | FLD | 107-GB | SOLENOID VALVE | RACK MOUNTED | 038 | VACUUM DVP03 TO DVP01 | PKG: 13308 |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  |  | v16.0
VACNTH | VACNTH-ZSC-001 | VACNTH-C-001 | FLD | 107-GB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 038 | VACUUM DVP03 TO DVP01 | 13308 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACNTH | VACNTH-ZSO-001 | VACNTH-C-001 | FLD | 107-GB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 038 | VACUUM DVP03 TO DVP01 | 13308 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACNTH | VACNTH-CV-003 | VACNTH-C-003 | FLD | 107-GB | HAND VALVE | 40-VP-PT1A-0-9021955 | 172 | VACUUM DVP05 TO DVP03 | REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01 | v16.0
VACNTH | VACNTH-CY-003 | VACNTH-C-003 | FLD | 107-GB | SOLENOID VALVE | RACK MOUNTED | 172 | VACUUM DVP05 TO DVP03 | PKG: 13309 |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  |  | v16.0
VACNTH | VACNTH-ZSC-003 | VACNTH-C-003 | FLD | 107-GB | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 172 | VACUUM DVP05 TO DVP03 | 13309 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACNTH | VACNTH-ZSO-003 | VACNTH-C-003 | FLD | 107-GB | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 172 | VACUUM DVP05 TO DVP03 | 13309 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACNTH | VACNTH-PI-001 | VACNTH-P-001 | PCS | 107-GB | INDICATOR - PRESSURE |  | 038 | VACUUM TO DVP01 | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01 | v16.0
VACNTH | VACNTH-PT-001 | VACNTH-P-001 | FLD | 107-GB | TRANSMITTER - PRESSURE - DIAPHRAGM | 40-VP-PT1A-0-9021955 | 038 | VACUUM TO TD02-VC1 | 13310 | -1 to 0.1 barg |  | REF | REQ | C | OPS | I.S | AI | 1 |  | 11 | UTIL | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 28 | v16.0
VACNTH | VACNTH-PI-002 | VACNTH-P-002 | PCS | 107-GB | INDICATOR - PRESSURE |  | 172 | VACUUM TO DVP05 / GP1 / GP2 | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01 | v16.0
VACNTH | VACNTH-PT-002 | VACNTH-P-002 | FLD | 107-GB | TRANSMITTER - PRESSURE - DIAPHRAGM | 40-VP-PT1A-0-9021955 | 172 | VACUUM TO TD01-VC1 & RCH-VC1 | 13311 | -1 to 0.1 barg |  | REF | REQ | C | OPS | I.S | AI | 1 |  | 11 | UTIL | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 28 | v16.0
VACSTH | VACSTH-CV-001 | VACSTH-C-001 | FLD | 107-GA | HAND VALVE | 50-VP-PT1A-0-902???? | 036 | VACUUM TO NORTH TO SOUTH | REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01 | v16.0
VACSTH | VACSTH-CY-001 | VACSTH-C-001 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED | 036 | VACUUM TO NORTH TO SOUTH | PKG: 13312 |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  |  | v16.0
VACSTH | VACSTH-ZSC-001 | VACSTH-C-001 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 036 | VACUUM TO NORTH TO SOUTH | 13312 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACSTH | VACSTH-ZSO-001 | VACSTH-C-001 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 036 | VACUUM TO NORTH TO SOUTH | 13312 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACSTH | VACSTH-CV-002 | VACSTH-C-002 | FLD | 107-GA | HAND VALVE | 50-VP-PT1A-0-902???? | 036 | VACUUM TO NORTH TO SOUTH | REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01 | v16.0
VACSTH | VACSTH-CY-002 | VACSTH-C-002 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED | 036 | VACUUM TO NORTH TO SOUTH | PKG: 13313 |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  |  | v16.0
VACSTH | VACSTH-ZSC-002 | VACSTH-C-002 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 036 | VACUUM TO NORTH TO SOUTH | 13313 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACSTH | VACSTH-ZSO-002 | VACSTH-C-002 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 036 | VACUUM TO NORTH TO SOUTH | 13313 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACSTH | VACSTH-CV-003 | VACSTH-C-003 | FLD | 107-GA | HAND VALVE | 40-VP-PT1A-0-9025923 | 036 | VACUUM DVP01 TO DVP04 | REF: N/A; REQ: -; F: -; Ref: - | [6 empty] | KV0007/P2 |  |  |  | 01 | v16.0
VACSTH | VACSTH-CY-003 | VACSTH-C-003 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED | 036 | VACUUM DVP01 TO DVP04 | PKG: 13314 |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  |  | v16.0
VACSTH | VACSTH-ZSC-003 | VACSTH-C-003 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 036 | VACUUM DVP01 TO DVP04 | 13314 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACSTH | VACSTH-ZSO-003 | VACSTH-C-003 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 036 | VACUUM DVP01 TO DVP04 | 13314 |  |  | N/A | - | - | - | I.S | DI | 1 |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VACSTH | VACSTH-PI-001 | VACSTH-P-001 | PCS | 107-GA | INDICATOR - PRESSURE |  | 036 | VACUUM TO | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01 | v16.0
VACSTH | VACSTH-PT-001 | VACSTH-P-001 | FLD | 107-GA | TRANSMITTER - PRESSURE - DIAPHRAGM | 40-VP-PT1A-0-9025923 | 036 | VACUUM TO PD01-VC1 | 13315 | -1 to 0.1 barg |  | REF | REQ | C | OPS | I.S | AI | 1 |  | 11 | UTIL | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 28 | v16.0
VACSTH | VACSTH-PI-002 | VACSTH-P-002 | PCS | 107-GA | INDICATOR - PRESSURE |  | 036 | VACUUM TO | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01 | v16.0
VACSTH | VACSTH-PT-002 | VACSTH-P-002 | FLD | 107-GA | TRANSMITTER - PRESSURE - DIAPHRAGM | 40-VP-PT1A-0-9025561 | 036 | VACUUM TO MES01-RC10-VC1 | 13316 | -1 to 0.1 barg |  | REF | REQ | C | OPS | I.S | AI | 1 |  | 11 | UTIL | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 28 | v16.0
VACSTH | VACSTH-PI-003 | VACSTH-P-003 | PCS | 107-GA | INDICATOR - PRESSURE |  | 036 | VACUUM TO | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01 | v16.0
VACSTH | VACSTH-PT-003 | VACSTH-P-003 | FLD | 107-GA | TRANSMITTER - PRESSURE - DIAPHRAGM | 40-VP-PT1A-0-9025511 | 036 | VACUUM TO FD04-VC1 | 13317 | -1 to 0.1 barg |  | REF | REQ | C | OPS | I.S | AI | 1 |  | 11 | UTIL | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 28 | v16.0
VACSTH | VACSTH-PI-004 | VACSTH-P-004 | PCS | 107-GA | INDICATOR - PRESSURE |  | 036 | VACUUM TO | REF: N/A; REQ: -; F: -; Ref: - | [10 empty] | 01 | v16.0
VACSTH | VACSTH-PT-004 | VACSTH-P-004 | FLD | 107-GA | TRANSMITTER - PRESSURE - DIAPHRAGM | 40-VP-PT1A-0-9022922 | 036 | VACUUM TO FD03-VC1 | 13318 | -1 to 0.1 barg |  | REF | REQ | C | OPS | I.S | AI | 1 |  | 11 | UTIL | ROSEMOUNT | 3051S | KP0001/P | TI702-SP-5041 |  |  | 28 | v16.0
VDIS | VDIS-CV-001 | VDIS-C-001 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025965 | 034.1 | FG1 PROCESS VACUUM | 8224 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-001 | VDIS-C-001 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-001 | VDIS-C-001 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-001 | VDIS-C-001 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-002 | VDIS-C-002 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025944 | 034.1 | FG1 PROCESS VACUUM | 8225 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-002 | VDIS-C-002 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-002 | VDIS-C-002 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-002 | VDIS-C-002 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-003 | VDIS-C-003 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025925 | 034.1 | GP1 PROCESS VACUUM | 7330 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-003 | VDIS-C-003 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-003 | VDIS-C-003 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-003 | VDIS-C-003 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-004 | VDIS-C-004 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025927 | 034.1 | GP1 PROCESS VACUUM | 7331 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-004 | VDIS-C-004 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-004 | VDIS-C-004 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-004 | VDIS-C-004 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-005 | VDIS-C-005 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025929 | 034.1 | GP1 PROCESS VACUUM | 7332 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-005 | VDIS-C-005 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-005 | VDIS-C-005 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-005 | VDIS-C-005 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-006 | VDIS-C-006 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025931 | 034.1 | GP1 PROCESS VACUUM | 7333 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-006 | VDIS-C-006 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-006 | VDIS-C-006 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-006 | VDIS-C-006 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-007 | VDIS-C-007 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025961 | 034.1 | FG1 PROCESS VACUUM | 7334 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-007 | VDIS-C-007 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-007 | VDIS-C-007 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-007 | VDIS-C-007 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-008 | VDIS-C-008 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025935 | 034.2 | FG1 PROCESS VACUUM | 7335 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-008 | VDIS-C-008 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-008 | VDIS-C-008 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-008 | VDIS-C-008 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | FG1 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-009 | VDIS-C-009 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025937 | 034.1 | GP2 PROCESS VACUUM | 7336 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-009 | VDIS-C-009 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-009 | VDIS-C-009 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-009 | VDIS-C-009 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-010 | VDIS-C-010 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025940 | 034.1 | GP2 PROCESS VACUUM | 7337 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-010 | VDIS-C-010 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-010 | VDIS-C-010 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-010 | VDIS-C-010 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-011 | VDIS-C-011 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025924 | 034.1 | GP2 PROCESS VACUUM | 7338 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-011 | VDIS-C-011 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-011 | VDIS-C-011 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-011 | VDIS-C-011 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-CV-012 | VDIS-C-012 | FLD | 107-GA | BALL VALVE - ON/OFF - F.C. | 50-VP-PT1A-0-9025933 | 034.1 | GP2 PROCESS VACUUM | 7339 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0007 |  |  |  | 01 | v16.0
VDIS | VDIS-CY-012 | VDIS-C-012 | FLD | 107-GA | SOLENOID VALVE | RACK MOUNTED |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01 | v16.0
VDIS | VDIS-ZSC-012 | VDIS-C-012 | FLD | 107-GA | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VDIS | VDIS-ZSO-012 | VDIS-C-012 | FLD | 107-GA | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | GP2 PROCESS VACUUM | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01 | v16.0
VP01 | VP01-DIC-001 | VP01-D-001 | PCS | 107-GK | INDICATING CONTR. - MOTOR DRIVE |  |  | VACUUM PUMP | [11 empty] | 0 | [7 empty] | 01 | bar: PKG
VP01 | VP01-DS-001 | VP01-D-001 | MCC | 107-GK | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | VACUUM PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
VP01 | VP01-DY-001 | VP01-D-001 | MCC | 107-GK | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | VACUUM PUMP | I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
VP01 | VP01-DYC-001 | VP01-D-001 | MCC | 107-GK | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 033.0 | VACUUM PUMP | 8972 | - | - | REF | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
VP01 | VP01-PI-001 | VP01-P-001 | FLD | 107-GK | PRESSURE GAUGE | 40-VP-PP1A-0-9025922 | 033.0 | INLET PRESSURE | -: -1 to 0 barg; -: +/- 5%; REF: REF; REQ: REQ; F: C |  |  | 0 |  | WIKA | 232.50.100 | KP0006/3 |  |  |  | 01
VP02 | VP02-CV-001 | VP02-C-001 | PKG | 107-GD | BALL VALVE - ON/OFF - F.C. | VP02 | 034.1 | ST1 LIQUID OUTLET | 8973 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
VP02 | VP02-CY-001 | VP02-C-001 | FLD | 107-GD | SOLENOID VALVE | RACK MOUNTED |  | ST1 LIQUID OUTLET | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
VP02 | VP02-ZSC-001 | VP02-C-001 | PKG | 107-GD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ST1 LIQUID OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP02 | VP02-ZSO-001 | VP02-C-001 | PKG | 107-GD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ST1 LIQUID OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP02 | VP02-CV-005 | VP02-C-005 | FLD | 107-GD | BALL VALVE - ON/OFF - F.C. | 50-SV-SS1C-0-9025244 | 008.1 | TO SCRUBBER 02 | 7103 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
VP02 | VP02-CY-005 | VP02-C-005 | FLD | 107-GD | SOLENOID VALVE | RACK MOUNTED |  | TO SCRUBBER 02 | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
VP02 | VP02-ZSC-005 | VP02-C-005 | FLD | 107-GD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO SCRUBBER 02 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP02 | VP02-ZSO-005 | VP02-C-005 | FLD | 107-GD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO SCRUBBER 02 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP02 | VP02-CV-006 | VP02-C-006 | FLD | 107-GD | BALL VALVE - ON/OFF - F.C. | 50-SV-SS1C-0-9025245 | 008.1 | TO SCRUBBER 01 | 7106 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
VP02 | VP02-CY-006 | VP02-C-006 | FLD | 107-GD | SOLENOID VALVE | RACK MOUNTED |  | TO SCRUBBER 01 | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
VP02 | VP02-ZSC-006 | VP02-C-006 | FLD | 107-GD | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO SCRUBBER 01 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP02 | VP02-ZSO-006 | VP02-C-006 | FLD | 107-GD | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO SCRUBBER 01 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP02 | VP02-DIC-001 | VP02-D-001 | PCS | 107-GD | INDICATING CONTR. - MOTOR DRIVE |  |  | VACUUM PUMP | REF: SHE |  |  | 0 | [7 empty] | 01
VP02 | VP02-DS-001 | VP02-D-001 | MCC | 107-GD | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | VACUUM PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
VP02 | VP02-DY-001 | VP02-D-001 | MCC | 107-GD | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | VACUUM PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
VP02 | VP02-DYC-001 | VP02-D-001 | MCC | 107-GD | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 034.1 | VACUUM PUMP | 8974 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
VP02 | VP02-FI-001 | VP02-F-001 | PKG | 107-GD | VA FLOW METER | VP02 | 034.1 | SEAL FLUID FLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | KROHNE | H250/RR/M9 | KF0027/P |  |  |  | 01
VP02 | VP02-HV-001 | VP02-H-001 | PKG | 107-GD | V BALL HAND VALVE | VP02 | [13 empty] | 0 |  | HABONIM | 31 Series V-FLOW |  |  |  |  | 01 | bar: PKG to -
VP02 | VP02-LAHH-001 | VP02-L-001 | PCS | 107-GD | ALARM - LEVEL - HI HI |  |  | ST1 HI-HI LEVEL | -: -; -: -; REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP02 | VP02-LSHH-001 | VP02-L-001 | PKG | 107-GD | SWITCH - LEVEL - HI HI | VP02-ST1 | 034.1 | ST1 HI-HI LEVEL |  | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
VP02 | VP02-LAH-002 | VP02-L-002 | PCS | 107-GD | ALARM - LEVEL - HIGH |  |  | ST1 HIGH LEVEL | -: On/off; -: On/off; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 01
VP02 | VP02-LSH-002 | VP02-L-002 | PKG | 107-GD | SWITCH - LEVEL - HIGH | VP02-ST1 | 034.1 | ST1 HIGH LEVEL | L15875 | On/off | On/off | REF | 24 | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
VP02 | VP02-LAL-003 | VP02-L-003 | PCS | 107-GD | ALARM - LEVEL - LOW |  |  | ST1 LOW LEVEL | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP02 | VP02-LSL-003 | VP02-L-003 | PKG | 107-GD | SWITCH - LEVEL - LOW | VP02-ST1 | 034.1 | ST1 LOW LEVEL |  | - | - | SHE | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
VP02 | VP02-LI-004 | VP02-L-004 | PKG | 107-GD | INDICATOR - LEVEL GAUGE | VP02-ST1 | 034.1 | ST1 LEVEL | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
VP02 | VP02-PI-001 | VP02-P-001 | PCS | 107-GD | INDICATOR - PRESSURE |  |  | HEADER PRESSURE | -: -; -: -; REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP02 | VP02-PIT-001 | VP02-P-001 | FLD | 107-GD | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-VP-PT1A-0-9025920 | 034.1 | HEADER PRESSURE |  | - | - | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
VP02 | VP02-PSV-002 | VP02-P-002 | FLD | 107-GD | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9025251 | 040.2 | ST1 HTF RELIEF | -: 10 barg; -: +/- 10%; REF: SHE; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
VP02 | VP02-PI-003 | VP02-P-003 | PCS | 107-GD | INDICATOR - PRESSURE |  |  | VACUUM PUMP VENT PRESSURE |  | -1 to 4 barg | +/- 1% | SHE | 12 | C |  | I.S | AI | [11 empty] | v18.0
VP02 | VP02-PIT-003 | VP02-P-003 | FLD | 107-GD | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-SS1C-0-9025243 | 034.1 | VACUUM PUMP VENT PRESSURE |  | -1 to 4 barg | +/- 1% | SHE | 12 | C |  |  | DI |  |  |  |  | ROSEMOUNT | 3051S | [5 empty] | v18.0
VP02 | VP02-PSH-003 | VP02-P-003 | FLD | 107-GD | SWITCH - PRESSURE - HIGH | RACK MOUNTED | 034.1 | VACUUM PUMP VENT PRESSURE | -: 0.3 barg rising; -: +/- 1%; REF: SHE; REQ: 12; F: F | [11 empty] | v18.0
VP02 | VP02-TE-001 | VP02-T-001 | PKG | 107-GD | ELEMENT - TEMPERATURE - RTD | VP02-ST1 |  | ST1 TEMPERATURE | PKG: L8978; -: -50 to 50 degC; -: +/- 2 degC; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 01
VP02 | VP02-TI-001 | VP02-T-001 | PCS | 107-GD | INDICATOR - TEMPERATURE |  |  | ST1 TEMPERATURE | PKG: L8978; -: -50 to 50 degC; -: +/- 2 degC; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 01
VP02 | VP02-TT-001 | VP02-T-001 | PKG | 107-GD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 034.1 | ST1 TEMPERATURE | L8978 | -50 to 50 degC | +/- 2 degC | REF | 24 | C |  | I.S | AI |  |  | 11 | UTIL | BOURDON SEDEME | Y76TR |  | TI702-SP-5075 |  |  | 01
VP02 | VP02-TE-002 | VP02-T-002 | FLD | 107-GD | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9025240 |  | HTF RTN TEMPERATURE | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP02 | VP02-TI-002 | VP02-T-002 | PCS | 107-GD | INDICATOR - TEMPERATURE |  |  | HTF RTN TEMPERATURE | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP02 | VP02-TT-002 | VP02-T-002 | FLD | 107-GD | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.2 | HTF RTN TEMPERATURE |  | - | - | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
VP03 | VP03-CV-001 | VP03-C-001 | PKG | 107-GE | BALL VALVE - ON/OFF - F.C. | VP03 | 034.2 | ST1 LIQUID OUTLET | 8979 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
VP03 | VP03-CY-001 | VP03-C-001 | FLD | 107-GE | SOLENOID VALVE | RACK MOUNTED |  | ST1 LIQUID OUTLET | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
VP03 | VP03-ZSC-001 | VP03-C-001 | PKG | 107-GE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ST1 LIQUID OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP03 | VP03-ZSO-001 | VP03-C-001 | PKG | 107-GE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ST1 LIQUID OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP03 | VP03-CV-005 | VP03-C-005 | FLD | 107-GE | BALL VALVE - ON/OFF - F.C. | 50-SV-SS1C-0-9025284 | 008.1 | TO SCRUBBER 02 | 7104 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
VP03 | VP03-CY-005 | VP03-C-005 | FLD | 107-GE | SOLENOID VALVE | RACK MOUNTED |  | TO SCRUBBER 02 | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
VP03 | VP03-ZSC-005 | VP03-C-005 | FLD | 107-GE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO SCRUBBER 02 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP03 | VP03-ZSO-005 | VP03-C-005 | FLD | 107-GE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO SCRUBBER 02 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP03 | VP03-CV-006 | VP03-C-006 | FLD | 107-GE | BALL VALVE - ON/OFF - F.C. | 50-SV-SS1C-0-9025285 | 008.1 | TO SCRUBBER 01 | 7107 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
VP03 | VP03-CY-006 | VP03-C-006 | FLD | 107-GE | SOLENOID VALVE | RACK MOUNTED |  | TO SCRUBBER 01 | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
VP03 | VP03-ZSC-006 | VP03-C-006 | FLD | 107-GE | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO SCRUBBER 01 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP03 | VP03-ZSO-006 | VP03-C-006 | FLD | 107-GE | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO SCRUBBER 01 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP03 | VP03-DIC-001 | VP03-D-001 | PCS | 107-GE | INDICATING CONTR. - MOTOR DRIVE |  |  | VACUUM PUMP | REF: SHE |  |  | 0 | [7 empty] | 01
VP03 | VP03-DS-001 | VP03-D-001 | MCC | 107-GE | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | VACUUM PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
VP03 | VP03-DY-001 | VP03-D-001 | MCC | 107-GE | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | VACUUM PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
VP03 | VP03-DYC-001 | VP03-D-001 | MCC | 107-GE | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 034.2 | VACUUM PUMP | 8980 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
VP03 | VP03-FI-001 | VP03-F-001 | PKG | 107-GE | VA FLOW METER | VP03 | 034.2 | SEAL FLUID FLOW | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 |  | KROHNE | H250/RR/M9 | KF0027/P |  |  |  | 01
VP03 | VP03-HV-001 | VP03-H-001 | PKG | 107-GE | V BALL HAND VALVE | VP03 | [13 empty] | 0 |  | HABONIM | 31 Series V-FLOW |  |  |  |  | 01 | bar: PKG to -
VP03 | VP03-LAH-001 | VP03-L-001 | [6 empty] | -: -; -: -; REF: REF; REQ: REQ
VP03 | VP03-LAHH-001 | VP03-L-001 | PCS | 107-GE | ALARM - LEVEL - HI HI |  |  | ST1 HI-HI LEVEL | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP03 | VP03-LSHH-001 | VP03-L-001 | PKG | 107-GE | SWITCH - LEVEL - HI HI | VP03-ST1 | 034.2 | ST1 HI-HI LEVEL |  | - | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
VP03 | VP03-LAH-002 | VP03-L-002 | PCS | 107-GE | ALARM - LEVEL - HIGH |  |  | ST1 HIGH LEVEL | PKG: L15876; -: On/off; -: On/off; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 01
VP03 | VP03-LSH-002 | VP03-L-002 | PKG | 107-GE | SWITCH - LEVEL - HIGH | VP03-ST1 | 034.2 | ST1 HIGH LEVEL | L15876 | On/off | On/off | REF | 24 | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
VP03 | VP03-LAL-003 | VP03-L-003 | PCS | 107-GE | ALARM - LEVEL - LOW |  |  | ST1 LOW LEVEL | -: -; -: -; REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP03 | VP03-LSL-003 | VP03-L-003 | PKG | 107-GE | SWITCH - LEVEL - LOW | VP03-ST1 | 034.2 | ST1 LOW LEVEL |  | - | - | SHE | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
VP03 | VP03-LI-004 | VP03-L-004 | PKG | 107-GE | INDICATOR - LEVEL GAUGE | VP03-ST1 | 034.2 | ST1 LEVEL | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
VP03 | VP03-PI-001 | VP03-P-001 | PCS | 107-GE | INDICATOR - PRESSURE |  |  | HEADER PRESSURE | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP03 | VP03-PIT-001 | VP03-P-001 | FLD | 107-GE | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-VP-PT1A-0-9025921 | 034.2 | HEADER PRESSURE |  | - | - | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | FOXBORO | 141GP (Note1) | KP0001 | TI702-SP-5006 |  |  | 01
VP03 | VP03-PSV-002 | VP03-P-002 | FLD | 107-GE | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9025289 | 040.2 | ST1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
VP03 | VP03-PI-003 | VP03-P-003 | PCS | 107-GE | INDICATOR - PRESSURE |  |  | VACUUM PUMP VENT PRESSURE |  | -1 to 4 barg | +/- 1% | SHE | 12 | C |  | I.S | AI | [11 empty] | v18.0
VP03 | VP03-PIT-003 | VP03-P-003 | FLD | 107-GE | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-SS1C-0-9025283 | 34.2 | VACUUM PUMP VENT PRESSURE |  | -1 to 4 barg | +/- 1% | SHE | 12 | C |  |  | DI |  |  |  |  | ROSEMOUNT | 3051S | [5 empty] | v18.0
VP03 | VP03-PSH-003 | VP03-P-003 | FLD | 107-GE | SWITCH - PRESSURE - HIGH | RACK MOUNTED | 34.2 | VACUUM PUMP VENT PRESSURE | -: 0.3 barg rising; -: +/- 1%; REF: SHE; REQ: 12; F: F | [11 empty] | v18.0
VP03 | VP03-TE-001 | VP03-T-001 | PKG | 107-GE | ELEMENT - TEMPERATURE - RTD | VP03-ST1 |  | ST1 TEMPERATURE | PKG: L6605; -: -50 to 50 degC; -: +/- 2 degC; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 01
VP03 | VP03-TI-001 | VP03-T-001 | PCS | 107-GE | INDICATOR - TEMPERATURE |  |  | ST1 TEMPERATURE | PKG: L6605; -: -50 to 50 degC; -: +/- 2 degC; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 01
VP03 | VP03-TT-001 | VP03-T-001 | PKG | 107-GE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 034.2 | ST1 TEMPERATURE | L6605 | -50 to 50 degC | +/- 2 degC | REF | 24 | C |  | I.S | AI |  |  | 11 | UTIL | BOURDON SEDEME | Y76TR |  | TI702-SP-5075 |  |  | 01
VP03 | VP03-TE-002 | VP03-T-002 | FLD | 107-GE | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9025280 |  | HTF RTN TEMPERATURE | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP03 | VP03-TI-002 | VP03-T-002 | PCS | 107-GE | INDICATOR - TEMPERATURE |  |  | HTF RTN TEMPERATURE | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP03 | VP03-TT-002 | VP03-T-002 | FLD | 107-GE | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.2 | HTF RTN TEMPERATURE |  | - | - | REF | REQ | C |  | I.S | AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 01
VP04 | VP04-CV-001 | VP04-C-001 | PKG | 107-GF | BALL VALVE - ON/OFF - F.C. | VP04 | 035.0 | ST1 LIQUID OUTLET | 8984 | - | - | REF | REQ | F | [5 empty] | 0 | [7 empty] | 01
VP04 | VP04-CY-001 | VP04-C-001 | FLD | 107-GF | SOLENOID VALVE | RACK MOUNTED |  | ST1 LIQUID OUTLET | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
VP04 | VP04-ZSC-001 | VP04-C-001 | PKG | 107-GF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | ST1 LIQUID OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP04 | VP04-ZSO-001 | VP04-C-001 | PKG | 107-GF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | ST1 LIQUID OUTLET | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP04 | VP04-CV-005 | VP04-C-005 | FLD | 107-GF | BALL VALVE - ON/OFF - F.C. | 50-SV-SS1C-0-9025323 | 008.3 | TO SCRUBBER 03 | 7105 | - | - | REF | REQ | F | [5 empty] | 0 |  |  |  | KV0017 |  |  |  | 01
VP04 | VP04-CY-005 | VP04-C-005 | FLD | 107-GF | SOLENOID VALVE | RACK MOUNTED |  | TO SCRUBBER 03 | I.S: I.S; DI: DO |  |  | 41 | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004 |  |  | 01
VP04 | VP04-ZSC-005 | VP04-C-005 | FLD | 107-GF | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE |  | TO SCRUBBER 03 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP04 | VP04-ZSO-005 | VP04-C-005 | FLD | 107-GF | PROXIMITY SENSOR - OPEN | MTD. ON VALVE |  | TO SCRUBBER 03 | I.S: I.S; DI: DI |  |  | 31 | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001 |  |  | 01
VP04 | VP04-DIC-001 | VP04-D-001 | PCS | 107-GF | INDICATING CONTR. - MOTOR DRIVE |  |  | VACUUM PUMP | REF: SHE |  |  | 0 | [7 empty] | 01
VP04 | VP04-DS-001 | VP04-D-001 | MCC | 107-GF | DRIVE - AVAILABLE | MOTOR CONTROL CENTRE |  | VACUUM PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
VP04 | VP04-DY-001 | VP04-D-001 | MCC | 107-GF | DRIVE - RUNNING | MOTOR CONTROL CENTRE |  | VACUUM PUMP | REF: SHE; I.S: N.I.S; DI: DI |  |  | 35 | UTIL | [6 empty] | 01
VP04 | VP04-DYC-001 | VP04-D-001 | MCC | 107-GF | DRIVE - START/STOP | MOTOR CONTROL CENTRE | 035.0 | VACUUM PUMP | 8985 | - | - | SHE | REQ | F |  | N.I.S | DO |  |  | 42 | UTIL | [6 empty] | 01
VP04 | VP04-FI-001 | VP04-F-001 | PKG | 107-GF | VA FLOW METER | VP04 | 035.0 | SEAL FLUID FLOW | REF: REF; REQ: REQ; F: F |  |  | 0 |  | KROHNE | H250/RR/M9 | KF0027/P |  |  |  | 01
VP04 | VP04-HV-001 | VP04-H-001 | PKG | 107-GF | V BALL HAND VALVE | VP04 | [13 empty] | 0 |  | HABONIM | 31 Series V-FLOW |  |  |  |  | 01 | bar: PKG to -
VP04 | VP04-LAHH-001 | VP04-L-001 | PCS | 107-GF | ALARM - LEVEL - HI HI |  |  | ST1 HI-HI LEVEL | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP04 | VP04-LSHH-001 | VP04-L-001 | PKG | 107-GF | SWITCH - LEVEL - HI HI | VP04-ST1 | 035.0 | ST1 HI-HI LEVEL |  |  | - | REF | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
VP04 | VP04-LAH-002 | VP04-L-002 | PCS | 107-GF | ALARM - LEVEL - HIGH |  |  | ST1 HIGH LEVEL | PKG: L15877; -: On/off; -: On/off; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 01
VP04 | VP04-LSH-002 | VP04-L-002 | PKG | 107-GF | SWITCH - LEVEL - HIGH | VP04-ST1 | 035.0 | ST1 HIGH LEVEL | L15877 | On/off | On/off | REF | 24 | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
VP04 | VP04-LAL-003 | VP04-L-003 | PCS | 107-GF | ALARM - LEVEL - LOW |  |  | ST1 LOW LEVEL | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP04 | VP04-LSL-003 | VP04-L-003 | PKG | 107-GF | SWITCH - LEVEL - LOW | VP04-ST1 | 035.0 | ST1 LOW LEVEL |  | - | - | SHE | REQ | F |  | I.S | DI |  |  | 32 | UTIL | MOBREY | 70866/186 |  | TI702-SP-5072 |  |  | 01
VP04 | VP04-LI-004 | VP04-L-004 | PKG | 107-GF | INDICATOR - LEVEL GAUGE | VP04-ST1 | 035.0 | ST1 LEVEL | -: -; -: -; REF: REF; REQ: REQ; F: F |  |  | 0 | [7 empty] | 01
VP04 | VP04-PI-001 | VP04-P-001 | PCS | 107-GF | INDICATOR - PRESSURE |  |  | HEADER PRESSURE | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 01
VP04 | VP04-PIT-001 | VP04-P-001 | FLD | 107-GF | TRANSMITTER - PRESSURE - DIAPHRAGM | 40-VP-PT1A-0-9025962 | 035.0 | HEADER PRESSURE | REF: REF; REQ: REQ; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | FOXBORO | 141GP (Note 1) | KP0001 | TI702-SP-5006 |  |  | 01
VP04 | VP04-PSV-002 | VP04-P-002 | FLD | 107-GF | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9025331 | 040.2 | ST1 HTF RELIEF | -: 10 barg; -: +/- 10%; REQ: 24; F: C |  |  | 0 |  | BROADY | 2531D-C-B000 | KS0001 |  |  |  | 01
VP04 | VP04-PI-003 | VP04-P-003 | PCS | 107-GF | INDICATOR - PRESSURE |  |  | VACUUM PUMP VENT PRESSURE |  | -1 to 4 barg | +/- 1% | SHE | 12 | C |  | I.S | AI | [11 empty] | v18.0
VP04 | VP04-PIT-003 | VP04-P-003 | FLD | 107-GF | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-P-SS1C-0-9025353 | 35.0 | VACUUM PUMP VENT PRESSURE |  | -1 to 4 barg | +/- 1% | SHE | 12 | C |  |  | DI |  |  |  |  | ROSEMOUNT | 3051S | [5 empty] | v18.0
VP04 | VP04-PSH-003 | VP04-P-003 | FLD | 107-GF | SWITCH - PRESSURE - HIGH | RACK MOUNTED | 35.0 | VACUUM PUMP VENT PRESSURE | -: 0.3 barg rising; -: +/- 1%; REF: SHE; REQ: 12; F: F | [11 empty] | v18.0
VP04 | VP04-TE-001 | VP04-T-001 | PKG | 107-GF | ELEMENT - TEMPERATURE - RTD | VP04-ST1 |  | ST1 TEMPERATURE | PKG: L8989; -: -50 to 50 degC; -: +/- 2degC; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 31
VP04 | VP04-TI-001 | VP04-T-001 | PCS | 107-GF | INDICATOR - TEMPERATURE |  |  | ST1 TEMPERATURE | -: -50 to 50 degC; -: +/- 2degC; REF: REF; REQ: 24 |  |  | 0 | [7 empty] | 31
VP04 | VP04-TT-001 | VP04-T-001 | PKG | 107-GF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 035.0 | ST1 TEMPERATURE | L8989 | -50 to 50 degC | +/- 2degC | REF | 24 | C |  | I.S | AI |  |  | 11 | UTIL | BOURDON SEDEME | Y76TR |  | TI702-SP-5075 |  |  | 31
VP04 | VP04-TE-002 | VP04-T-002 | FLD | 107-GF | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9025320 |  | HTF RTN TEMPERATURE | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 31
VP04 | VP04-TI-002 | VP04-T-002 | PCS | 107-GF | INDICATING CONTROLLER - TEMPERATURE |  |  | HTF RTN TEMPERATURE | REF: REF; REQ: REQ |  |  | 0 | [7 empty] | 31
VP04 | VP04-TT-002 | VP04-T-002 | FLD | 107-GF | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.2 | HTF RTN TEMPERATURE | REF: REF; REQ: REQ; F: C; I.S: I.S; DI: AI |  |  | 11 | UTIL | MOORE INDUSTRIES | TRX/PRG / DM400X | KT0004 | TI702-SP-5040 |  |  | 31
VP05 | VP05-CV-001 | VP05-C-001 | FLD | 107-GM | BALL VALVE - ON/OFF - F.C. | VP05 | 034.3 | ST1 LIQUID OUTLET | 02189 | - | - | - | - | F |  | - | - |  |  | 0
VP05 | VP05-CY-001 | VP05-C-001 | FLD | 107-GM | SOLENOID VALVE | RACK MOUNTED | 034.3 | ST1 LIQUID OUTLET | 02189 | - | - | - | - | F |  | I.S | DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004
VP05 | VP05-ZSC-001 | VP05-C-001 | FLD | 107-GM | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 034.3 | ST1 LIQUID OUTLET | 02189 | - | - | - | - | F |  | I.S | DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
VP05 | VP05-ZSO-001 | VP05-C-001 | FLD | 107-GM | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 034.3 | ST1 LIQUID OUTLET | 02189 | - | - | - | - | F |  | I.S | DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
VP05 | VP05-CV-005 | VP05-C-005 | FLD | 107-GM | BALL VALVE - ON/OFF - F.C. | 50-SV-SS1C-0-9027723 | 008.2 | TO SCRUBBER 02 | 02190 | - | - | - | - | F |  | - | -
VP05 | VP05-CY-005 | VP05-C-005 | FLD | 107-GM | SOLENOID VALVE | RACK MOUNTED | 008.2 | TO SCRUBBER 02 | 02190 | - | - | - | - | F |  | I.S | DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004
VP05 | VP05-ZSC-005 | VP05-C-005 | FLD | 107-GM | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 008.2 | TO SCRUBBER 02 | 02190 | - | - | - | - | F |  | I.S | DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
VP05 | VP05-ZSO-005 | VP05-C-005 | FLD | 107-GM | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 008.2 | TO SCRUBBER 02 | 02190 | - | - | - | - | F |  | I.S | DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
VP05 | VP05-CV-006 | VP05-C-006 | FLD | 107-GM | BALL VALVE - ON/OFF - F.C. | 50-SV-SS1C-0-9027724 | 008.1 | TO SCRUBBER 01 | 02191 | - | - | REF | REQ | F |  | - | -
VP05 | VP05-CY-006 | VP05-C-006 | FLD | 107-GM | SOLENOID VALVE | RACK MOUNTED | 008.1 | TO SCRUBBER 01 | 02191 | - | - | REF | REQ | F |  | I.S | DO |  |  |  | UTIL | CROUZET | 81 519 _35 |  | TI702-SP-5004
VP05 | VP05-ZSC-006 | VP05-C-006 | FLD | 107-GM | PROXIMITY SENSOR - CLOSED | MTD. ON VALVE | 008.1 | TO SCRUBBER 01 | 02191 | - | - | REF | REQ | F |  | I.S | DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
VP05 | VP05-ZSO-006 | VP05-C-006 | FLD | 107-GM | PROXIMITY SENSOR - OPEN | MTD. ON VALVE | 008.1 | TO SCRUBBER 01 | 02191 | - | - | REF | REQ | F |  | I.S | DI |  |  |  | UTIL | PEPPERL + FUCHS | NJ2-V3-N |  | TI702-SP-5001
VP05 | VP05-DIC-001 | VP05-D-001 | PKG | 107-GM | INDICATING CONTR. - MOTOR DRIVE |  |  | VACUUM PUMP | PKG: Deleted; F: F
VP05 | VP05-DS-001 | VP05-D-001 | PKG | 107-GM | DRIVE - AVAILABLE | VP05 PANEL | 034.3 | VACUUM PUMP | 02192 | - | - | SHE | - | F |  | N.I.S | DI |  |  |  | UTILA
VP05 | VP05-DY-001 | VP05-D-001 | PKG | 107-GM | DRIVE - RUNNING | VP05 PANEL | 034.3 | VACUUM PUMP | 02192 | - | - | SHE | - | F |  | N.I.S | DI |  |  |  | UTILA
VP05 | VP05-DYC-001 | VP05-D-001 | PKG | 107-GM | DRIVE - START/STOP | VP05 PANEL | 034.3 | VACUUM PUMP | 02192 | - | - | SHE | - | F |  | N.I.S | DO |  |  |  | UTILA
VP05 | VP05-FSL-001 | VP05-F-001 | PKG | 107-GM | SWITCH-FLOW-LOW | VP05 | 034.3 | LOW FLOW SERVICE LIQUID | Vendor | - | - | REF | REQ | F | [7 empty] | FLOW-MON LTD | FML.40.SS.LP 3EE ATEX 1
VP05 | VP05-HV-001 | VP05-H-001 | FLD | 107-GM | GLOBE HAND VALVE | VP05 | 034.3 | SERVICE LIQUID ISOLATION | N/A | - | - | - | - | F |  | - | -
VP05 | VP05-LAHH-001 | VP05-L-001 | PCS | 107-GM | ALARM - LEVEL - HI HI | PCS | 034.3 | ST1 HI-HI LEVEL | 02193 | - | - | REF | REQ | F
VP05 | VP05-LSHH-001 | VP05-L-001 | FLD | 107-GM | SWITCH - LEVEL - HI HI | VP05-ST1 | 034.3 | ST1 HI-HI LEVEL | 02193 | - | - | REF | REQ | F |  | I.S | DI |  |  |  | UTIL | Vega | Vegaswing 61 |  | TI702-SP-5029
VP05 | VP05-LAH-002 | VP05-L-002 | PCS | 107-GM | ALARM - LEVEL - HIGH | PCS | 034.3 | ST1 HIGH LEVEL | 02194 | On/off | On/off | REF | 12 | F
VP05 | VP05-LSH-002 | VP05-L-002 | FLD | 107-GM | SWITCH - LEVEL - HIGH | VP05-ST1 | 034.3 | ST1 HIGH LEVEL | 02194 | On/off | On/off | REF | 12 | F |  | I.S | DI |  |  |  | UTIL | Vega | Vegaswing 61 |  | TI702-SP-5029
VP05 | VP05-LAL-003 | VP05-L-003 | PCS | 107-GM | ALARM - LEVEL - LOW | PCS | 034.3 | ST1 LOW LEVEL | 02195 | On/off | On/off | SHE | 12 | F
VP05 | VP05-LSL-003 | VP05-L-003 | FLD | 107-GM | SWITCH - LEVEL - LOW | VP05-ST1 | 034.3 | ST1 LOW LEVEL | 02195 | On/off | On/off | SHE | 12 | F |  | I.S | DI |  |  |  | UTIL | Vega | Vegaswing 61 |  | TI702-SP-5029
VP05 | VP05-LI-004 | VP05-L-004 | FLD | 107-GM | INDICATOR - LEVEL GAUGE | VP05-ST1 | 034.3 | ST1 LEVEL | N/A | - | - | REF | REQ | F |  | - | - |  |  |  |  | VISILUME | N/A
VP05 | VP05-PI-001 | VP05-P-001 | PCS | 107-GM | INDICATOR - PRESSURE | 50-VP-PT1A-0-9025922 | 034.3 | VACUUM HEADER PRESSURE | 02196 | - | - | REF | REQ | C |  | - | -
VP05 | VP05-PIT-001 | VP05-P-001 | FLD | 107-GM | TRANSMITTER - PRESSURE - DIAPHRAGM | 50-VP-PT1A-0-9025922 | 034.3 | VACUUM HEADER PRESSURE | 02196 | - | - | REF | REQ | C |  | I.S | AI |  |  |  | UTIL | ROSEMOUNT | 3051S2T2A2G11A1BD1K1MSQ4 |  | TI702-SP-5013
VP05 | VP05-PI-002 | VP05-P-002 | FLD | 107-GM | INDICATOR - PRESSURE | VENDOR PACKAGE | 034.3 | VACUUM HEADER PRESSURE | N/A | - | - | REF | REQ | C |  | - | - |  |  |  |  | WIKA | 232.50.100
VP05 | VP05-PSV-002 | VP05-P-002 | FLD | 107-GM | PRESSURE RELIEF VALVE | 25-HT-CS3A-C-9027727 | 040.2 | PC1 HTF RELIEF | N/A | 9 barg | +/- 10% | - | - | F |  | - | -
VP05 | VP05-PSH-003 | VP05-P-003 | PKG | 107-GM | SWITCH-PRESSURE-HIGH | VENDOR PACKAGE | 034.3 | VP05 DISCHARGE PRESSURE | Vendor | 0 to 2 bar | On/off | SHE | 12 | F | [7 empty] | WIKA / ELLA | PCA2MA
VP05 | VP05-PI-004 | VP05-P-004 | FLD | 107-GM | INDICATOR - PRESSURE | VENDOR PACKAGE | 034.3 | SEAL FLUID PRESSURE | N/A | 0 to 600mbar | - | REF | REQ | C |  | - | - |  |  |  |  | WIKA | 232.50.100
| VP05-RO-001 | VP05-R-001 | FLD | 107-GM | RESTRICTION ORIFICE PLATE | VP05-ST1 Drain | 034.3 | SEAL FLUID DRAIN | N/A | 12mm |  | N/A | - | - | - | [6 empty] | SITE FABRICATED
VP05 | VP05-TE-001 | VP05-T-001 | FLD | 107-GM | ELEMENT - TEMPERATURE - RTD | VP05-ST1 | 034.3 | ST1 TEMPERATURE | 02197 | -50 to 50 degC | +/- 2 degC | REF | 12 | C
VP05 | VP05-TI-001 | VP05-T-001 | PCS | 107-GM | INDICATOR - TEMPERATURE | PCS | 034.3 | ST1 TEMPERATURE | 02197 | -50 to 50 degC | +/- 2 degC | REF | 12 | C |  | - | -
VP05 | VP05-TT-001 | VP05-T-001 | FLD | 107-GM | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 034.3 | ST1 TEMPERATURE | 02197 | -50 to 50 degC | +/- 2 degC | REF | 12 | C |  | I.S | AI |  |  |  | UTIL | ROSEMOUNT | 644H |  | TI702-SP-5012
VP05 | VP05-TE-002 | VP05-T-002 | FLD | 107-GM | ELEMENT - TEMPERATURE - RTD | 40-HT-CS3A-C-9027721 | 040.2 | HTF RTN TEMPERATURE | 02198 | - | - | REF | REQ | C
VP05 | VP05-TI-002 | VP05-T-002 | PCS | 107-GM | INDICATOR - TEMPERATURE | PCS | 040.2 | HTF RTN TEMPERATURE | PKG: 02198; REF: REF; REQ: REQ; F: C |  |  | 0
VP05 | VP05-TT-002 | VP05-T-002 | FLD | 107-GM | TRANSMITTER - TEMPERATURE | HEAD MOUNTED | 040.2 | HTF RTN TEMPERATURE | 02198 | -50 to 450 degC |  | REF | REQ | C |  | I.S | AI |  |  |  | UTIL | ROSEMOUNT | 0065101F105 / 644H |  | TI702-SP-5012
VP05 | VP05-TSH-003 | VP05-T-003 | PKG | 107-GM | SWITCH-TEMPERATURE-HIGH | VENDOR PACKAGE | 034.3 | PUMP DISCHARGE TEMPERATURE | Vendor | 0 to 100 degC | On/off | SHE | 12 | C |  | I.S | DI |  |  |  | UTILA | WIKA / ELLA | TC52BB
VP05 | VP05-TSH-004 | VP05-T-004 | PKG | 107-GM | SWITCH-TEMPERATURE-HIGH | VENDOR PACKAGE | 034.3 | SEAL FLUID TEMPERATURE | Vendor | 0 to 60 degC | On/off | REF | REQ | C |  | I.S | DI |  |  |  | UTILA | WIKA / ELLA | TC52BB
VP05 | VP05-TI-005 | VP05-T-005 | FLD | 107-GM | INDICATOR - TEMPERATURE | VENDOR PACKAGE | 034.3 | SEAL FLUID TEMPERATURE - VP05 INLET | N/A | 0 to 100 degC | - | REF | REQ | C |  | - | - |  |  |  |  | WIKA | R5442
VP05 | VP05-TI-006 | VP05-T-006 | FLD | 107-GM | INDICATOR - TEMPERATURE | VENDOR PACKAGE | 034.3 | PROCESS HEADER TEMPERATURE | N/A | 0 to 100 degC | - | REF | REQ | C |  | - | - |  |  |  |  | WIKA | R5442
VP05 | VP05-TI-007 | VP05-T-007 | FLD | 107-GM | INDICATOR - TEMPERATURE |  | 034.3 | RESERVED FOR HTF SUPPLY TEMP | PKG: Not Used
VP05 | VP05-TI-008 | VP05-T-008 | FLD | 107-GM | INDICATOR - TEMPERATURE |  | 034.3 | RESERVED FOR HTF RTN TEMP | PKG: Not Used
VP05 | VP05-TI-009 | VP05-T-009 | PKG | 107-GM | INDICATOR - TEMPERATURE | VENDOR PACKAGE | 034.3 | SEAL FLUID TEMPERATURE | N/A | 0 to 100 degC | - | REF | REQ | C |  | - | - |  |  |  |  | WIKA | R5442
WS01 | WS01-HS-001 | WS01-W-001 | LCP | 107-PA | SWITCH - HAND OP. | BOOTH CONTROL PANEL | 030.6 | LF03 WEIGH SCALE | 8990 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS01 | WS01-HS-002 | WS01-W-001 | LCP | 107-PA | SWITCH - HAND OP. | BOOTH CONTROL PANEL | 030.6 | LF03 WEIGH SCALE | 8990 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS01 | WS01-WE-001 | WS01-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | LF03 | 030.6 | LF03 WEIGH SCALE | 8990 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS01 | WS01-WI-001A | WS01-W-001 | PCS | 107-PA | INDICATOR - WEIGH |  |  | LF03 WEIGH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS01 | WS01-WI-001B | WS01-W-001 | LCP | 107-PA | INDICATOR - WEIGH | BOOTH CONTROL PANEL | 030.6 | LF03 WEIGH SCALE | 8990 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS01 | WS01-WIT-001 | WS01-W-001 | CPR | 107-PA | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.6 | LF03 WEIGH SCALE |  | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | UTIL |  |  |  |  | PROFIBUS |  | 01
WS02 | WS02-HS-001 | WS02-W-001 | LCP | 107-PA | SWITCH - HAND OP. | BOOTH CONTROL PANEL | 030.6 | LF03 BENCH SCALE | 8991 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS02 | WS02-HS-002 | WS02-W-001 | LCP | 107-PA | SWITCH - HAND OP. | BOOTH CONTROL PANEL | 030.6 | LF03 BENCH SCALE | 8991 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS02 | WS02-WE-001 | WS02-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | LF03 | 030.6 | LF03 BENCH SCALE | 8991 | 0 to 5 kg | +/- 5g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS02 | WS02-WI-001A | WS02-W-001 | PCS | 107-PA | INDICATOR - WEIGH |  |  | LF03 BENCH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS02 | WS02-WI-001B | WS02-W-001 | LCP | 107-PA | INDICATOR - WEIGH | BOOTH CONTROL PANEL | 030.6 | LF03 BENCH SCALE | 8991 | 0 to 5 kg | +/- 5g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS02 | WS02-WIT-001 | WS02-W-001 | CPR | 107-PA | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.6 | LF03 BENCH SCALE |  | 0 to 5 kg | +/- 5g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | UTIL |  |  |  |  | PROFIBUS |  | 01
WS03 | WS03-HS-001 | WS03-W-001 | LCP | 107-PA | SWITCH - HAND OP. | BOOTH CONTROL PANEL | 030.6 | LF04 WEIGH SCALE | 8992 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS03 | WS03-HS-002 | WS03-W-001 | LCP | 107-PA | SWITCH - HAND OP. | BOOTH CONTROL PANEL | 030.6 | LF04 WEIGH SCALE | 8992 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS03 | WS03-WE-001 | WS03-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | LF04 | 030.6 | LF04 WEIGH SCALE | 8992 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS03 | WS03-WI-001A | WS03-W-001 | PCS | 107-PA | INDICATOR - WEIGH |  |  | LF04 WEIGH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS03 | WS03-WI-001B | WS03-W-001 | LCP | 107-PA | INDICATOR - WEIGH | BOOTH CONTROL PANEL | 030.6 | LF04 WEIGH SCALE | 8992 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS03 | WS03-WIT-001 | WS03-W-001 | CPR | 107-PA | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.6 | LF04 WEIGH SCALE |  | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | UTIL |  |  |  |  | PROFIBUS |  | 01
WS04 | WS04-HS-001 | WS04-W-001 | LCP | 107-PA | SWITCH - HAND OP. | BOOTH CONTROL PANEL | 030.6 | LF04 BENCH SCALE | 8993 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS04 | WS04-HS-002 | WS04-W-001 | LCP | 107-PA | SWITCH - HAND OP. | BOOTH CONTROL PANEL | 030.6 | LF04 BENCH SCALE | 8993 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS04 | WS04-WE-001 | WS04-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | LF04 | 030.6 | LF04 BENCH SCALE | 8993 | 0 to 5 kg | +/- 5g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS04 | WS04-WI-001A | WS04-W-001 | PCS | 107-PA | INDICATOR - WEIGH |  |  | LF04 BENCH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS04 | WS04-WI-001B | WS04-W-001 | LCP | 107-PA | INDICATOR - WEIGH | BOOTH CONTROL PANEL | 030.6 | LF04 BENCH SCALE | 8993 | 0 to 5 kg | +/- 5g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS04 | WS04-WIT-001 | WS04-W-001 | CPR | 107-PA | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.6 | LF04 BENCH SCALE |  | 0 to 5 kg | +/- 5g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | UTIL |  |  |  |  | PROFIBUS |  | 01
WS05 | WS05-HS-001 | WS05-W-001 | LCP | 107-DU | SWITCH - HAND OP. | LOCAL PANEL | 030.1 | PD01 WEIGH SCALE | 8994 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS05 | WS05-HS-002 | WS05-W-001 | LCP | 107-DU | SWITCH - HAND OP. | LOCAL PANEL | 030.1 | PD01 WEIGH SCALE | 8994 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS05 | WS05-WE-001 | WS05-W-001 | FLD | 107-DU | WEIGH SCALE - LOAD CELLS | MOBILE | 030.1 | MOBILE SCALE | 8994 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS05 | WS05-WI-001A | WS05-W-001 | PCS | 107-DU | INDICATOR - WEIGH | MOBILE |  | MOBILE SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS05 | WS05-WI-001B | WS05-W-001 | LCP | 107-DU | INDICATOR - WEIGH | MOBILE | 030.1 | MOBILE SCALE | 8994 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS05 | WS05-WIT-001 | WS05-W-001 | CPR | 107-DU | TRANSMITTER - WEIGH SCALE | MOBILE | 030.1 | MOBILE SCALE |  | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | GP1 |  |  |  |  | PROFIBUS |  | 01
WS06 | WS06-HS-001 | WS06-W-001 | LCP | 107-CU | SWITCH - HAND OP. | LOCAL PANEL | 030.2 | FD03 WEIGH SCALE | 8995 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS06 | WS06-HS-002 | WS06-W-001 | LCP | 107-CU | SWITCH - HAND OP. | LOCAL PANEL | 030.2 | FD03 WEIGH SCALE | 8995 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS06 | WS06-WE-001 | WS06-W-001 | FLD | 107-CU | WEIGH SCALE - LOAD CELLS | UNDER FD03 GLOVEBOX | 030.2 | FD03 WEIGH SCALE | 8995 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS06 | WS06-WI-001A | WS06-W-001 | PCS | 107-CU | INDICATOR - WEIGH |  |  | FD03 WEIGH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS06 | WS06-WI-001B | WS06-W-001 | LCP | 107-CU | INDICATOR - WEIGH | LOCAL PANEL | 030.2 | FD03 WEIGH SCALE | 8995 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS06 | WS06-WIT-001 | WS06-W-001 | CPR | 107-CU | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.2 | FD03 WEIGH SCALE |  | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | GP2 |  |  |  |  | PROFIBUS |  | 01
WS07 | WS07-HS-001 | WS07-W-001 | LCP | 107-BV | SWITCH - HAND OP. | LOCAL PANEL | 030.3 | LF01 WEIGH SCALE | 8996 | - | - | OPS | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | REMOVED FROM SERVICE eCC15027 |  | 22
WS07 | WS07-HS-002 | WS07-W-001 | LCP | 107-BV | SWITCH - HAND OP. | LOCAL PANEL | 030.3 | LF01 WEIGH SCALE | 8996 | - | - | OPS | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | REMOVED FROM SERVICE eCC15027 |  | 22
WS07 | WS07-WE-001 | WS07-W-001 | FLD | 107-BV | WEIGH SCALE - LOAD CELLS | LF01 | 030.3 | LF01 WEIGH SCALE | 8996 | 0 to 100 kg | +/- 50g | OPS | 12 | C | SER | I.S |  |  |  | 0 | [5 empty] | REMOVED FROM SERVICE eCC15027 |  | 22
WS07 | WS07-WI-001A | WS07-W-001 | PCS | 107-BV | INDICATOR - WEIGH |  |  | LF01 WEIGH SCALE | [11 empty] | 0 | [5 empty] | REMOVED FROM SERVICE eCC15027 |  | 22
WS07 | WS07-WI-001B | WS07-W-001 | LCP | 107-BV | INDICATOR - WEIGH | LOCAL PANEL | 030.3 | LF01 WEIGH SCALE | 8996 | 0 to 100 kg | +/- 50g | OPS | 12 | C | SER | I.S |  |  |  | 0 | [5 empty] | REMOVED FROM SERVICE eCC15027 |  | 22
WS07 | WS07-WIT-001 | WS07-W-001 | CPR | 107-BV | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.3 | LF01 WEIGH SCALE |  | 0 to 100 kg | +/- 50g | OPS | 12 | C | SER | N.I.S | * |  |  | 51 | FG1 |  |  |  |  | REMOVED FROM SERVICE eCC15027 |  | 22
WS08 | WS08-HS-001 | WS08-W-001 | LCP | 107-EV | SWITCH - HAND OP. | LOCAL PANEL | 030.4 | FD02 WEIGH SCALE | 8997 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS08 | WS08-HS-002 | WS08-W-001 | LCP | 107-EV | SWITCH - HAND OP. | LOCAL PANEL | 030.4 | FD02 WEIGH SCALE | 8997 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS08 | WS08-WE-001 | WS08-W-001 | FLD | 107-EV | WEIGH SCALE - LOAD CELLS | UNDER FD02 GLOVEBOX | 030.4 | FD02 WEIGH SCALE | 8997 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS08 | WS08-WI-001A | WS08-W-001 | PCS | 107-EV | INDICATOR - WEIGH |  |  | FD02 WEIGH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS08 | WS08-WI-001B | WS08-W-001 | LCP | 107-EV | INDICATOR - WEIGH | LOCAL PANEL | 030.4 | FD02 WEIGH SCALE | 8997 | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS08 | WS08-WIT-001 | WS08-W-001 | CPR | 107-EV | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.4 | FD02 WEIGH SCALE |  | 0 to 100 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | C1 |  |  |  |  | PROFIBUS |  | 01
WS09 | WS09-HS-001 | WS09-W-001 | LCP | 107-BS | SWITCH - HAND OP. | LOCAL PANEL | 030.1 | TB01 WEIGH SCALE | 8998 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS09 | WS09-HS-002 | WS09-W-001 | LCP | 107-BS | SWITCH - HAND OP. | LOCAL PANEL | 030.1 | TB01 WEIGH SCALE | 8998 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS09 | WS09-WE-001 | WS09-W-001 | FLD | 107-BS | WEIGH SCALE - LOAD CELLS | TB01 | 030.1 | TB01 WEIGH SCALE | 8998 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS09 | WS09-WI-001A | WS09-W-001 | PCS | 107-BS | INDICATOR - WEIGH |  |  | TB01 WEIGH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS09 | WS09-WI-001B | WS09-W-001 | LCP | 107-BS | INDICATOR - WEIGH | LOCAL PANEL | 030.1 | TB01 WEIGH SCALE | 8998 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS09 | WS09-WIT-001 | WS09-W-001 | CPR | 107-BS | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.1 | TB01 WEIGH SCALE |  | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | GP1 |  |  |  |  | PROFIBUS |  | 01
WS10 | WS10-HS-001 | WS10-W-001 | LCP | 107-CS | SWITCH - HAND OP. | LOCAL PANEL | 030.2 | TB02 WEIGH SCALE | 8999 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS10 | WS10-HS-002 | WS10-W-001 | LCP | 107-CS | SWITCH - HAND OP. | LOCAL PANEL | 030.2 | TB02 WEIGH SCALE | 8999 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS10 | WS10-WE-001 | WS10-W-001 | FLD | 107-CS | WEIGH SCALE - LOAD CELLS | TB02 | 030.2 | TB02 WEIGH SCALE | 8999 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS10 | WS10-WI-001A | WS10-W-001 | PCS | 107-CS | INDICATOR - WEIGH |  |  | TB02 WEIGH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS10 | WS10-WI-001B | WS10-W-001 | LCP | 107-CS | INDICATOR - WEIGH | LOCAL PANEL | 030.2 | TB02 WEIGH SCALE | 8999 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS10 | WS10-WIT-001 | WS10-W-001 | CPR | 107-CS | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.2 | TB02 WEIGH SCALE |  | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | GP2 |  |  |  |  | PROFIBUS |  | 01
WS11 | WS11-HS-001 | WS11-W-001 | LCP | 107-DT | SWITCH - HAND OP. | LOCAL PANEL | 030.3 | TB03 WEIGH SCALE | 9000 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS11 | WS11-HS-002 | WS11-W-001 | LCP | 107-DT | SWITCH - HAND OP. | LOCAL PANEL | 030.3 | TB03 WEIGH SCALE | 9000 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS11 | WS11-WE-001 | WS11-W-001 | FLD | 107-DT | WEIGH SCALE - LOAD CELLS | TB03 | 030.3 | TB03 WEIGH SCALE | 9000 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS11 | WS11-WI-001A | WS11-W-001 | PCS | 107-DT | INDICATOR - WEIGH |  |  | TB03 WEIGH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS11 | WS11-WI-001B | WS11-W-001 | LCP | 107-DT | INDICATOR - WEIGH | LOCAL PANEL | 030.3 | TB03 WEIGH SCALE | 9000 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS11 | WS11-WIT-001 | WS11-W-001 | CPR | 107-DT | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.3 | TB03 WEIGH SCALE |  | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | FG1 |  |  |  |  | PROFIBUS |  | 01
WS12 | WS12-HS-001 | WS12-W-001 | LCP | 107-ET | SWITCH - HAND OP. | LOCAL PANEL | 030.4 | TB04 WEIGH SCALE | 9001 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS12 | WS12-HS-002 | WS12-W-001 | LCP | 107-ET | SWITCH - HAND OP. | LOCAL PANEL | 030.4 | TB04 WEIGH SCALE | 9001 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS12 | WS12-WE-001 | WS12-W-001 | FLD | 107-ET | WEIGH SCALE - LOAD CELLS | TB04 | 030.4 | TB04 WEIGH SCALE | 9001 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS12 | WS12-WI-001A | WS12-W-001 | PCS | 107-ET | INDICATOR - WEIGH |  |  | TB04 WEIGH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS12 | WS12-WI-001B | WS12-W-001 | LCP | 107-ET | INDICATOR - WEIGH | LOCAL PANEL | 030.4 | TB04 WEIGH SCALE | 9001 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS12 | WS12-WIT-001 | WS12-W-001 | CPR | 107-ET | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.4 | TB04 WEIGH SCALE |  | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | C1 |  |  |  |  | PROFIBUS |  | 01
WS13 | WS13-HS-001 | WS13-W-001 | LCP | 107-FA | SWITCH - HAND OP. | LOCAL PANEL | 030.5 | EH01 BENCH SCALE |  | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS13 | WS13-HS-002 | WS13-W-001 | LCP | 107-FA | SWITCH - HAND OP. | LOCAL PANEL | 030.5 | EH01 BENCH SCALE |  | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS13 | WS13-WE-001 | WS13-W-001 | FLD | 107-FA | WEIGH SCALE - LOAD CELLS | EH01 | 030.5 | EH01 BENCH SCALE | 9002 | 0 to 5 kg | +/- 5g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS13 | WS13-WI-001A | WS13-W-001 | PCS | 107-FA | INDICATOR - WEIGH | PCS | 030.5 | EH01 BENCH SCALE | PKG: 9002; REF: GxP |  |  | 0 | [7 empty] | 01
WS13 | WS13-WI-001B | WS13-W-001 | LCP | 107-FA | INDICATOR - WEIGH | LOCAL PANEL | 030.5 | EH01 BENCH SCALE | 9002 | 0 to 5 kg | +/- 5g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS13 | WS13-WIT-001 | WS13-W-001 | CPR | 107-FA | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.5 | EH01 BENCH SCALE | 9002 | 0 to 5 kg | +/- 5g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | HYD |  |  |  |  | PROFIBUS |  | 01
WS14 | WS14-HS-001 | WS14-W-001 | LCP | 107-FA | SWITCH - HAND OP. | LOCAL PANEL | 030.5 | HYDROG WEIGH SCALE |  | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS14 | WS14-HS-002 | WS14-W-001 | LCP | 107-FA | SWITCH - HAND OP. | LOCAL PANEL | 030.5 | HYDROG WEIGH SCALE |  | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS14 | WS14-WE-001 | WS14-W-001 | FLD | 107-FA | WEIGH SCALE - LOAD CELLS | HYDROG ROOM | 030.5 | HYDROG WEIGH SCALE | 9003 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS14 | WS14-WI-001A | WS14-W-001 | PCS | 107-FA | INDICATOR - WEIGH | PCS | 030.5 | HYDROG WEIGH SCALE | PKG: 9003; REF: GxP |  |  | 0 | [7 empty] | 01
WS14 | WS14-WI-001B | WS14-W-001 | LCP | 107-FA | WEIGH SCALE - LOAD CELLS | LOCAL PANEL | 030.5 | HYDROG WEIGH SCALE | 9003 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS14 | WS14-WIT-001 | WS14-W-001 | CPR | 107-FA | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.5 | HYDROG WEIGH SCALE | 9003 | 0 to 400 kg | +/- 50g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | HYD |  |  |  |  | PROFIBUS |  | 01
WS16 | WS16-WI-001 | WS16-W-001 | FLD | 107-PA | INDICATOR - WEIGH | ADJ TO EH02 | 030.4 | PORTABLE WEIGH SCALE | -: +/- 5g; REF: GxP; REQ: 12; F: C; Ref: SER |  |  | 0 | [5 empty] | BY PFIZER |  | 01
WS16 | WS18-HS-001 | WS18-W-001 | LCP | 107-PA | SWITCH - HAND OP. | LOCAL PANEL | 030.4 | EH02 BENCH SCALE | 9004 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | SET ZERO |  | 01
WS16 | WS18-HS-002 | WS18-W-001 | LCP | 107-PA | SWITCH - HAND OP. | LOCAL PANEL | 030.4 | EH02 BENCH SCALE | 9004 | - | - | GxP | 12 | F | SER | I.S |  |  |  | 0 | [5 empty] | ACQUIRE/CLEAR TARE |  | 01
WS18 | WS18-WE-001 | WS18-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | EH02 | 030.4 | EH02 BENCH SCALE | 9004 | 0 to 10 kg | +/- 5g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS18 | WS18-WI-001A | WS18-W-001 | PCS | 107-PA | INDICATOR - WEIGH |  |  | EH02 BENCH SCALE | REF: GxP |  |  | 0 | [7 empty] | 01
WS18 | WS18-WI-001B | WS18-W-001 | LCP | 107-PA | INDICATOR - WEIGH | LOCAL PANEL | 030.4 | EH02 BENCH SCALE | 9004 | 0 to 10 kg | +/- 5g | GxP | 12 | C | SER | I.S |  |  |  | 0 | [7 empty] | 01
WS18 | WS18-WIT-001 | WS18-W-001 | CPR | 107-PA | TRANSMITTER - WEIGH SCALE | WEIGH SYSTEM PANEL | 030.4 | EH02 BENCH SCALE |  | 0 to 10 kg | +/- 5g | GxP | 12 | C | SER | N.I.S | * |  |  | 51 | UTIL |  |  |  |  | PROFIBUS |  | 01
WS19 | WS19-WE-001 | WS19-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 600 kg | +/- 60g | GxP | 12 | C | SER | I.S | [11 empty] | 01
WS19 | WS19-WI-001 | WS19-W-001 | FLD | 107-PA | INDICATOR - WEIGH | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 600 kg | +/- 60g | GxP | 12 | C | SER | I.S | [11 empty] | 01
WS20 | WS20-WE-001 | WS20-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 60 kg | +/- 6g | GxP | 12 | C | SER | I.S | [11 empty] | 01
WS20 | WS20-WI-001 | WS20-W-001 | FLD | 107-PA | INDICATOR - WEIGH | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 60 kg | +/- 6g | GxP | 12 | C | SER | I.S | [11 empty] | 01
WS21 | WS21-WE-001 | WS21-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 1000 kg | +/- 100g | GxP | 12 | C | SER | I.S | [11 empty] | 01
WS21 | WS21-WI-001 | WS21-W-001 | FLD | 107-PA | INDICATOR - WEIGH | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 1000 kg | +/- 100g | GxP | 12 | C | SER | I.S | [11 empty] | 01
WS22 | WS22-WE-001 | WS22-W-001 | FLD | N/A | WEIGH SCALE - LOAD CELLS | IPC LAB | 030.7 | PORTABLE SCALE | 10554 | 0 to 2.2 kg | +/- 2g | GxP | 12 | C | SER | [12 empty] | 01
WS22 | WS22-WI-001 | WS22-W-001 | FLD | N/A | INDICATOR - WEIGH | IPC LAB | 030.7 | PORTABLE SCALE | 10554 | 0 to 2.2 kg | +/- 02g | GxP | 12 | C | SER | [12 empty] | 01
WS23 | WS23-WE-001 | WS23-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 15 kg | +/- 1.5g | GxP | 12 | C | SER | [12 empty] | 01
WS23 | WS23-WI-001 | WS23-W-001 | FLD | 107-PA | INDICATOR - WEIGH | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 15 kg | +/- 1.5g | GxP | 12 | C | SER | [12 empty] | 01
WS24 | WS24-WE-001 | WS24-W-001 | FLD | 107-PA | WEIGH SCALE - LOAD CELLS | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 600 kg | +/- 60g | GxP | 12 | C | SER | I.S | [11 empty] | 01
WS24 | WS24-WI-001 | WS24-W-001 | FLD | 107-PA | INDICATOR - WEIGH | SOLIDS DISPENSARY | 030.6 | PORTABLE SCALE | 10554 | 0 to 600 kg | +/- 60g | GxP | 12 | C | SER | I.S | [11 empty] | 01
WS25 | WS25-WE-001 | WS25-W-001 | FLD | 107-BV | WEIGH SCALE - LOAD CELLS | LF01 | 030.1 | MOBILE SCALE | 10554 | 60 to 150 kg | 0.033% | GxP | 12 | C | SER | I.S | [5 empty] | AVERY BERKELL | RDREX |  |  |  |  | 01
WS25 | WS25-WI-001 | WS25-W-001 | FLD | 107-BV | INDICATOR - WEIGH | LF01 | 030.1 | MOBILE SCALE | 10554 | 60 to 150 kg | 0.033% | GxP | 12 | C | SER | I.S | [5 empty] | AVERY BERKELL | RDREX |  |  |  |  | 01
WS26 | WS26-WE-001 | WS26-W-001 | FLD | N/A | WEIGH SCALE - LOAD CELLS | MOBILE | 030.1 | MOBILE SCALE | -: 2 to 300kg; -: +/- 2Kg; REF: REF; REQ: By Request |  |  |  |  | AVERY BERKELL | L117EX-ATEX IND
WS26 | WS26-WI-001 | WS26-W-001 | FLD | N/A | INDICATOR - WEIGH | MOBILE | 030.1 | MOBILE SCALE | -: 2 to 300kg; -: +/- 2Kg; REF: REF; REQ: By Request |  |  |  |  | DINI ARGEO | DFW ATEX 2GD
WS27 | WS27-WE-001 | WS27-W-001 | FLD | N/A | WEIGH SCALE - LOAD CELLS | MOBILE | 030.1 | MOBILE SCALE | -: 2 to 300kg; -: +/- 2Kg; REF: GxP; REQ: 12 |  |  |  |  | AVERY BERKELL | L117EX-ATEX IND
WS27 | WS27-WI-001 | WS27-W-001 | FLD | N/A | INDICATOR - WEIGH | MOBILE | 030.1 | MOBILE SCALE | -: 2 to 300kg; -: +/- 2Kg; REF: GxP; REQ: 12 |  |  |  |  | DINI ARGEO | DFW ATEX 2GD
WS29 | WS29-WE-001 | WS29-W-001 | FLD | N/A | WEIGH SCALE - LOAD CELLS | MOBILE | 030.1 | MOBILE SCALE | -: 20 to 2000kg; -: +/- 8Kg; REF: GxP; REQ: 12
WS29 | WS29-WI-001 | WS29-W-001 | FLD | N/A | INDICATOR - WEIGH | MOBILE | 030.1 | MOBILE SCALE | -: 20 to 2000kg; -: +/- 8Kg; REF: GxP; REQ: 12
WS30 | WS30-WE-001 | WS30-W-001 | FLD | N/A | WEIGH SCALE - LOAD CELLS | MOBILE | 030.1 | MOBILE SCALE | -: 20 to 2000kg; -: +/- 8Kg; REF: GxP; REQ: 12
WS30 | WS30-WI-001 | WS30-W-001 | FLD | N/A | INDICATOR - WEIGH | MOBILE | 030.1 | MOBILE SCALE | -: 20 to 2000kg; -: +/- 8Kg; REF: GxP; REQ: 12
WS31 | WS31-WE-001 | WS31-W-001 | FLD | N/A | WEIGH SCALE - LOAD CELLS | MOBILE | 030.1 | MOBILE SCALE | -: 0.4 to 60kg; -: +/- 0.4Kg; REF: GxP; REQ: 12
WS31 | WS31-WI-001 | WS31-W-001 | FLD | N/A | INDICATOR - WEIGH | MOBILE | 030.1 | MOBILE SCALE | -: 0.4 to 60kg; -: +/- 0.4Kg; REF: GxP; REQ: 12
| SAN-902-WIP-H-001 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 5degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-H-002 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 5degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-H-003 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 5degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-HAH-001 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 5degC; REF: REF; REQ: By Request |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-HAH-002 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 5degC; REF: REF; REQ: By Request |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-HAH-003 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 5degC; REF: REF; REQ: By Request |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-HAL-001 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 5degC; REF: REF; REQ: By Request |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-HAL-002 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 5degC; REF: REF; REQ: By Request |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-HAL-003 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 5degC; REF: REF; REQ: By Request |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-T-001 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 2degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-T-002 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 2degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-T-003 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 2degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-TAH-001 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 2degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-TAH-002 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 2degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-TAH-003 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 2degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-TAL-001 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 2degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-TAL-002 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 2degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
| SAN-902-WIP-TAL-003 |  | FLD | 902-012-003-000-00001 | TEMPERATURE/HUMIDITY LOGGER | PG.13 | 191 | TEMPERATURE AND HUMIDITY | PKG: L16222; -: 0-100 oC; -: +/- 2degC; REF: GxP; REQ: 6 |  |  |  |  | Saveris | Saveris 2 H2 | [5 empty] | 11
Note on K3547: dillrussellc: To be user configurable depending upon product being processed
Note on B7941: Jefferies, Keith: Duplicate tag
Note on B10240: Jefferies, Keith: Duplicate tag
Note on B10296: Jefferies, Keith: Duplicate tag

## Rev. history
Instrument Schedule Revision History
Revision Number | Summary of Changes | Initials | Date
10 | SWT09-PSV-001 added, moved to B902 from B901 (originally KL40) MCR01 Thermocouples supplier changed | DB | 2009-09-29
11 | Additional MCR01 Thermocouples supplier changed for additional thermocouples eCC12029 | DB | 2009-11-04
12 | Addition of MIR Base valves under B902-1488 | DB | 2010-01-05
13 | Further additional information for MIR Basevalve temperature probes | DB | 2010-01-11
14 | Addition of MCR01-PSV-006 following B902-1495 | DB | 2010-01-26
15 | Addition of MPH02 instruments following B902-1490 | DB | 2010-02-15
16 | MIR02 instruments added under B902-1481 | SF | 2010-02-22
17 | Final completion of information for MIR base valves added under B901-1488 | DB | 2010-03-24
18 | Correction for MPH02, Pressure Transmitters changed to Pressure Switches B902-1490 | DB | 2010-04-15
19 | Updated to include HTF Energy Savings changes as per B902-1505 | DB | 2010-07-22
20 | Updated to include SC03 Oxygen Monitor, pH Meter and Flow Meter as per B902-1509 and B902-1507 | DB | 2010-08-03
21 | Updated to show SP01-PRV-001 removed under B902-1496 | DB | 2010-09-22
22 | Updated to remove WS07 instruments eCC15027 and updated to removed MNF04 instruments eCC15028 | DB | 2010-10-28
23 | Updated to include all new instruments for the carbon drum project | DB | 2010-11-09
24 | Updated to include all new instruments for the hastelloy Cuno Filter MCF13 | SF | 2010-12-06
25 | Updated to include additional MIR base valve MIR-CV-001C B902-1525 | DB | 2011-01-24
26 | Updated to change R23-TT-009's calibration frequency, item is now By Request | DB | 2011-03-30
27 | Updated to include instrument corrections and new loop numbers for the purified water system instruments | DB | 2011-04-07
28 | Updated following eCC's 16722 and 16702 to change instrument category and frequency for VACNTH/VACSTH PT's and MI01-ZS-004 | DB | 2011-06-08
29 | Updated following eCC's 16078, 16079, 16080, 16081 change of pressure indicator models | DB | 2011-06-29
30 | Updated following eCC's 17634, 17635, 17686 change of instrument category and frequency | DB | 2011-07-05
31 | Updated following eCC17685 change of instrument category and frequency | DB | 2011-07-12
32 | Updated following eCC17643 change of instrument category and frequency | DB | 2011-07-25
33 | Updated following eCC18299 change of instrument category and frequency | DB | 2011-08-10
34 | Updated following eCC18439 and eCC184467 change of instrument category and frequency | DB | 2011-09-19
35 | Updated to include SC03-CV-010 and SC03-FI-004 for SC03 nitrogen purge | DB | 2011-10-06
36 | SC03-CV-010 items changed to SC03-CV-008A as per change control B902-1531 | DB | 2011-11-15
37 | Updated following eCC21373 for the completion of the purified water CAT Assessment | DB | 2012-05-16
38 | Updated LR1-FAL-005 model number following eCC22052 | DB | 2012-06-18
39 | Updated ET02-LSH-002 model number following B902-1535 | DB | 2012-07-31
40 | Updated R14-FI-001, R16-FI-001 and R18-FI-001 to FIT's | DB | 2012-10-23
41 | Updated R06-TT-003 to reflect the updated model being installed under CC554671 | DB | 2013-03-18
42 | Updated to include new transmitters FD02-TT-008, FD02-TT-009 and FD02-FT-002 under eCC644675 | DB | 2013-05-29
43 | Addition of MHT08 and MHT09 PI's and BD's | DB | 2013-07-11
44 | Updated following Compressor change control eCC619630 | DB | 2013-07-22
45 | R20-PSV-014 updated to relfect the pressure setting change from 10 barg to 9 barg under CC560285 | DB | 2013-11-07
46 | Updated following CC791196 to change R15-LT-001 model and manufacturer. Also updated following CC752023 to change LR1-PIT-003 model and manufacturer. | DB | 2014-04-14
47 | HTF01-LIT-001 and LIT-002 transmitters replaced following change control 743115. NS01-FT-001 updated following change control 874162. | DB | 2014-07-22
48 | Addition of PW01-AIT-009 and PW01-AIT-010 as per change control eCC871317 | DS | 2014-10-20
49 | Change of cal frequency for GP1MFD02-PIC-002 and GP1MFD02-PIC-033, changed to on request calibration following change control 970593 and to include convective drying changes | DS | 2015-02-03
50 | Removed from Use all MCR01 instruments under CC1316722 | DS | 2015-11-11
51&52 | Updated following changes from QTS CC's 1494928, 1496377, 1496474, 1497376 | DS | 2016-06-13
53 | Updated to include new hastelloy base valves HAST-CV-001 and HAST-CV-002 | DS | 2018-04-17
54 | Updated to include new filter dryer FD05 and VP05 and removal of MES03 | DS | 2018-05-16
55 | Updated to correct duplicate tag no R23-TI-009, TI-009 for the R23-TP1 seal pot temperature changed to TI-010 | DS | 2018-07-04
56 | Updated to reflect installation of new agitator and sampling system for R23 | DS | 2018-11-26
57 | Updated to reflect the current model number for replaced PIT-002's on reactors R01-R22 | DS | 2019-10-03
58 | Updated to include purified water meter PWF01 | DS | 2020-06-19
59 (GDMS v8.0) | Corrected revision history. Updated SHE designation to align with PDF Process Hazard Review (ABB Report ref 300126185-050 rev A1). General update for PCS upgrade project. IS Calculation cross reference added. MM03 Instruments added. | DS | 2020-09-15
60 (GDMS v9.0) | Updated to include ST03. Clarified ST01 tags impacted by ST03 installation. Corrected MM03 line numbers. | SA/KJ | 2020-09-24
61 (GDMS v10.0) | TI702-SP IS calculation reference added for Rev 60 ST03 instruments Added TD02-RO-003 and TB01-PT-007 | JB/KJ | 2020-12-10
62 (GDMS v11.0) | Added TB01-PI-007. Corrected line ID for MM03-F-001. Added CW-RO-003. Added VP05-RO-001. Added TB0x-P-007 for TB02/3/4. Updated Instrumentation for MM03. Added WIP store temperature and humidity logging instruments. | JB/KJ | 2021-10-01
63 (GDMS v12.0) | Updated to include new weigh scale instruments for WS31 and B287-WS01 | DS | 2021-10-05
64 (GDMS v13.0) | Updated to include the revision history for v12.0, data omitted at the time | DS | 2021-10-05
65 (GDMS v14.0) | Corrected P&ID No. for MM03 Instruments. Renamed valve R23-CV31B to R23-CV32B. | KJ | 2021-10-22
66 (GDMS v15) | Allocated tags for Mobile PW Flow Meters PW-FI-001, PW-FI-002, PW-FI-003, PW-FI-004 Added MEA01 Instruments to schedule Added MINST-AT-001 & MINST-YS-001 to schedule Added MPH01-P-001 to schedule | KJ | 2022-03-16
67 (GDMS v16) | Added ST01-PSV-009/010/011, ST03-CV04/05 Changed ST03-Y-002 Fill Permissive to Earth Bonding Changed ST03-L-003 Low Level to High Level Added MCF20-PI-001 & MCF20-PI-002 Corrected tags for Vac Distribution (VDIS) Changed VACSTH & VACNTH Hand Valves to CV's Updated model number for ST01-FIT-001 Added additional Mobile Interface Detector Signals Added Mobile Purified Water Flowmeter PWF05 Added MM04 Instrumentation.
68 (GDMS v17) | Added/corrected MM04 Instrumentation as part of detailed design. Corrected P&ID cross reference for MHT14 instruments. | KJ | 2023-05-03
69 (GDMS v18) | Added T-2218 Pressure transmitters Added remarks for MINST-YS-002, MINST-YS-003 & MINST-YS-004 | KJ | 2023-10-04
70 (GDMS v19) | Added T-2207 Instruments (MHT15) and updated to reflect WS05 is now a mobile scale | KJ/DS | 2023-11-24
71 (GDMS v20) | Added instruments MHT15-P-004 & MHT15-P-005. Added instruments for MS01 Mobile Sifter. Updated instrument details for TT01-L-001, TT01-L-002, LR1-F-002, LR1-F-003, LR1-F-004 and TB03-F-001 | KJ/DS | 2024-05-28
v0.0 | Transition to Asymchem - Front sheet updated and revision changed to v0.0 prior to upload to ZenQMS document management system. | KJ | 2025-11-19

## CAT #
Instrument Criticality Assessment | Unit | Version
SW/CAT/902/061 | R18 | 1
SW/CAT/902/148 | CV-001A,Band C | 2
SW/CAT/902/115 | R17 | 1
SW/CAT/902/189 | HAST-CV-001& CV-002 | 2
SW/CAT/902/059 | R14 | 1
SW/CAT/902/052 | R06 | 3
SW/CAT/902/009 & 010 | CT01 & CT03 | 1
SW/CAT/902/104 | Pan Dryer, PD01 | 0.2
SW/CAT/902/113 | R13 | 1
SW/CAT/902/114 | R15 | 1
SW/CAT/902/066 | R23 | 0.7
SW/CAT/902/050 | R04 | 3
SW/CAT/902/168 | TD02 | 1
SW/CAT/902/RU4 | RU4 | 1
SW/CAT/902/036,038,&172 | DVP01,DVP03,DVP04 & DVP05 | 2
SW/CAT/902/034.3 | VP05 | 0.2
SW/CAT/902/138 | SWT01-09 | 1
SW/CAT/902/075 | MES04 | 1
SW/CAT/902/103 | FD03 | 2
SW/CAT/902/011 | ET01,TT01 & TT02 | 1
SW/CAT/902/139 | MCF01-MCF18 | 1
SW/CAT/902 | Assessment philosophy | 1
SW/CAT/902/187 | FD05 | 0.4 | Check on MES03 for GxP (No GxP on unit )
SW/CAT/902/166 | MFD02 | 0.2 | Check on MES01 for GxP (No GxP on unit )
SW/CAT/902/137 | LR1 | 0.1
SW/CAT/902/ST01 & ST02 | ST01 & ST02 | 1
SW/CAT/902/0041.0 | Purified Water | 1
SW/CAT/902/CMP01 & CMP02 | CMP01 & CMP02 | 1
SW/CAT/902/FQIC-001 | C1,FG01,GP01 & GP02 | 1
SW/CAT/902/008.4 | SC04 | 1
SW/CAT/902/008.3 | SC03 | 1
SW/CAT/902/167 | FD04 | 2
SW/CAT/902/174 | MCE01 | 1
SW/CAT/902/087 | MNF | 1
SW/CAT/902/088 | MPF01 & MPF02 | 1
SW/CAT/902/144 | MDH01 & MDH02, DHC01 | 1
SW/CAT/902/065 | R22 | 2
SW/CAT/902/060 | R16 | 1
SW/CAT/902/040 | HOT HTF | 1
SW/CAT/902/072 &169 & 171 | MES01 | 1
SW/CAT/902/Reactor TE-006 | Gas temperture TE-006 | 1
SW/CAT/902/029 | LF01,LF03& LF04 TB01-04 | 2
SW/CAT/902/012 | ET02 & TT03 | 2
SW/CAT/902/171.4 | FD05-HC1 | 1
SW/CAT/902/102 | TD01 | 1
SW/CAT/902/106 | FD02 | 2
SW/CAT/902/062 | R19 | 2
SW/CAT/902/053 | R07 | 2
SW/CAT/902/008.1 & 008.2 | SC01 & SC02 | 2
SW/CAT/902/056 | R10 | 2
SW/CAT/902/025 | HVAC | 2
SW/CAT/902/063 | R20 | 1
SW/CAT/902/040 | Cold HTF | 1
SW/CAT/902/047 | R01 | 2
SW/CAT/902/155 | MI01 | 1
SW/CAT/902/107 | MCD01 | 1
SW/CAT/902/048 | R02 | 2
SW/CAT/902/045 | CD01 & CD02 | 1
SW/CAT/902/034,035 & 037 | DVP02,VP02,VP03 & VP04 | 1
SW/CAT/902/064 | R21 | 2
SW/CAT/902/044 | Process Water | 1
SW/CAT/902/057 | R11 | 1
SW/CAT/902/054 | R08 | 2
SW/CAT/902/049 | R03 | 2
SW/CAT/902/092,094 | Mobile Head Tanks | 2
SW/CAT/902/058 | R12 | 2
SW/CAT/902/055 | R09 | 2
SW/CAT/902/051 | R05 | 2
SW/CAT/902/040 | Tempered HTF | 1
SW/CAT/902/041-FQIC's | PW Meters C1,FG1,GP1 & GP2 | 1
SW/CAT/902/022 | CR01 condensate return | 1
SW/CAT/902/Reactor TT-004 | Re-categorising TT-004 | 1
SW/CAT/902/176.2 | mobile pH Probe Skid MPH 02 | 1
SW/CAT/902/
SW/CAT/902/
SW/CAT/902/