## Version
Date | Version | Comments
2026-01-12 | v0.0 | Original

## PLC IO Schedule
IO COUNT |  | 83
Prefix | Tag | Number | Suffix | Tag No | Loop No | PLC Descriptor | PLC I/O Tag | I/O Type | Elect Class | Field / System Power | Field (I.S.) / PLC Cabinet Marshalling | Rack | Slot | Channel | Interface Terminal ID | Unit Alarm Group | PLC Tag | Faceplate Description | Description | PID Loop Gain | PID Loop Reset | PID Loop Rate | Action Dir/Rev | Eng Units Range - Min | Eng Units Range - Max | Eng Units | Alarm State | Zero State Descriptor | One State Descriptor | Alarm Group | HiHi | Hi | Lo | LoLo | SP Dev | ROC(+) | ROC(-) | Slew | Failure | Comments | Revision Description | Revision
R24 | CY | 1 |  | R24-CY-001 | R24-C-001 | SOLENOID VALVE |  | DO | I.S. |  | Field |  |  |  |  | R24 | R24-CV01 | BT03 Hydrogen Supply Valve | SOLENOID VALVE | [8 empty] | CLOSE | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | ZSC | 1 |  | R24-ZSC-001 | R24-C-001 | PROXIMITY SENSOR - CLOSED |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV01 | BT03 Hydrogen Supply Valve | PROXIMITY SENSOR - CLOSED | [8 empty] | NOT CLOSED | CLOSED | R24 | - | - | - | - | - | - | - | -
R24 | ZSO | 1 |  | R24-ZSO-001 | R24-C-001 | PROXIMITY SENSOR - OPEN |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV01 | BT03 Hydrogen Supply Valve | PROXIMITY SENSOR - OPEN | [8 empty] | NOT OPEN | OPEN | R24 | - | - | - | - | - | - | - | -
R25 | CY | 3 |  | R24-CY-003 | R24-C-003 | SOLENOID VALVE |  | DO | I.S. |  | Field |  |  |  |  | R24 | R24-CV03 | BT03 Outlet Isolation Valve | SOLENOID VALVE | [8 empty] | CLOSE | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | CY | 4 |  | R24-CY-004 | R24-C-004 | SOLENOID VALVE |  | DO |  |  | PLC/ Field |  |  |  |  | R24 | R24-CV04 | BT04 Inlet Valve | SOLENOID VALVE | [8 empty] | CLOSE | OPEN | R24 | - | - | - | - | - | - | - | - |  | Final Element for HW Safety Interlock
R24 | ZSC | 4 |  | R24-ZSC-004 | R24-C-004 | PROXIMITY SENSOR - CLOSED |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV04 | BT04 Inlet Valve | PROXIMITY SENSOR - CLOSED | [8 empty] | NOT CLOSED | CLOSED | R24 | - | - | - | - | - | - | - | -
R24 | ZSO | 4 |  | R24-ZSO-004 | R24-C-004 | PROXIMITY SENSOR - OPEN |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV04 | BT04 Inlet Valve | PROXIMITY SENSOR - OPEN | [8 empty] | NOT OPEN | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | CY | 5 |  | R24-CY-005 | R24-C-005 | SOLENOID VALVE |  | DO | I.S. |  | Field |  |  |  |  | R24 | R24-CV05 | BT04 Outlet Valve | SOLENOID VALVE | [8 empty] | CLOSE | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | ZSC | 5 |  | R24-ZSC-005 | R24-C-005 | PROXIMITY SENSOR - CLOSED |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV05 | BT04 Outlet Valve | PROXIMITY SENSOR - CLOSED | [8 empty] | NOT CLOSED | CLOSED | R24 | - | - | - | - | - | - | - | -
R24 | ZSO | 5 |  | R24-ZSO-005 | R24-C-005 | PROXIMITY SENSOR - OPEN |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV05 | BT04 Outlet Valve | PROXIMITY SENSOR - OPEN | [8 empty] | NOT OPEN | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | CY | 6 |  | R24-CY-006 | R24-C-006 | SOLENOID VALVE |  | DO | I.S. |  | Field |  |  |  |  | R24 | R24-CV06 | MP01 Feed Valve | SOLENOID VALVE | [8 empty] | CLOSE | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | ZSC | 6 |  | R24-ZSC-006 | R24-C-006 | PROXIMITY SENSOR - CLOSED |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV06 | MP01 Feed Valve | PROXIMITY SENSOR - CLOSED | [8 empty] | NOT CLOSED | CLOSED | R24 | - | - | - | - | - | - | - | -
R24 | ZSO | 6 |  | R24-ZSO-006 | R24-C-006 | PROXIMITY SENSOR - OPEN |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV06 | MP01 Feed Valve | PROXIMITY SENSOR - OPEN | [8 empty] | NOT OPEN | OPEN | R24 | - | - | - | - | - | - | - | -
R25 | CY | 8 |  | R24-CY-008 | R24-C-008 | SOLENOID VALVE |  | DO |  |  | PLC/ Field |  |  |  |  | R24 | R24-CV08 | SE01 Vent Isolation Valve | SOLENOID VALVE | [8 empty] | CLOSE | OPEN | R24 | - | - | - | - | - | - | - | - |  | Final Element for HW safety Interlock
R24 | CY | 10 |  | R24-CY-010 | R24-C-010 | SOLENOID VALVE |  | DO | I.S. |  | Field |  |  |  |  | R24 | R24-CV10 | BT03 Nitrogen Supply | SOLENOID VALVE | [8 empty] | CLOSE | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | ZSC | 10 |  | R24-ZSC-010 | R24-C-010 | PROXIMITY SENSOR - CLOSED |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV10 | BT03 Nitrogen Supply Valve | PROXIMITY SENSOR - CLOSED | [8 empty] | NOT CLOSED | CLOSED | R24 | - | - | - | - | - | - | - | -
R24 | ZSO | 10 |  | R24-ZSO-010 | R24-C-010 | PROXIMITY SENSOR - OPEN |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV10 | BT03 Nitrogen Supply Valve | PROXIMITY SENSOR - OPEN | [8 empty] | NOT OPEN | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | CY | 12 |  | R24-CY-012 | R24-C-012 | SOLENOID VALVE |  | DO | I.S. |  | Field |  |  |  |  | R24 | R24-CV12 | BT01 Outlet Valve | SOLENOID VALVE | [8 empty] | CLOSE | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | ZSC | 12 |  | R24-ZSC-012 | R24-C-012 | PROXIMITY SENSOR - CLOSED |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV12 | BT01 Outlet Valve | PROXIMITY SENSOR - CLOSED | [8 empty] | NOT CLOSED | CLOSED | R24 | - | - | - | - | - | - | - | -
R24 | ZSO | 12 |  | R24-ZSO-012 | R24-C-012 | PROXIMITY SENSOR - OPEN |  | DI | I.S. |  | Field |  |  |  |  | R24 | R24-CV12 | BT01 Outlet Valve | PROXIMITY SENSOR - OPEN | [8 empty] | NOT OPEN | OPEN | R24 | - | - | - | - | - | - | - | -
R24 | DS | 1 |  | R24-DS-001 | R24-D-001 | DRIVE - AVAILABLE |  | DI |  |  | PLC |  |  |  |  | R24 | R24-MP01 | Metering Pump 1 | DRIVE - AVAILABLE | [8 empty] | NOT AVAILABLE | AVAILABLE | R24 | - | - | - | - | - | - | - | -
R24 | DY | 1 |  | R24-DY-001 | R24-D-001 | DRIVE - RUNNING |  | DI |  |  | PLC |  |  |  |  | R24 | R24-MP01 | Metering Pump 1 | DRIVE - RUNNING | [8 empty] | NOT RUNNING | RUNNING | R24 | - | - | - | - | - | - | - | -
R24 | DYC | 1 |  | R24-DYC-001 | R24-D-001 | DRIVE - START/STOP |  | DO |  |  | PLC |  |  |  |  | R24 | R24-MP01 | Metering Pump 1 | DRIVE - START/STOP | [8 empty] | STOP | START | R24 | - | - | - | - | - | - | - | -
R24 | FT | 1 |  | R24-FT-001 | R24-F-001 | INDICATOR - TRANSMITTER - FLOW |  | AI | I.S. | Field | Field |  |  |  |  | R24 | R24-FI01 | MP01 Flow | TRANSMITTER - FLOW |  |  |  |  | 0 | 40 | Ltrs/hr |  | Not Applicable | Not Applicable | R24 | - | 22 | 2 | - | 1 | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer | Low alarm changed to 2.0 | 0.6
R24 | FI | 3 |  | R24-FI-003 | R24-F-003 | FLOW CONTROLLER |  | Comms | IS | Field | Field |  |  |  |  | R24 | R24-FI-003 | Hydrogen Flow | FLOW CONTROLLER |  |  |  |  | 0 | 30 | N.Ltrs/min |  | Not Applicable | Not Applicable | R24 | - | - | - | - | - | - | - | - |  | Comms link to PLC or traditional I/O (AI/AO)? | Corrected I/O tag/descriptor | 0.6
R24 | FI | 4 |  | R24-FI-004 | R24-F-004 | FLOW CONTROLLER |  | Comms | IS | Field | Field |  |  |  |  | R24 | R24-FI-004 | BT04 Inlet Flow | FLOW CONTROLLER |  |  |  |  | 0 | 40 | Ltrs/hr |  | Not Applicable | Not Applicable | R24 | - | 30 | - | - | - | - | - | - |  | Comms link to PLC or traditional I/O (AI/AO)? | Corrected I/O tag/descriptor | 0.6
R24 | FI | 5 |  | R24-FI-005 | R24-F-005 | FLOW CONTROLLER |  | Comms | IS | Field | Field |  |  |  |  | R24 | R24-FI-005 | N2 Sweep to BT01 | FLOW CONTROLLER |  |  |  |  | 0 | 40 | N.Ltrs/min |  | Not Applicable | Not Applicable | R24 | - | 20 | - | - | - | - | - | - |  | Comms link to PLC or traditional I/O (AI/AO)? | Corrected I/O tag/descriptor | 0.6
R24 | FI | 7 |  | R24-FI-007 | R24-F-007 | FLOW CONTROLLER |  | Comms | IS | Field | Field |  |  |  |  | R24 | R24-FI-007 | N2 Sweep to BT04 | FLOW CONTROLLER |  |  |  |  | 0 | 40 | N.Ltrs/min |  | Not Applicable | Not Applicable | R24 |  | 35 | [7 empty] | Comms link to PLC or traditional I/O (AI/AO)? | Corrected I/O tag/descriptor | 0.6
R24 | HS | 1 | A | R24-HS-001A | R24-H-001 | SWITCH - ESD |  | DI | I.S. |  | PLC |  |  |  |  | R24 | R24-HS01A | Process Stop Push Button | SWITCH - PUSHBUTTON | [7 empty] | 0 | PRESSED | NOT PRESSED | R24 | - | - | - | - | - | - | - | - |  | Sensor for HW Safety Interlock
R24 | LIT | 1 |  | R24-LIT-001 | R24-L-001 | INDICATOR - TRANSMITTER - LEVEL |  | AI | I.S. |  | Field |  |  |  |  | R24 | BT01-LI01 | BT01 Tank Level | TRANSMITTER - LEVEL |  |  |  |  | 0 | 300 | Litres |  | Not Applicable | Not Applicable | R24 | 250 | 230 | 20 | - | - | - | - | -
R24 | LIT | 3 |  | R24-LIT-003 | R24-L-003 | INDICATOR - TRANSMITTER - LEVEL |  | AI | I.S. |  | Field |  |  |  |  | R24 | BT01-LIC03 | SE01 Tank Level | TRANSMITTER - LEVEL |  |  |  |  | 0 | 20 | Litres |  | Not Applicable | Not Applicable | R24 | 17 | 15 | 9 | 7 | - | - | - | -
R24 | LIT | 4 |  | R24-LIT-004 | R24-L-004 | INDICATOR - TRANSMITTER - LEVEL |  | AI | I.S. |  | Field |  |  |  |  | R24 | BT01-LI04 | BT04 Tank Level | TRANSMITTER - LEVEL |  |  |  |  | 0 | 300 | Litres |  | Not Applicable | Not Applicable | R24 | 220 | 180 | - | - | - | - | - | -
R24 | LSL | 5 |  | R24-LSL-005 | R24-L-005 | SWITCH - LEVEL - LOW |  | DI | I.S. |  | PLC |  |  |  |  | R24 | R24-LAL05 | Separator Tank Low Level | SWITCH - LEVEL - LOW | [8 empty] | LOW LEVEL | NOT LOW LEVEL | R24 | - | - | - | - | - | - | - | - |  | Sensor for HW Safety Interlock
R24 | LSH | 6 |  | R24-LSH-006 | R24-L-006 | SWITCH - LEVEL - HIGH |  | DI | I.S. |  | PLC |  |  |  |  | R24 | R24-LAH06 | Separator Tank High Level | SWITCH - LEVEL - HIGH | [7 empty] | 0 | HIGH LEVEL | NOT HIGH LEVEL | R24 | - | - | - | - | - | - | - | - |  | Sensor for HW Safety Interlock
R24 | PIT | 1 |  | R24-PIT-001 | R24-P-001 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI01 | BT03 Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 75 | 70 | 60 | - | - | - | - | - |  | Low Alarm Enabled when System Pressure Control Sequence is Active
R24 | PT | 2 |  | R24-PIT-002 | R24-P-002 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI02 | CR01 Inlet Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | - | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer
R24 | PT | 3 |  | R24-PIT-003 | R24-P-003 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI03 | Metering Pump Outlet Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | - | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer
R24 | PIT | 4 |  | R24-PIT-004 | R24-P-004 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI04 | CR01 Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | - | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer
R24 | PT | 5 |  | R24-PIT-005 | R24-P-005 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI05 | CR01 Outlet Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | - | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer
R24 | PIT | 6 |  | R24-PIT-006 | R24-P-006 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI06 | CR02 Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | - | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer
R24 | PT | 7 |  | R24-PIT-007 | R24-P-007 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI07 | CR02 Outlet Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | - | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer
R24 | PIT | 8 |  | R24-PIT-008 | R24-P-008 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI08 | CR03 Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | - | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer
R24 | PT | 9 |  | R24-PIT-009 | R24-P-009 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI09 | CR03 Outlet Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | - | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer
R24 | PDIT | 10 |  | R24-PDIT-010 | R24-P-010 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PDI10 | Filter Differential Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 1000 | mbarg |  | Not Applicable | Not Applicable | R24 | 250 | 200 | - | - | - | - | - | -
R24 | PIT | 14 |  | R24-PIT-014 | R24-P-014 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI14 | BT04 Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 6 | barg |  | Not Applicable | Not Applicable | R24 | 1 | 0.8 | - | - | - | - | - | -
R24 | PIT | 20 |  | R24-PIT-020 | R24-P-020 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-PI20 | BT01 Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 6 | barg |  | Not Applicable | Not Applicable | R24 | 1 | 0.8 | - | - | - | - | - | -
R24 | PAH | 27 |  | R24-PAH-027 | R24-P-027 | SWITCH - LEVEL - HIGH |  | DI |  |  | PLC |  |  |  |  | R24 | R24-PAH27 | SE01 High Pressure | SWITCH - LEVEL - HIGH | [8 empty] | HIGH PRESSURE | NOT HIGH PRESSURE | R24 | [10 empty] | I/O point added to PLC | 0.6
R24 | PIT | 27 |  | R24-PIT-027 | R24-P-027 | INDICATOR - TRANSMITTER - PRESSURE |  | AI | I.S. |  | PLC |  |  |  |  | R24 | R24-PI27 | SE01 Pressure | TRANSMITTER - PRESSURE - DIAPHRAGM |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | - | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer
R24 | PI | 28 |  | R24-PI-028 | R24-P-028 | PRESSURE CONTROLLER |  | Comms | IS | Field | Field |  |  |  |  | R24 | R24-PI-028 | System Back Pressure | PRESSURE CONTROLLER |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 | 70 | 60 | 10 | - | 3 | - | - | - |  | Low Alarm Enabled when MP01 is 'Running', 10 second On Delay Timer | Corrected I/O tag/descriptor | 0.6
R24 | PI | 30 |  | R24-PI-030 | R24-P-030 | PRESSURE CONTROLLER |  | Comms | IS | Field | Field |  |  |  |  | R24 | R24-PI-030 | SE01 Outlet Pressure Reducer | PRESSURE CONTROLLER |  |  |  |  | 0 | 80 | barg |  | Not Applicable | Not Applicable | R24 |  | 6 | [8 empty] | I/O point added to PLC | 0.6
R24 | PI | 49 |  | R24-PI-049 | R24-P-049 | PRESSURE CONTROLLER |  | Comms | IS | Field | Field |  |  |  |  | R24 | R24-PI-049 | BT04 Back Pressure | PRESSURE CONTROLLER |  |  |  |  | 0 | 6 | barg |  | Not Applicable | Not Applicable | R24 | 0.8 | 0.6 | - | - | - | - | - | - |  |  | Corrected I/O tag/descriptor | 0.6
R24 | SYC | 1 |  | R24-SYC-001 | R24-S-001 | DRIVE - SPEED |  | AO |  |  | PLC |  |  |  |  | R24 | R24-SYC-001 | Metering Pump 1 | SPEED CONTROLLER - MCC |  |  |  |  | 0 | 100 | % |  | Not Applicable | Not Applicable | R24 | - | - | - | - | - | - | - | -
R24 | TT | 1 |  | R24-TT-001 | R24-T-001 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI01 | CR01 Temperature 1 | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 2 |  | R24-TT-002 | R24-T-002 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI02 | CR01 Temperature 2 | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 3 |  | R24-TT-003 | R24-T-003 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI03 | CR01 Temperature 3 | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 4 |  | R24-TT-004 | R24-T-004 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI04 | CR02 Temperature 1 | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 5 |  | R24-TT-005 | R24-T-005 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI05 | CR02 Temperature 2 | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 6 |  | R24-TT-006 | R24-T-006 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI06 | CR02 Temperature 3 | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 7 |  | R24-TT-007 | R24-T-007 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI07 | CR03 Temperature 1 | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 8 |  | R24-TT-008 | R24-T-008 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI08 | CR03 Temperature 2 | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 9 |  | R24-TT-009 | R24-T-009 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI09 | CR03 Temperature 3 | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 10 |  | R24-TT-010 | R24-T-010 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI10 | CR01 Jkt Return Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 11 |  | R24-TT-011 | R24-T-011 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI11 | CR02 Jkt Return Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 12 |  | R24-TT-012 | R24-T-012 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI12 | CR03 Jkt Return Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 13 |  | R24-TT-013 | R24-T-013 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI13 | CR01 Jkt Supply Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 14 |  | R24-TT-014 | R24-T-014 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI14 | CR02 Jkt Supply Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 15 |  | R24-TT-015 | R24-T-015 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI15 | CR03 Jkt Supply Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 16 |  | R24-TT-016 | R24-T-016 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI16 | PH01 Liquid Outlet Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 17 |  | R24-TT-017 | R24-T-017 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI17 | PH01 Gas Outlet Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 135 | 130 | -20 | -25 | - | - | - | -
R24 | TT | 18 |  | R24-TT-018 | R24-T-018 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI18 | CU01 Outlet Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 150 | degC |  | Not Applicable | Not Applicable | R24 | 45 | 40 | 10 | 5 | - | - | - | - |  |  | Alarm levels updated | 0.6
R24 | TT | 19 |  | R24-TT-019 | R24-T-019 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI19 | BT04 Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 80 | degC |  | Not Applicable | Not Applicable | R24 | 45 | 40 | 10 | 5 | - | - | - | -
R24 | TT | 20 |  | R24-TT-020 | R24-T-020 | INDICATOR - TRANSMITTER - TEMPERATURE |  | AI | I.S. |  | Field |  |  |  |  | R24 | R24-TI20 | BT01 Temperature | TRANSMITTER - TEMPERATURE |  |  |  |  | -30 | 80 | degC |  | Not Applicable | Not Applicable | R24 | 45 | 40 | 10 | 5 | - | - | - | -
R24 | XA | 10 |  | R24-XA-010 | R24-X-010 | ALARM SOUNDER |  | DO | I.S. |  | Field |  |  |  |  | R24 | R24-XA10 | Continuous Hydrogenation Alarm Sounder | ALARM - AUDIBLE | [8 empty] | NOT ACTIVE | ACTIVE | R24 | - | - | - | - | - | - | - | -
R24 | XL | 10 |  | R24-XL-010 | R24-X-010 | ALARM BEACON |  | DO | I.S. |  | Field |  |  |  |  | R24 | R24-XL10 | Continuous Hydrogenation Alarm Beacon | ANNUNCIATOR - LAMP | [8 empty] | NOT ACTIVE | ACTIVE | R24 | - | - | - | - | - | - | - | -
R24 | XS | 11 |  | R24-XS-011 | R24-X-011 | SWITCH - STATUS- H2SUPPLY |  | DI |  |  | PLC |  |  |  |  | R24 | R24-XS11 | Hydrogen Supply Status | SWITCH - STATUS - H2SUPPLY | [8 empty] | HYDROGEN NOT AVAILABLE | HYDROGEN AVAILABLE | R24 | - | - | - | - | - | - | - | -
R24 | XS | 12 |  | R24-XS-012 | R24-X-012 | SWITCH - STATUS- CT02AVAIL |  | DI |  |  | PLC |  |  |  |  | R24 | R24-XS12 | CT02 Status | SWITCH - STATUS - CT02AVAIL | [8 empty] | CT02 NOT AVAILABLE | CT02 AVAILABLE | R24 | - | - | - | - | - | - | - | -
R24 | XS | 13 |  | R24-XS-013 | R24-X-013 | ALARM - HYDROGENLEAK |  | DI |  |  | PLC |  |  |  |  | R24 | R24-XS13 | Hydrogen Leak Alarm | ALARM - HYDROGENLEAK | [7 empty] | 0 | LEAK DETECTED | LEAK NOT DETECTED | R24 | - | - | - | - | - | - | - | -
R24 | XS | 14 |  | R24-XS-014 | R24-X-014 | ALARM - CRITICALFAULT |  | DI |  |  | PLC |  |  |  |  | R24 | R24-XS14 | Critical Fault Alarm | ALARM - CRITICALFAULT | [7 empty] | 0 | ACTIVE | NOT ACTIVE | R24 | - | - | - | - | - | - | - | -
R24 | YS | 1 |  | R24-YS-001 | R24-Y-001 | INTERFACE SIGNAL - CONTINUOUS HYDROGENATION HEALTHY |  | DO |  |  | PLC |  |  |  |  | R24 | R24-YS01 | R24 Skid Healthy | STATUS SIGNAL | [7 empty] | 0 | NOT HEALTHY | HEALTHY | R24 | - | - | - | - | - | - | - | -
R24 | YS | 2 |  | R24-YS-002 | R24-Y-002 | INTERFACE SIGNAL - CONTINUOUS HYDROGENATION CRITICAL FAULT |  | DO |  |  | PLC |  |  |  |  | R24 | R24-YS02 | R24 Skid Critical Fault | STATUS SIGNAL | [7 empty] | 0 | NO CRITICAL FAULT | CRITICAL FAULT | R24 | - | - | - | - | - | - | - | -
R24 | YS | 3 |  | R24-YS-003 | R24-Y-003 | INTERFACE SIGNAL - CONTINUOUS HYDROGENATION FAULT |  | DO |  |  | PLC |  |  |  |  | R24 | R24-YS03 | R24 Skid Fault | STATUS SIGNAL | [7 empty] | 0 | NO FAULT | FAULT | R24 | - | - | - | - | - | - | - | -
R24 | YS | 4 |  | R24-YS-004 | R24-Y-004 | INTERFACE SIGNAL - CONTINUOUS HYDROGENATION RUNNING |  | DO |  |  | PLC |  |  |  |  | R24 | R24-YS04 | R24 Skid Running | STATUS SIGNAL | [8 empty] | NOT RUNNING | RUNNING | R24 | - | - | - | - | - | - | - | -
R24 | YS | 5 |  | R24-YS-005 | R24-Y-005 | INTERFACE SIGNAL - HYDROGEN SUPPLY REQUEST |  | DO |  |  | PLC |  |  |  |  | R24 | R24-YS05 | R24 Hydrogen Request | REQUEST SIGNAL | [8 empty] | Not Applicable | REQUEST HYDROGEN | R24 | - | - | - | - | - | - | - | -

## Comms to DeltaV
Comms to DeltaV

## Comms to TCU
Comms to TCU
Source: | Huber
| HEX Address | Parameter | Descriptor | Read/Write | Default Value
0 | 0 | Setpoint temperature controller | TCU Set Point (SP) | Write to TCU
1 | 1 | Internal temperature | TCU Supply Temperature (PV) | Read from TCU
2 | 2 | Return flow temperature | Jacket Return Temp | Read from TCU
3 | 3 | Pump pressure (absolute) | HTF Supply Pressure | Read from TCU
4 | 4 | Current output
5 | 5 | Fault report
6 | 6 | Warning report
7 | 7 | Process temperature (Lemosa)
8 | 8 | Actual value specification internal temperature
9 | 9 | Specification process temperature
10 | A | Status of the thermostat
11 | B | Activate the Blow-Down slider
12 | C | Activate Blow-Down slider heating
15 | F | Fill level
18 | 12 | PID parameter automatic temperature controller
19 | 13 | Temperature control mode
20 | 14 | Temperature control | TCU Off/On (0/1) | Write to TCU
21 | 15 | Operating mode compressor
22 | 16 | Circulation
23 | 17 | Operating lock
24 | 18 | Mode actual value specification internal temperature
25 | 19 | Mode actual value specification process temperature
26 | 1A | Freeze protection
27 | 1B + 1C | Serial number
29 | 1D | Kp of the internal controller
30 | 1E | Tn of the internal controller
31 | 1F | Tv of the internal controller
32 | 20 | Kp of the jacket controller
33 | 21 | Tn of the jacket controller
34 | 22 | Tv of the jacket controller
35 | 23 | Kp of the process controller
36 | 24 | Tn of the process controller
37 | 25 | Tv of the process controller
38 | 26 | Pump speed | Pump Speed | Read from TCU
44 | 2C | Cooling water inlet temperature
45 | 2D | Cooling water pressure
46 | 2E | Network connection conditions
48 | 30 | Minimum setpoint | Operating Low Limit | N/A - Temerature set via Pilot One Controller | -20 degC
49 | 31 | Maximum setpoint | Operating High Limit | N/A - Temerature set via Pilot One Controller | 130 degC
51 | 33 | Over-level limit
52 | 34 | Sub-level limit
53 | 35 | Setting the digital level output
58 | 3A | Process temperature
60 | 3C | Status of the thermostat
61 | 3D | Interference variables
62 | 3E | Pressure in return (absolute)
63 | 3F | Status Blow-Down
64 | 40 | Watchdog (Fault) | Watchdog (Fault) | Read from TCU
65 | 41 | Watchdog (2nd setpoint)
66 | 42 | 2. Setpoint | Crash cool temperature setpoint | N/A - Temerature set via Pilot One Controller | 5 degC
67 | 43 | PMA Mode
68 | 44 | Specify PMA output
72 | 48 | Setpoint pump speed
73 | 49 | Setpoint pump pressure
74 | 4A | VPC bypass operating mode
75 | 4B | VPC bypass target position
76 | 4C | Cooling water outlet temperature
77 | 4D | Thermal fluid volume flow
78 | 4E | Setpoint thermal fluid volume flow
79 | 4F | Setpoint Delta-T control
80 | 50 | Alarm limit Delta-T
81 | 51 | Upper alarm limit internal temperature
82 | 52 | Lower alarm limit internal temperature
83 | 53 | Upper alarm limit process temperature
84 | 54 | Lower alarm limit process temperature
85 | 55 | Setting of heating overtemperature protection
86 | 56 | Setting of overtemperature protection expansion vessel
88 | 58 | Start temperature control program
89 | 59 | Specify ramp duration
90 | 5A | Start ramp
91 | 5B | Specify Blow-Down operating status
92 | 5C | Days until maintenance
93 | 5D | Days to F-Gas check
94 | 5E | Create service packet
95 | 5F | Change program status
98 | 62 | Pressure of the VPC bypass
105 | 69 | Mode actual value specification thermal fluid volume flow
106 | 6A | Specification thermal fluid volume flow
107 | 6B | Control mode of the pump
108 | 6C | External POKO control
109 | 6D | POKO status
110 | 6E | Current output (high bytes)
111 | 6F | Ventilation
112 | 70 | Emptying
113 | 71 | Setpoint temperature controller
114 | 72 | VPC bypass position
115 | 73 | Message
116 | 74 | Disturbance feedforward VPC
117 | 75 | Actual value specification mode pump pressure
118 | 76 | Actual value specification pump pressure (relative) for pump control